## Read Me
ASHRAE Standard 140-2014
Informative Annex B16, Section B16.5.1 Example Results
for
Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
This spreadsheet contains the Standard 140, Informative Annex B16, Section B16.5.1 example results.
Users interested in looking at the example result tables and figures should go to the "Table List"
and "Figure List" sheets for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE: (see RESULTS5-3A.DOC for spreadsheet navigation)
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results. See instructions on page.
"Program List" : Documentation of simulation programs used to produce informative Annex B16, Section B16.5.1 example results
"Table List" : Listing of informative Annex B16, Section B16.5.1 Tables with locations
"Figure List" : Listing of informative Annex B16, Section B16.5.1 Figures with locations
"Q-Ptr1" through "Q-Ptr7" : Formatted result tables
"Fig B16.5.1-1 COP" through "Fig B16.5.1-26 QCL-QZL" : Result figures
"A" : Unformatted raw data compilation, all programs used by tables.
"Q" : Formatted results for use in tables and charts, Same results presented on "Q-Ptr1" to "Q-Ptr7"
"Data-Electr" through "Data-TempHum" : Unformatted results for use in charts.
Individual Example Result Worksheets as follows:
DOE21E-NREL: Example Results for DOE 2.1E, build 133, submitted by NREL
DOE21E-CIEMAT: Example Results for DOE 2.1E, build 88, submitted by CIEMAT
CLM2000: Example Results for CLIM2000, version 2.1.6, submitted by Electricité de France, France
TRN-ID: Example Results for TRNSYS, Version 14.2 with ideal controller model submitted by Technische Universität Dresden, Germany
TRN-RE: Example Results for TRNSYS, Version 14.2 with realistic controller model submitted by Technische Universität Dresden, Germany
CA-SIS: Example Results for CA-SIS version 1, submitted by Electricité de France, France
E+V1: Example Results for EnergyPlus Version 1.0 submitted by GARD Analytics
"Analytical-TUD": Analytical results for ideal controller model submitted by Technische Universität Dresden, Germany
"Analytical-HTAL1": Analytical results for ideal controller model submitted by Hochschule Technik & Architektur Luzern, Switzerland
"Analytical-HTAL2": Analytical results for realistic controller model submitted by Hochschule Technik & Architektur Luzern, Switzerland

## Adding Results
RESULTS5-3A.XLS
Output spreadsheet for Section 5.3 - Cooling Equipment Tests CE100-CE200
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
Import data so that Cell B25 of Sec5-3Aout.XLS is in B25 of Sheet "YourData"
Check that the first value (Total consumption kWh for E100) lands in YourData!B25.
Data should land in "YourData" cells as tabulated below. The new data will then appear in column L of Sheet A
and in rightmost column of each table on sheets "Q-Ptr1" to "Q-Ptr7" and "Q". Chart update of "your data" is also automated.
Complete the program information block on "Yourdata" which is used for legend titles for the tables and graphs.
CELL ADDRESS GUIDE FOR EXAMPLE RESULT WORKSHEETS AND NEW RESULTS
Gives locations in participant spreadsheets (.xls)
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) |  |  | (°C) |  |  | (°C)
| B25 | C25 | D25 | E25 | F25 | G25 | H25 | I25 | J25 | K25 | L25 | M25 | N25 | O25 | P25 | Q25 | R25 | S25 | T25
CE110 | B26 | C26 | D26 | E26 | F26 | G26 | H26 | I26 | J26 | K26 | L26 | M26 | N26 | O26 | P26 | Q26 | R26 | S26 | T26
CE120 | B27 | C27 | D27 | E27 | F27 | G27 | H27 | I27 | J27 | K27 | L27 | M27 | N27 | O27 | P27 | Q27 | R27 | S27 | T27
CE130 | B28 | C28 | D28 | E28 | F28 | G28 | H28 | I28 | J28 | K28 | L28 | M28 | N28 | O28 | P28 | Q28 | R28 | S28 | T28
CE140 | B29 | C29 | D29 | E29 | F29 | G29 | H29 | I29 | J29 | K29 | L29 | M29 | N29 | O29 | P29 | Q29 | R29 | S29 | T29
CE150 | B30 | C30 | D30 | E30 | F30 | G30 | H30 | I30 | J30 | K30 | L30 | M30 | N30 | O30 | P30 | Q30 | R30 | S30 | T30
CE160 | B31 | C31 | D31 | E31 | F31 | G31 | H31 | I31 | J31 | K31 | L31 | M31 | N31 | O31 | P31 | Q31 | R31 | S31 | T31
CE165 | B32 | C32 | D32 | E32 | F32 | G32 | H32 | I32 | J32 | K32 | L32 | M32 | N32 | O32 | P32 | Q32 | R32 | S32 | T32
CE170 | B33 | C33 | D33 | E33 | F33 | G33 | H33 | I33 | J33 | K33 | L33 | M33 | N33 | O33 | P33 | Q33 | R33 | S33 | T33
CE180 | B34 | C34 | D34 | E34 | F34 | G34 | H34 | I34 | J34 | K34 | L34 | M34 | N34 | O34 | P34 | Q34 | R34 | S34 | T34
CE185 | B35 | C35 | D35 | E35 | F35 | G35 | H35 | I35 | J35 | K35 | L35 | M35 | N35 | O35 | P35 | Q35 | R35 | S35 | T35
CE190 | B36 | C36 | D36 | E36 | F36 | G36 | H36 | I36 | J36 | K36 | L36 | M36 | N36 | O36 | P36 | Q36 | R36 | S36 | T36
CE195 | B37 | C37 | D37 | E37 | F37 | G37 | H37 | I37 | J37 | K37 | L37 | M37 | N37 | O37 | P37 | Q37 | R37 | S37 | T37
CE200 | B38 | C38 | D38 | E38 | F38 | G38 | H38 | I38 | J38 | K38 | L38 | M38 | N38 | O38 | P38 | Q38 | R38 | S38 | T38

## YourData
Sec5-3Aout.xls |  |  |  |  | Program Name and Version (with full build detail): |  |  |  |  | Paste new data in row 25 and below.
Output spreadsheet for HVAC BESTEST |  |  |  |  | OpenStudio 3.3.0 |  |  |  |  | Cells in blue are used in titles and labels
[5 empty] | Program Version Release Date: |  |  |  | 11/05/2021 | Editing them here flows thru to other tabs
[5 empty] | Program Name for Tables and Charts (short): |  |  |  | OS | To print pdf file, see instructions on "Title Page" tab.
Content Instructions (same as for Sec5-3Aout.XLS) |  |  |  |  | Results Submission Date: |  |  |  | 01/20/2022
Modeler Organization for Titles (long):
1. Use specified units |  |  |  |  | National Renewable Energy Laboratory
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | NREL
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
Program Name: |  | EnergyPlus 8.6.0
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1521.32 |  | 143.72 |  | 3797.78 | 3797.78 | -1.4324e-14 | 3654.07 | 3654.07 | 4.8976e-13 | 2.4019 | 22.2098 | 0.0074007 | 2.4038 | 22.2101 | 0.0074007 | 2.3988 | 22.2095 | 0.0074007
CE110 | 1070.17 |  | 127.739 |  | 3763.19 | 3763.19 | -1.3188e-14 | 3635.45 | 3635.45 | 3.9086e-13 | 3.3971 | 22.2 | 0.0065055 | 3.3998 | 22.2 | 0.0065055 | 3.3927 | 22.2 | 0.0065055
CE120 | 1007.53 |  | 116.592 |  | 3746.96 | 3746.96 | 5.457e-15 | 3630.36 | 3630.36 | 3.8745e-13 | 3.6032 | 26.7001 | 0.0079385 | 3.6061 | 26.7001 | 0.0079385 | 3.5985 | 26.7001 | 0.0079385
CE130 | 108.722 |  | 10.2709 |  | 216.987 | 216.987 | -7.9581e-16 | 206.716 | 206.716 | 2.5196e-14 | 1.9013 | 22.2001 | 0.0074028 | 1.9035 | 22.2001 | 0.0074028 | 1.8979 | 22.2001 | 0.0074028
CE140 | 67.9637 |  | 8.1116 |  | 196.205 | 196.205 | 1.5348e-15 | 188.093 | 188.093 | 2.0847e-14 | 2.7675 | 22.2001 | 0.0065112 | 2.7708 | 22.2001 | 0.0065112 | 2.7625 | 22.2001 | 0.0065112
CE150 | 1197.98 |  | 140.41 |  | 4508.72 | 3769.52 | 739.201 | 4368.31 | 3635.45 | 732.856 | 3.6464 | 22.2 | 0.0083559 | 3.6508 | 22.2 | 0.0083735 | 3.6426 | 22.2 | 0.0082847
CE160 | 1132.64 |  | 128.451 |  | 4490.98 | 3751.78 | 739.2 | 4362.53 | 3630.36 | 732.167 | 3.8516 | 26.7 | 0.010187 | 3.8563 | 26.7 | 0.010211 | 3.8479 | 26.7 | 0.0101
CE165 | 1492.12 |  | 148.682 |  | 4528.65 | 3789.45 | 739.201 | 4379.97 | 3646.67 | 733.299 | 2.9354 | 23.3058 | 0.0093261 | 2.9396 | 23.3062 | 0.0093448 | 2.9319 | 23.3054 | 0.0092453
CE170 | 635.681 |  | 73.0655 |  | 2224.79 | 1485.59 | 739.201 | 2151.72 | 1417.85 | 733.868 | 3.3849 | 22.2002 | 0.010522 | 3.3887 | 22.2002 | 0.010538 | 3.3802 | 22.2002 | 0.010438
CE180 | 1081.87 |  | 118.361 |  | 4480.97 | 1524.16 | 2956.81 | 4362.61 | 1417.85 | 2944.75 | 4.0325 | 22.2001 | 0.016193 | 4.0381 | 22.2001 | 0.016215 | 4.0271 | 22.2001 | 0.016074
CE185 | 1540.09 |  | 139.076 |  | 4522.35 | 1565.54 | 2956.81 | 4383.28 | 1436.48 | 2946.8 | 2.8461 | 22.2 | 0.016071 | 2.8515 | 22.2 | 0.016092 | 2.8408 | 22.2 | 0.015949
CE190 | 164.265 |  | 18.0235 |  | 574.168 | 204.567 | 369.601 | 556.145 | 188.093 | 368.052 | 3.3857 | 22.2003 | 0.015863 | 3.3916 | 22.2003 | 0.015935 | 3.3781 | 22.2002 | 0.015713
CE195 | 250.173 |  | 22.6548 |  | 597.626 | 228.024 | 369.601 | 574.971 | 206.716 | 368.255 | 2.2983 | 22.2003 | 0.015443 | 2.3029 | 22.2003 | 0.015504 | 2.2925 | 22.2003 | 0.015296
CE200 | 1465.63 |  | 153.526 |  | 5484.46 | 4263.43 | 1221.03 | 5330.93 | 4120.41 | 1210.52 | 3.6373 | 26.7013 | 0.011377 | 3.6425 | 26.7018 | 0.011399 | 3.6331 | 26.701 | 0.011281
|  | * |  | **
* | EnergyPlus compressor values includes the condenser fan
** | EnergyPlus can't calculate isolated condenser fan values

## Title Page
ASHRAE Standard 140-2014 | To print example results:
Informative Annex B16, Section B16.5.1 | 1. Select results type in cell B21:
"Example" for Standard 140 Annex B16.5.1 Example Results;
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 5.3 - HVAC Equipment Performance Tests CE100-CE200 | "Title Page" thru "Figure List"
"Q-Prt1" thru "Q-Prt7"
"Fig B16.5.1-1 COP" thru "Fig B16.5.1-26 QCL-QZL"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Scratch area for Table subtitle 1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Scratch area for Table subtitle 2
Scratch area for chart subtitles
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1 Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200

## Program List
ASHRAE Standard 140-2014
Participating Organizations and Computer Programs for
Quasi-analytical Solutions and Example Simulation Results
Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
The quasi-analytical solutions and programs used to generate the example simulation results are described in Table B17-1.
The first column of Table B17-1 ("Model"), indicates the proper program name and version number, or indicates a
quasi-analytical solution.
The second column ("Authoring Organization") indicates the national research facility, university, or industry organization
with expertise in building science that wrote the simulation software or did the quasi-analytical solutions.
The third column ("Implemented By") indicates the national research facility, university, or industry organization with
expertise in building science that performed the simulations or did the quasi-analytical solutions.
The entries in the fourth column are the abbreviations for the simulations and quasi-analytical solutions generally used in the
tables and charts which follow.
See Standard 140, Annex B17 for further details.
TABLE B17-1
Participating Organizations and Computer Programs
Model | Authoring Organization | Implemented By | Abbreviation
Quasi-Analytical solution with ideal controller model | Hochschule Technik & Architektur Luzern, Switzerland (HTAL) | Hochschule Technik & Architektur Luzern, Switzerland | HTAL1
Quasi-Analytical solution with realistic controller model | Hochschule Technik & Architektur Luzern, Switzerland | Hochschule Technik & Architektur Luzern, Switzerland | HTAL2
Quasi-Analytical Solution with ideal controller model | Technische Universität Dresden, Germany (TUD) | Technische Universität Dresden, Germany | TUD
CA-SIS V1 | Electricité de France, France (EDF) | Electricité de France, France | CA-SIS
CLIM2000 2.1.6 | Electricité de France, France | Electricité de France, France | CLM2000
DOE-2.1E-088 | LANL/LBNL/ESTSC,a,b,c USA | CIEMAT,d Spain | DOE21E/CIEMAT DOE2.1-E/CIEMAT
DOE-2.1E-133 | LANL/LBNL/JJH,a,b,e USA | NREL/JNA,f USA | DOE21E/NREL DOE2.1-E/NREL
ENERGYPLUS 1.0.0.023 | LBNL/UIUC/CERL/OSU/GARD Analytics/FSEC/DOE-OBT,a,g,h,i,j,k | GARD Analytics, USA | E+ EnergyPlus
TRNSYS 14.2-TUD with ideal controller model | University of Wisconsin, USA; Technische Universität Dresden, Ger. | Technische Universität Dresden, Germany | TRN-id TRNSYS-ideal
TRNSYS 14.2-TUD with real controller model | University of Wisconsin, USA; Technische Universität Dresden, Ger. | Technische Universität Dresden, Germany | TRN-re TRNSYS-real
aLANL: Los Alamos National Laboratory, United States
bLBNL: Lawrence Berkeley National Laboratory
cESTSC: Energy Science and Technology Software Center (at Oak Ridge National Laboratory, USA)
dCIEMAT: Centro de Investigaciones Energeticas, Medioambientales y Tecnologicas
eJJH: James J. Hirsch & Associates
fNREL/JNA: National Renewable Energy Laboratory/J. Neymark & Associates
gUIUC: University of Illinois Urbana/Champaign
hCERL: U.S. Army Corps of Engineers, Construction Engineering Research Laboratories
iOSU: Oklahoma State University
jFSEC: University of Central Florida, Florida Solar Energy Center
kDOE-OBT: U.S. Department of Energy, Office of Building Technology, State and Community Programs,
Energy Efficiency and Renewable Energy

## Table List
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B16.5.1-1 | Space Cooling Electricity Consumption | Q-Prt1 | A7 – Q76
| B16.5.1-2 | COP: Mean, and (Max-Min)/Mean | Q-Prt2 | A7 – Q42
| B16.5.1-3 | Coil Loads: Total, Sensible, and Latent | Q-Prt3 | A7 – Q59
| B16.5.1-4 | Sensible Coil Load minus Zone Load (Fan Heat) | Q-Prt3 | A60 – Q78
| B16.5.1-5 | Zone Loads: Total, Sensible, and Latent | Q-Prt4 | A7 – Q59
| B16.5.1-6 | Latent Coil Load minus Zone Load (Should be 0) | Q-Prt4 | A60 – Q78
| B16.5.1-7 | Sensitivities for Space Cooling Electricity Consumption | Q-Prt5 | A7 – Q96
| B16.5.1-8 | Sensitivities for COP and Coil Loads | Q-Prt6 | A7 – Q96
| B16.5.1-9 | Indoor Drybulb Temperature: Mean and (Max-Min)/Mean | Q-Prt7 | A7 – Q41
| B16.5.1-10 | Humidity Ratio: Mean and (Max-Min)/Mean | Q-Prt7 | A43 – Q78

## Figure List
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
List of Figures
| Figure | Title | Sheet Tab
| B16.5.1-1 | HVAC BESTEST: Mean COP | Fig B16.5.1-1 COP
| B16.5.1-2 | HVAC BESTEST: (Maximum - Minimum)/Mean COP | Fig B16.5.1-2 COPvar
| B16.5.1-3 | HVAC BESTEST: Mean COP Sensitivities | Fig B16.5.1-3 delCOP
| B16.5.1-4 | HVAC BESTEST: Total Space Cooling Electricity Consumption | Fig B16.5.1-4 Qtot
| B16.5.1-5 | HVAC BESTEST: Total Space Cooling Electricity Sensitivities | Fig B16.5.1-5 dQtot
| B16.5.1-6 | HVAC BESTEST: Compressor Electricity Consumption | Fig B16.5.1-6 Qcomp
| B16.5.1-7 | HVAC BESTEST: Total Compressor Electricity Sensitivities | Fig B16.5.1-7 dQcomp
| B16.5.1-8 | HVAC BESTEST: Total Indoor (Supply) Fan Electricity Consumption | Fig B16.5.1-8 Qidfan
| B16.5.1-9 | HVAC BESTEST: Indoor (Supply) Fan Electricity Sensitivities | Fig B16.5.1-9 dQidfan
| B16.5.1-10 | HVAC BESTEST: Outdoor (Condenser) Fan Electricity Consumption | Fig B16.5.1-10 Qodfan
| B16.5.1-11 | HVAC BESTEST: Outdoor (Condenser) Fan Electricity Sensitivities | Fig B16.5.1-11dQodfan
| B16.5.1-12 | HVAC BESTEST: Total Coil Load | Fig B16.5.1-12 QCtot
| B16.5.1-13 | HVAC BESTEST: Total Coil Load Sensitivities | Fig B16.5.1-13 dQCtot
| B16.5.1-14 | HVAC BESTEST: Sensible Coil Load | Fig B16.5.1-14 QCsens
| B16.5.1-15 | HVAC BESTEST: Sensible Coil Load Sensitivities | Fig B16.5.1-15 dQCsens
| B16.5.1-16 | HVAC BESTEST: Latent Coil Load | Fig B16.5.1-16 QClat
| B16.5.1-17 | HVAC BESTEST: Latent Coil Load Sensitivities | Fig B16.5.1-17 dQClat
| B16.5.1-18 | HVAC BESTEST: Mean Indoor Drybulb Temperature | Fig B16.5.1-18 IDB
| B16.5.1-19 | HVAC BESTEST: (Maximum - Minimum)/Mean Indoor Drybulb Temperature | Fig B16.5.1-19 IDBvar
| B16.5.1-20 | HVAC BESTEST: Mean Indoor Humidity Ratio | Fig B16.5.1-20 Humrat
| B16.5.1-21 | HVAC BESTEST: (Maximum - Minimum)/Mean Indoor Humidity Ratio | Fig B16.5.1-21Humratvar
| B16.5.1-22 | HVAC BESTEST: Total Zone Load | Fig B16.5.1-22 QZtot
| B16.5.1-23 | HVAC BESTEST: Sensible Zone Load | Fig B16.5.1-23 QZsens
| B16.5.1-24 | HVAC BESTEST: Latent Zone Load | Fig B16.5.1-24 QZlat
| B16.5.1-25 | HVAC BESTEST: Sensible Coil Load - Zone Load (Fan Heat) | Fig B16.5.1-25 QZfan
| B16.5.1-26 | HVAC BESTEST: Latent Coil Load - Latent Zone Load (Should = 0) | Fig B16.5.1-26 QCL-QZL

## Q-Prt1
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.1-1. Space Cooling Electricity Consumption
Energy Consumption, Total (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 1531 | 1530 | 1520.817 | 1519 | 1520.0282 | 1522.2661 | 1511.9369 | 1511.9369 | 1531 | 1.245% | 1530.548 | 1530.8 | 1530.6
CE110 | 1077 | 1089 | 1061.196 | 1065 | 1069.0685 | 1066.9607 | 1061.9658 | 1061.196 | 1089 | 2.582% | 1076.2349 | 1077.2 | 1077.4
CE120 | 1012 | 1012 | 1011.104 | 1003 | 1006.3903 | 1007.3023 | 1001.6637 | 1001.6637 | 1012 | 1.022% | 1012.6774 | 1011 | 1011
CE130 | 110 | 109 | 105.419 | 106 | 108.5963 | 108.7246 | 110.1161 | 105.419 | 110.1161 | 4.276% | 110.5818 | 109.5 | 109.5
CE140 | 68 | 69 | 65.008 | 66 | 67.903 | 67.7641 | 68.6428 | 65.008 | 69 | 5.819% | 68.9953 | 68.5 | 68.3
CE150 | 1208 | 1207 | 1202.424 | 1183 | 1197.1085 | 1199.055 | 1191.613 | 1183 | 1208 | 2.072% | 1206.49 | 1206.5 | 1206.5
CE160 | 1140 | 1139 | 1137.63 | 1107 | 1131.7342 | 1136.7334 | 1132.8835 | 1107 | 1140 | 2.896% | 1140.44 | 1139.3 | 1138.9
CE165 | 1502 | 1501 | 1499.447 | 1470 | 1491.0755 | 1499.7105 | 1489.9268 | 1470 | 1502 | 2.135% | 1497.8302 | 1499.7 | 1499.6
CE170 | 638 | 638 | 629.076 | 620 | 635.3716 | 635.909 | 635.8287 | 620 | 638 | 2.817% | 641.1173 | 637.7 | 637.8
CE180 | 1083 | 1082 | 1077.109 | 1080 | 1082.0002 | 1081.2706 | 1080.0377 | 1077.109 | 1083 | 0.5443% | 1082.666 | 1082.3 | 1081.9
CE185 | 1544 | 1543 | 1541.155 | 1547 | 1540.3879 | 1541.5256 | 1538.3972 | 1538.3972 | 1547 | 0.5573% | 1544.6397 | 1543.4 | 1542.9
CE190 | 164 | 164 | 160.219 | 160 | 164.3348 | 163.9975 | 165.1202 | 160 | 165.1202 | 3.113% | 165.173 | 164.1 | 164.2
CE195 | 250 | 250 | 244.919 | 246 | 250.2299 | 249.7321 | 251.5799 | 244.919 | 251.5799 | 2.657% | 252.1605 | 250 | 250
CE200 | 1477 | 1464 | 1468.214 | 1440 | 1464.5945 | 1479.9926 | 1479.9926 | 1440 | 1479.9926 | 2.708% | 1475.8104 | 1477.4 | 1477.1
Energy Consumption, Compressor (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 1319 | 1318 | 1307.458 | 1311 |  | 1311.1661 | 1302.7258 | 1302.7258 | 1319 | 1.234% | 1318.8515 | 1319 | 1318.9
CE110 | 889 | 899 | 865.866 | 883 |  | 879.3187 | 875.8322 | 865.866 | 899 | 3.728% | 887.9378 | 889.2 | 889.4
CE120 | 840 | 840 | 850.068 | 838 |  | 835.847 | 831.9292 | 831.9292 | 850.068 | 2.16% | 840.8662 | 839.1 | 839.2
CE130 | 95 | 94 | 93.198 | 93 |  | 93.6472 | 94.8489 | 93 | 95 | 2.113% | 95.2867 | 94.4 | 94.3
CE140 | 57 | 57 | 54.799 | 56 |  | 55.8468 | 56.5735 | 54.799 | 57 | 3.888% | 56.924 | 56.5 | 56.4
CE150 | 1000 | 999 | 1007.094 | 982 |  | 992.0333 | 986.7503 | 982 | 1007.094 | 2.512% | 998.9576 | 999.2 | 999.2
CE160 | 950 | 949 | 962.675 | 926 |  | 946.9958 | 944.3585 | 926 | 962.675 | 3.862% | 950.4111 | 949.4 | 949.1
CE165 | 1283 | 1281 | 1291.242 | 1256 |  | 1280.2205 | 1272.4664 | 1256 | 1291.242 | 2.754% | 1278.7205 | 1280.2 | 1280.2
CE170 | 531 | 530 | 538.959 | 523 |  | 528.3976 | 528.5837 | 523 | 538.959 | 3.005% | 532.9693 | 530 | 530.1
CE180 | 909 | 908 | 914.262 | 912 |  | 907.1462 | 906.4398 | 906.4398 | 914.262 | 0.8615% | 908.1216 | 908 | 907.7
CE185 | 1340 | 1339 | 1342.681 | 1344 |  | 1336.897 | 1334.3908 | 1334.3908 | 1344 | 0.7177% | 1339.7996 | 1338.6 | 1338.2
CE190 | 138 | 138 | 139.423 | 138 |  | 137.5107 | 138.4572 | 137.5107 | 139.423 | 1.387% | 138.4708 | 137.6 | 137.7
CE195 | 217 | 217 | 218.867 | 217 |  | 216.4828 | 218.0909 | 216.4828 | 218.867 | 1.097% | 218.6235 | 216.8 | 216.8
CE200 | 1250 | 1239 | 1249.027 | 1218 |  | 1252.8566 | 1252.8566 | 1218 | 1252.8566 | 2.789% | 1248.8198 | 1250.2 | 1250
Energy Consumption, Supply Fan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 144 | 144 | 145.185 | 141 | 143.5533 | 143.6481 | 142.3625 | 141 | 145.185 | 2.905% | 144.0538 | 144.1 | 144
CE110 | 128 | 129 | 132.917 | 122 | 127.5385 | 127.6854 | 126.659 | 122 | 132.917 | 8.53% | 128.1312 | 127.9 | 127.9
CE120 | 117 | 117 | 109.581 | 110 | 116.3845 | 116.6706 | 115.4998 | 109.581 | 117 | 6.346% | 116.9129 | 116.9 | 116.9
CE130 | 10 | 10 | 8.316 | 8 | 10.2557 | 10.2598 | 10.3889 | 8 | 10.3889 | 23.11% | 10.4079 | 10.3 | 10.3
CE140 | 8 | 8 | 6.947 | 6 | 8.1004 | 8.1094 | 8.2128 | 6 | 8.2128 | 27.19% | 8.2142 | 8.1 | 8.1
CE150 | 141 | 141 | 132.917 | 136 | 140.2495 | 140.8727 | 139.4036 | 132.917 | 141 | 5.727% | 141.2203 | 141.1 | 141.1
CE160 | 129 | 129 | 119.052 | 121 | 128.2763 | 129.1114 | 128.2863 | 119.052 | 129.1114 | 7.784% | 129.3096 | 129.2 | 129.2
CE165 | 149 | 150 | 141.678 | 145 | 148.5366 | 149.3574 | 147.976 | 141.678 | 150 | 5.577% | 149.0983 | 149.3 | 149.3
CE170 | 73 | 73 | 61.322 | 63 | 73.0096 | 73.1586 | 72.9774 | 61.322 | 73.1586 | 16.14% | 73.5918 | 73.2 | 73.2
CE180 | 118 | 119 | 110.813 | 112 | 118.3832 | 118.487 | 118.1287 | 110.813 | 119 | 6.902% | 118.7728 | 118.6 | 118.5
CE185 | 139 | 139 | 135.056 | 137 | 139.1103 | 139.2444 | 138.821 | 135.056 | 139.2444 | 3.005% | 139.3882 | 139.4 | 139.3
CE190 | 18 | 18 | 14.151 | 14 | 18.0337 | 18.0236 | 18.1435 | 14 | 18.1435 | 22.95% | 18.1701 | 18 | 18
CE195 | 23 | 23 | 17.728 | 18 | 22.6607 | 22.6253 | 22.7884 | 17.728 | 23 | 23.25% | 22.821 | 22.6 | 22.6
CE200 | 154 | 153 | 149.151 | 151 | 153.3548 | 154.56 | 154.56 | 149.151 | 154.56 | 3.5% | 154.4611 | 154.6 | 154.6
Energy Consumption, Condenser Fan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 68 | 68 | 68.174 | 67 |  | 67.452 | 66.8486 | 66.8486 | 68.174 | 1.96% | 67.6427 | 67.6 | 67.6
CE110 | 60 | 61 | 62.413 | 60 |  | 59.9566 | 59.4747 | 59.4747 | 62.413 | 4.887% | 60.166 | 60.1 | 60.1
CE120 | 55 | 55 | 51.455 | 55 |  | 54.7846 | 54.2347 | 51.455 | 55 | 6.457% | 54.8982 | 54.9 | 54.9
CE130 | 5 | 5 | 3.905 | 5 |  | 4.8176 | 4.8783 | 3.905 | 5 | 22.68% | 4.8872 | 4.8 | 4.8
CE140 | 4 | 4 | 3.262 | 4 |  | 3.8079 | 3.8565 | 3.262 | 4 | 19.32% | 3.8571 | 3.8 | 3.8
CE150 | 66 | 66 | 62.413 | 65 |  | 66.1491 | 65.4591 | 62.413 | 66.1491 | 5.638% | 66.3121 | 66.3 | 66.2
CE160 | 61 | 61 | 55.903 | 60 |  | 60.6262 | 60.2388 | 55.903 | 61 | 8.396% | 60.7193 | 60.7 | 60.7
CE165 | 70 | 70 | 66.527 | 69 |  | 70.1326 | 69.4843 | 66.527 | 70.1326 | 5.146% | 70.0114 | 70.1 | 70.1
CE170 | 34 | 34 | 28.795 | 34 |  | 34.3527 | 34.2676 | 28.795 | 34.3527 | 16.13% | 34.5562 | 34.4 | 34.4
CE180 | 56 | 56 | 52.034 | 56 |  | 55.6374 | 55.4691 | 52.034 | 56 | 7.117% | 55.7716 | 55.7 | 55.7
CE185 | 65 | 65 | 63.418 | 66 |  | 65.3842 | 65.1855 | 63.418 | 66 | 3.947% | 65.4519 | 65.4 | 65.4
CE190 | 8 | 9 | 6.645 | 8 |  | 8.4632 | 8.5195 | 6.645 | 9 | 27.67% | 8.5321 | 8.5 | 8.5
CE195 | 11 | 11 | 8.324 | 11 |  | 10.6241 | 10.7006 | 8.324 | 11 | 25.15% | 10.716 | 10.6 | 10.6
CE200 | 73 | 72 | 70.036 | 71 |  | 72.576 | 72.576 | 70.036 | 73 | 4.084% | 72.5296 | 72.6 | 72.6
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]

## Q-Prt2
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.1-2. COP: Mean, and (Max-Min)/Mean
Mean COP | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 2.39 | 2.389 | 2.4304 | 2.4064 | 2.404 | 2.4017 | 2.4184 | 2.389 | 2.4304 | 1.732% | 2.3889 | 2.39 | 2.39
CE110 | 3.38 | 3.342 | 3.4589 | 3.4146 | 3.4007 | 3.4087 | 3.4271 | 3.342 | 3.4589 | 3.459% | 3.3795 | 3.38 | 3.38
CE120 | 3.59 | 3.59 | 3.6139 | 3.623 | 3.6075 | 3.6054 | 3.6313 | 3.59 | 3.6313 | 1.15% | 3.5865 | 3.59 | 3.59
CE130 | 1.91 | 1.909 | 1.9752 | 1.953 | 1.9038 | 1.9198 | 1.9163 | 1.9038 | 1.9752 | 3.751% | 1.8895 | 1.91 | 1.91
CE140 | 2.77 | 2.734 | 2.9151 | 2.854 | 2.7714 | 2.7974 | 2.7996 | 2.734 | 2.9151 | 6.553% | 2.7502 | 2.77 | 2.77
CE150 | 3.62 | 3.63 | 3.6675 | 3.7 | 3.6544 | 3.6496 | 3.6734 | 3.62 | 3.7 | 2.204% | 3.6273 | 3.63 | 3.63
CE160 | 3.84 | 3.84 | 3.8658 | 3.95 | 3.8611 | 3.8452 | 3.8599 | 3.84 | 3.95 | 2.866% | 3.8329 | 3.84 | 3.84
CE165 | 2.92 | 2.92 | 2.9514 | 2.9853 | 2.9415 | 2.9257 | 2.9449 | 2.92 | 2.9853 | 2.228% | 2.9295 | 2.93 | 2.93
CE170 | 3.38 | 3.39 | 3.4423 | 3.477 | 3.3951 | 3.3944 | 3.4033 | 3.38 | 3.477 | 2.868% | 3.3672 | 3.39 | 3.39
CE180 | 4.04 | 4.04 | 4.0842 | 4.026 | 4.0432 | 4.0472 | 4.055 | 4.026 | 4.0842 | 1.44% | 4.0423 | 4.04 | 4.04
CE185 | 2.85 | 2.85 | 2.8744 | 2.823 | 2.8521 | 2.8512 | 2.8574 | 2.823 | 2.8744 | 1.803% | 2.8458 | 2.85 | 2.85
CE190 | 3.41 | 3.41 | 3.4865 | 3.457 | 3.3942 | 3.4096 | 3.4048 | 3.3942 | 3.4865 | 2.714% | 3.3865 | 3.41 | 3.41
CE195 | 2.31 | 2.31 | 2.3598 | 2.337 | 2.3033 | 2.3158 | 2.3054 | 2.3033 | 2.3598 | 2.453% | 2.2944 | 2.31 | 2.31
CE200 | 3.62 | 3.61 | 3.6677 | 3.708 | 3.6471 | 3.6102 | 3.6102 | 3.61 | 3.708 | 2.707% | 3.6206 | 3.62 | 3.62
(Max - Min)/Mean COP | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 0 | 0.00083717 | 0.0015062 | 0.0012467 | 0.0026072 | 0 | 0 | 0 | 0.0026072 | ---- | 0 |  | 0.00012552
CE110 | 0 | 0.010473 | 0.0017378 | 0.0011714 | 0.0027731 | 0 | 0.010592 | 0 | 0.010592 | ---- | 0 |  | 0.00038462
CE120 | 0 | 0.0036212 | 0.00079758 | 0.0011041 | 0.0027415 | 0 | 0.012271 | 0 | 0.012271 | ---- | 0 |  | 0.00030641
CE130 | 0 | 0.03824 | 0.012602 | 0.0087046 | 0.0037428 | 0 | 0.17198 | 0 | 0.17198 | ---- | 0 |  | -5.2356e-05
CE140 | 0 | 0.055962 | 0.010989 | 0.018921 | 0.0038004 | 0 | 0.20433 | 0 | 0.20433 | ---- | 0 |  | 3.6101e-05
CE150 | 0.0027624 | 0.0027548 | 0.0014674 | 0.0048649 | 0.010553 | 0 | 0.0092759 | 0 | 0.010553 | ---- | 0 |  | 0.00096419
CE160 | 0.0026042 | 0.0052083 | 0.0010614 | 0.0032911 | 0.011024 | 0 | 0.010193 | 0 | 0.011024 | ---- | 0 |  | 0.00026042
CE165 | 0.010274 | 0.0034247 | 0.0012002 | 0.0026798 | 0.011921 | 0 | 0.0084429 | 0 | 0.011921 | ---- | 0 |  | 0.00030717
CE170 | 0 | 0.0058997 | 0.0021466 | 0.0040265 | 0.015183 | 0 | 0.043444 | 0 | 0.043444 | ---- | 0 |  | 0.00026549
CE180 | 0.0049505 | 0.0024752 | 0.0023307 | 0.009687 | 0.029331 | 0 | 0.011687 | 0 | 0.029331 | ---- | 0 |  | 4.9505e-05
CE185 | 0.0070175 | 0.0035088 | 0.0023597 | 0.010273 | 0.034252 | 0 | 0.0091078 | 0 | 0.034252 | ---- | 0 |  | 0.00017544
CE190 | 0 | 0.02346 | 0.0071705 | 0.018802 | 0.039563 | 0 | 0.10066 | 0 | 0.10066 | ---- | 0 |  | -8.7977e-05
CE195 | 0 | 0.017316 | 0.0078108 | 0.016688 | 0.043389 | 0 | 0.08606 | 0 | 0.08606 | ---- | 0 |  | 0.00012987
CE200 | 0.0055249 | 0 | -1.2839e-05 | 0.0051241 | 0.011968 | 0 | 0 | -1.2839e-05 | 0.011968 | ---- | 0 |  | 8.2873e-05
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]

## Q-Prt3
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.1-3. Coil Loads: Total, Sensible, and Latent
Coil Load, Total (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 3800 | 3800 | 3841.47 | 3793.9625 | 3797.6497 | 3799.7366 | 3797.9491 | 3793.9625 | 3841.47 | 1.25% | 3800.3599 | 3800.4 | 3800.4
CE110 | 3765 | 3766 | 3803.58 | 3755.5686 | 3763.0688 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 1.275% | 3765.2438 | 3765 | 3765.3
CE120 | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.9059 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 0.6489% | 3748.902 | 3748.8 | 3748.5
CE130 | 219 | 219 | 215.778 | 215.1231 | 217.0012 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 2.119% | 219.3541 | 219.3 | 219.2
CE140 | 198 | 198 | 195.53 | 194.6073 | 196.2821 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 2.001% | 197.9671 | 197.9 | 197.3
CE150 | 4517 | 4517 | 4542.78 | 4527.5498 | 4508.7225 | 4516.9958 | 4515.0285 | 4508.7225 | 4542.78 | 0.7539% | 4517.5274 | 4517.4 | 4518.3
CE160 | 4501 | 4500 | 4516.378 | 4508.4994 | 4491.0487 | 4500.0682 | 4498.8816 | 4491.0487 | 4516.378 | 0.5628% | 4500.5449 | 4500.3 | 4499.9
CE165 | 4538 | 4538 | 4567.458 | 4548.9449 | 4528.6592 | 4537.0685 | 4535.1008 | 4528.6592 | 4567.458 | 0.8551% | 4536.998 | 4537.3 | 4537.9
CE170 | 2233 | 2232 | 2226.057 | 2236.5182 | 2224.8677 | 2231.6851 | 2231.6345 | 2224.8677 | 2236.5182 | 0.5219% | 2232.3427 | 2231.9 | 2232.5
CE180 | 4495 | 4495 | 4509.984 | 4534.5838 | 4481.208 | 4494.6115 | 4494.0999 | 4481.208 | 4534.5838 | 1.188% | 4495.2651 | 4494.9 | 4493.8
CE185 | 4507 | 4535 | 4564.894 | 4582.6495 | 4522.5899 | 4534.5283 | 4533.9432 | 4507 | 4582.6495 | 1.668% | 4535.1231 | 4534.9 | 4533.9
CE190 | 578 | 577 | 572.607 | 578.5463 | 574.3018 | 577.1889 | 577.6703 | 572.607 | 578.5463 | 1.028% | 577.5279 | 577.3 | 577.7
CE195 | 602 | 601 | 595.24 | 601.6999 | 597.7018 | 600.9508 | 601.339 | 595.24 | 602 | 1.124% | 601.3744 | 601.2 | 601.2
CE200 | 5498 | 5436 | 5534.2 | 5521.9812 | 5484.4779 | 5497.5648 | 5497.5648 | 5436 | 5534.2 | 1.786% | 5497.8008 | 5497.8 | 5497.8
Coil Load, Sensible (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 3800 | 3800 | 3841.47 | 3793.9625 | 3797.6448 | 3799.7366 | 3797.9491 | 3793.9625 | 3841.47 | 1.25% | 3800.3599 | 3800.4 | 3800.4
CE110 | 3765 | 3766 | 3803.58 | 3755.5686 | 3763.0651 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 1.275% | 3765.2438 | 3765 | 3765.3
CE120 | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.9017 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 0.6489% | 3748.902 | 3748.8 | 3748.5
CE130 | 219 | 219 | 215.778 | 215.1231 | 217.0004 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 2.119% | 219.3541 | 219.3 | 219.2
CE140 | 198 | 198 | 195.53 | 194.6073 | 196.2815 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 2.001% | 197.9671 | 197.9 | 197.3
CE150 | 3778 | 3778 | 3803.58 | 3786.0492 | 3776.027 | 3777.7958 | 3775.8216 | 3775.8216 | 3803.58 | 0.7346% | 3778.3318 | 3778.2 | 3779
CE160 | 3761 | 3761 | 3777.178 | 3769.0504 | 3759.0367 | 3760.8682 | 3759.6868 | 3759.0367 | 3777.178 | 0.4823% | 3761.3053 | 3761.1 | 3760.8
CE165 | 3798 | 3798 | 3828.258 | 3808.6166 | 3795.4926 | 3797.8685 | 3795.9117 | 3795.4926 | 3828.258 | 0.8627% | 3797.7525 | 3798.1 | 3798.6
CE170 | 1493 | 1493 | 1486.857 | 1497.6553 | 1491.221 | 1492.4851 | 1492.423 | 1486.857 | 1497.6553 | 0.7233% | 1493.027 | 1492.7 | 1493.1
CE180 | 1537 | 1538 | 1553.184 | 1606.6823 | 1537.3461 | 1537.8115 | 1537.3001 | 1537 | 1606.6823 | 4.531% | 1537.7939 | 1538.1 | 1537.7
CE185 | 1548 | 1578 | 1608.094 | 1652.6964 | 1576.6014 | 1577.7283 | 1577.1233 | 1548 | 1652.6964 | 6.636% | 1577.6007 | 1578.1 | 1577.7
CE190 | 208 | 208 | 203.007 | 212.1923 | 206.3654 | 207.5889 | 208.0235 | 203.007 | 212.1923 | 4.42% | 207.8123 | 207.7 | 207.9
CE195 | 232 | 232 | 225.64 | 235.0528 | 229.5563 | 231.3508 | 231.7335 | 225.64 | 235.0528 | 4.064% | 231.645 | 231.6 | 231.6
CE200 | 4276 | 4215 | 4313.176 | 4302.755 | 4274.2567 | 4276.5408 | 4276.5408 | 4215 | 4313.176 | 2.296% | 4276.6945 | 4276.8 | 4276.8
Coil Load, Latent (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 0 | 0 | 0 | 0 | 0.0049461 | 0 | 3.3138e-14 | 0 | 0.0049461 | ---- | 0 | 0 | 0
CE110 | 0 | 0 | 0 | 0 | 0.00371 | 0 | 2.6912e-15 | 0 | 0.00371 | ---- | 0 | 0 | 0
CE120 | 0 | 0 | 0 | 0 | 0.0042294 | 0 | 3.8103e-15 | 0 | 0.0042294 | ---- | 0 | 0 | 0
CE130 | 0 | 0 | 0 | 0 | 0.000795 | 0 | 3.1415e-14 | 0 | 0.000795 | ---- | 0 | 0 | 0
CE140 | 0 | 0 | 0 | 0 | 0.00067806 | 0 | -2.7533e-16 | -2.7533e-16 | 0.00067806 | ---- | 0 | 0 | 0
CE150 | 739 | 739 | 739.2 | 741.5006 | 732.6956 | 739.2 | 739.2069 | 732.6956 | 741.5006 | 1.191% | 739.1956 | 739.2 | 739.4
CE160 | 740 | 739 | 739.2 | 739.449 | 732.0119 | 739.2 | 739.1947 | 732.0119 | 740 | 1.081% | 739.2396 | 739.2 | 739.1
CE165 | 740 | 739 | 739.2 | 740.3283 | 733.1667 | 739.2 | 739.1892 | 733.1667 | 740.3283 | 0.9688% | 739.2454 | 739.2 | 739.3
CE170 | 740 | 739 | 739.2 | 738.8628 | 733.6467 | 739.2 | 739.2115 | 733.6467 | 740 | 0.8594% | 739.3157 | 739.2 | 739.4
CE180 | 2958 | 2957 | 2956.8 | 2927.9015 | 2943.8619 | 2956.8 | 2956.7992 | 2927.9015 | 2958 | 1.018% | 2957.4713 | 2956.8 | 2956.1
CE185 | 2959 | 2957 | 2956.8 | 2929.9531 | 2945.9884 | 2956.8 | 2956.8195 | 2929.9531 | 2959 | 0.9824% | 2957.5224 | 2956.8 | 2956.2
CE190 | 370 | 370 | 369.6 | 366.354 | 367.9364 | 369.6 | 369.6468 | 366.354 | 370 | 0.9862% | 369.7156 | 369.6 | 369.8
CE195 | 370 | 370 | 369.6 | 366.6471 | 368.1456 | 369.6 | 369.6055 | 366.6471 | 370 | 0.9071% | 369.7294 | 369.6 | 369.6
CE200 | 1222 | 1221 | 1221 | 1219.2263 | 1210.2212 | 1221.024 | 1221.024 | 1210.2212 | 1222 | 0.9647% | 1221.1063 | 1221 | 1221
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]
Table B16.5.1-4. Sensible Coil Load minus Zone Load (Fan Heat)
Sensible Coil - Zone Load, (Fan Heat) (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 144 | 144 | 187.05 | 138.6284 | 143.5176 | 143.6534 | 142.3632 | 138.6284 | 187.05 | 33.61% | 144.0536 | 144.1 | 144.1
CE110 | 128 | 129 | 167.979 | 118.9918 | 127.5306 | 127.6867 | 126.6828 | 118.9918 | 167.979 | 38.25% | 128.1309 | 127.9 | 128.2
CE120 | 117 | 117 | 133.008 | 107.5615 | 116.3664 | 116.6726 | 115.4889 | 107.5615 | 133.008 | 21.79% | 116.9127 | 116.9 | 116.6
CE130 | 10 | 10 | 8.434 | 7.6202 | 10.2529 | 10.2601 | 10.3985 | 7.6202 | 10.3985 | 26.97% | 10.4079 | 10.3 | 10.2
CE140 | 8 | 8 | 7.027 | 6.1547 | 8.0983 | 8.1097 | 8.2063 | 6.1547 | 8.2063 | 25.63% | 8.2142 | 8.2 | 7.6
CE150 | 141 | 141 | 167.979 | 149.4725 | 140.4768 | 140.8714 | 139.4441 | 139.4441 | 167.979 | 20.18% | 141.2189 | 141.1 | 141.9
CE160 | 129 | 129 | 146.726 | 137.456 | 128.5138 | 129.1114 | 128.2687 | 128.2687 | 146.726 | 14.29% | 129.316 | 129.2 | 128.9
CE165 | 149 | 149 | 181.387 | 160.6096 | 148.7644 | 149.3587 | 147.9512 | 147.9512 | 181.387 | 22.37% | 149.1144 | 149.4 | 149.9
CE170 | 73 | 73 | 68.706 | 79.1325 | 73.2822 | 73.1606 | 73.002 | 68.706 | 79.1325 | 14.2% | 73.5141 | 73.2 | 73.6
CE180 | 117 | 118 | 135.132 | 188.1594 | 119.3938 | 118.487 | 118.1294 | 117 | 188.1594 | 60.12% | 118.281 | 118.6 | 118.2
CE185 | 109 | 139 | 171.245 | 215.4162 | 140.0773 | 139.2451 | 138.8308 | 109 | 215.4162 | 76.5% | 138.8945 | 139.4 | 139
CE190 | 18 | 18 | 14.517 | 23.7397 | 18.1832 | 18.0237 | 18.1676 | 14.517 | 23.7397 | 50.99% | 18.0594 | 18 | 18.2
CE195 | 23 | 23 | 18.314 | 27.5498 | 22.8083 | 22.6256 | 22.7915 | 18.314 | 27.5498 | 40.81% | 22.6987 | 22.6 | 22.6
CE200 | 154 | 153 | 192.674 | 181.1254 | 153.7356 | 154.56 | 154.56 | 153 | 192.674 | 25.67% | 154.4636 | 154.6 | 154.6
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]

## Q-Prt4
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.1-5. Zone Loads: Total, Sensible, and Latent
Zone Load, Total (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 |  | NREL
CE100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3654.1272 | 3656.0832 | 3655.5859 | 3654.1272 | 3656.0832 | 0.0535% | 3656.3062 | 3656.3 | 3656.3
CE110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5345 | 3636.9245 | 3636.5534 | 3635.5345 | 3637 | 0.04029% | 3637.1129 | 3637.1 | 3637.1
CE120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3630.5353 | 3631.7568 | 3631.3216 | 3630.472 | 3632 | 0.04207% | 3631.9893 | 3631.9 | 3631.9
CE130 | 209 | 209 | 207.344 | 207.5029 | 206.7475 | 208.7252 | 209.371 | 206.7475 | 209.371 | 1.255% | 208.9462 | 209 | 209
CE140 | 190 | 190 | 188.503 | 188.4525 | 188.1832 | 189.5652 | 190.358 | 188.1832 | 190.358 | 1.146% | 189.7529 | 189.7 | 189.7
CE150 | 4376 | 4376 | 4374.801 | 4376.0258 | 4374.7468 | 4376.1245 | 4375.5775 | 4374.7468 | 4376.1245 | 0.03148% | 4376.3129 | 4376.3 | 4376.3
CE160 | 4371 | 4371 | 4369.652 | 4371.0434 | 4369.7196 | 4370.9568 | 4370.6181 | 4369.652 | 4371.0434 | 0.03183% | 4371.1893 | 4371.1 | 4371.1
CE165 | 4388 | 4388 | 4386.071 | 4387.456 | 4385.9248 | 4387.7098 | 4387.1605 | 4385.9248 | 4388 | 0.04729% | 4387.8381 | 4387.9 | 4387.9
CE170 | 2159 | 2159 | 2157.351 | 2157.9719 | 2157.1388 | 2158.5245 | 2158.621 | 2157.1388 | 2159 | 0.08622% | 2158.7129 | 2158.7 | 2158.7
CE180 | 4376 | 4376 | 4374.852 | 4376.0258 | 4374.7389 | 4376.1245 | 4375.9707 | 4374.7389 | 4376.1245 | 0.03166% | 4376.3129 | 4376.3 | 4376.3
CE185 | 4396 | 4396 | 4393.649 | 4394.7831 | 4393.3107 | 4395.2832 | 4395.0925 | 4393.3107 | 4396 | 0.06118% | 4395.5062 | 4395.5 | 4395.5
CE190 | 557 | 559 | 558.09 | 558.0305 | 557.7813 | 559.1652 | 559.4558 | 557 | 559.4558 | 0.4391% | 559.3529 | 559.3 | 559.3
CE195 | 576 | 579 | 576.926 | 577.0809 | 576.347 | 578.3252 | 578.542 | 576 | 579 | 0.5185% | 578.5462 | 578.6 | 578.6
CE200 | 5343 | 5283 | 5341.526 | 5342.9074 | 5341.5034 | 5343.0048 | 5343.0048 | 5283 | 5343.0048 | 1.123% | 5343.2549 | 5343.2 | 5343.2
Zone Load, Sensible (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 |  | NREL
CE100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3654.1272 | 3656.0832 | 3655.5859 | 3654.1272 | 3656.0832 | 0.0535% | 3656.3062 | 3656.3 | 3656.3
CE110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5345 | 3636.9245 | 3636.5534 | 3635.5345 | 3637 | 0.04029% | 3637.1129 | 3637.1 | 3637.1
CE120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3630.5353 | 3631.7568 | 3631.3216 | 3630.472 | 3632 | 0.04207% | 3631.9893 | 3631.9 | 3631.9
CE130 | 209 | 209 | 207.344 | 207.5029 | 206.7475 | 208.7252 | 209.371 | 206.7475 | 209.371 | 1.255% | 208.9462 | 209 | 209
CE140 | 190 | 190 | 188.503 | 188.4525 | 188.1832 | 189.5652 | 190.358 | 188.1832 | 190.358 | 1.146% | 189.7529 | 189.7 | 189.7
CE150 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5501 | 3636.9245 | 3636.3775 | 3635.5501 | 3637 | 0.03986% | 3637.1129 | 3637.1 | 3637.1
CE160 | 3632 | 3632 | 3630.452 | 3631.5944 | 3630.5229 | 3631.7568 | 3631.4181 | 3630.452 | 3632 | 0.04262% | 3631.9893 | 3631.9 | 3631.9
CE165 | 3649 | 3649 | 3646.871 | 3648.007 | 3646.7281 | 3648.5098 | 3647.9605 | 3646.7281 | 3649 | 0.06227% | 3648.6381 | 3648.7 | 3648.7
CE170 | 1420 | 1420 | 1418.151 | 1418.5229 | 1417.9388 | 1419.3245 | 1419.421 | 1417.9388 | 1420 | 0.1452% | 1419.5129 | 1419.5 | 1419.5
CE180 | 1420 | 1420 | 1418.052 | 1418.5229 | 1417.9523 | 1419.3245 | 1419.1707 | 1417.9523 | 1420 | 0.1443% | 1419.5129 | 1419.5 | 1419.5
CE185 | 1439 | 1439 | 1436.849 | 1437.2802 | 1436.5241 | 1438.4832 | 1438.2925 | 1436.5241 | 1439 | 0.1721% | 1438.7062 | 1438.7 | 1438.7
CE190 | 190 | 190 | 188.49 | 188.4525 | 188.1822 | 189.5652 | 189.8558 | 188.1822 | 190 | 0.9581% | 189.7529 | 189.7 | 189.7
CE195 | 209 | 209 | 207.326 | 207.5029 | 206.7479 | 208.7252 | 208.942 | 206.7479 | 209 | 1.078% | 208.9462 | 209 | 209
CE200 | 4122 | 4062 | 4120.502 | 4121.6295 | 4120.521 | 4121.9808 | 4121.9808 | 4062 | 4122 | 1.456% | 4122.2309 | 4122.2 | 4122.2
Zone Load, Latent (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 |  | NREL
CE100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- | 0 | 0 | 0
CE110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- | 0 | 0 | 0
CE120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- | 0 | 0 | 0
CE130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- | 0 | 0 | 0
CE140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- | 0 | 0 | 0
CE150 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
CE160 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
CE165 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
CE170 | 739 | 739 | 739.2 | 739.449 | 739.2 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
CE180 | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.7866 | 2957.5029 | 0.02423% | 2956.8 | 2956.8 | 2956.8
CE185 | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.7866 | 2957.5029 | 0.02423% | 2956.8 | 2956.8 | 2956.8
CE190 | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 367 | 370 | 0.8117% | 369.6 | 369.6 | 369.6
CE195 | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 367 | 370 | 0.8117% | 369.6 | 369.6 | 369.6
CE200 | 1221 | 1221 | 1221.024 | 1221.2778 | 1220.9824 | 1221.024 | 1221.024 | 1220.9824 | 1221.2778 | 0.0242% | 1221.024 | 1221 | 1221
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]
Table B16.5.1-6. Latent Coil Load minus Zone Load ( Should be 0 )
Latent Coil - Zone Load, (Should be 0) (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 |  | NREL
CE100 | 0 | 0 | 0 | 0 | 0.0049461 | 0 | 3.3138e-14 | 0 | 0.0049461 | ---- | 0 | 0 | 0 | 0
CE110 | 0 | 0 | 0 | 0 | 0.00371 | 0 | 2.6912e-15 | 0 | 0.00371 | ---- | 0 | 0 | 0 | 0
CE120 | 0 | 0 | 0 | 0 | 0.0042294 | 0 | 3.8103e-15 | 0 | 0.0042294 | ---- | 0 | 0 | 0 | 0
CE130 | 0 | 0 | 0 | 0 | 0.000795 | 0 | 3.1415e-14 | 0 | 0.000795 | ---- | 0 | 0 | 0 | 0
CE140 | 0 | 0 | 0 | 0 | 0.00067806 | 0 | -2.7533e-16 | -2.7533e-16 | 0.00067806 | ---- | 0 | 0 | 0 | 0
CE150 | 0 | 0 | 0 | 2.0516 | -6.5011 | 0 | 0.00687 | -6.5011 | 2.0516 | ---- | -0.0044111 | 0 | 0.2 | 0
CE160 | 1 | 0 | 0 | 0 | -7.1847 | 0 | -0.00534 | -7.1847 | 1 | ---- | 0.039573 | 0 | -0.1 | 0
CE165 | 1 | 0 | 0 | 0.87925 | -6.03 | 0 | -0.01082 | -6.03 | 1 | ---- | 0.045435 | 0 | 0.1 | 0
CE170 | 1 | 0 | 0 | -0.58617 | -5.5533 | 0 | 0.01152 | -5.5533 | 1 | ---- | 0.1157 | 0 | 0.2 | 0
CE180 | 1 | 0 | 0 | -29.6014 | -12.9246 | 0 | -0.00076 | -29.6014 | 1 | ---- | 0.67126 | 0 | -0.7 | 0
CE185 | 2 | 0 | 0 | -27.5498 | -10.7981 | 0 | 0.01946 | -27.5498 | 2 | ---- | 0.72237 | 0 | -0.6 | 0
CE190 | 3 | 0 | 0 | -3.2239 | -1.6626 | 0 | 0.046846 | -3.2239 | 3 | ---- | 0.11557 | 0 | 0.2 | 0
CE195 | 3 | 0 | 0 | -2.9308 | -1.4535 | 0 | 0.0055 | -2.9308 | 3 | ---- | 0.1294 | 0 | 0 | 0
CE200 | 1 | 0 | -0.024 | -2.0516 | -10.7612 | 0 | 0 | -10.7612 | 1 | ---- | 0.082262 | 0 | 0 | 0
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]

## Q-Prt5
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.1-7. Sensitivities for Space Cooling Electricity Consumption
Delta Qtot (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | -454 | -441 | -459.621 | -454 | -450.9597 | -455.3055 | -449.9711 | -459.621 | -441 | 4.104% | -454.3131 | -453.6 | -453.2
CE120-CE110 | -65 | -77 | -50.092 | -62 | -62.6782 | -59.6584 | -60.3021 | -77 | -50.092 | 41.15% | -63.5575 | -66.2 | -66.4
CE120-CE100 | -519 | -518 | -509.713 | -516 | -513.638 | -514.9639 | -510.2732 | -519 | -509.713 | 1.789% | -517.8706 | -519.8 | -519.6
CE130-CE100 | -1421 | -1421 | -1415.398 | -1413 | -1411.4319 | -1413.5415 | -1401.8208 | -1421 | -1401.8208 | 1.35% | -1419.9663 | -1421.3 | -1421.1
CE140-CE130 | -42 | -40 | -40.411 | -40 | -40.6934 | -40.9605 | -41.4733 | -42 | -40 | 4.847% | -41.5864 | -41 | -41.2
CE140-CE110 | -1009 | -1020 | -996.188 | -999 | -1001.1655 | -999.1966 | -993.323 | -1020 | -993.323 | 2.646% | -1007.2396 | -1008.7 | -1009.1
CE150-CE110 | 131 | 118 | 141.228 | 118 | 128.04 | 132.0944 | 129.6472 | 118 | 141.228 | 17.93% | 130.2551 | 129.3 | 129.1
CE160-CE150 | -68 | -68 | -64.794 | -76 | -65.3743 | -62.3216 | -58.7295 | -76 | -58.7295 | 25.8% | -66.05 | -67.2 | -67.6
CE165-CE160 | 362 | 362 | 361.817 | 363 | 359.3413 | 362.977 | 357.0433 | 357.0433 | 363 | 1.657% | 357.3902 | 360.4 | 360.7
CE170-CE150 | -570 | -569 | -573.348 | -563 | -561.7369 | -563.1461 | -555.7842 | -573.348 | -555.7842 | 3.094% | -565.3727 | -568.8 | -568.7
CE180-CE150 | -125 | -125 | -125.315 | -103 | -115.1083 | -117.7844 | -111.5753 | -125.315 | -103 | 17.97% | -123.824 | -124.2 | -124.6
CE180-CE170 | 445 | 444 | 448.033 | 460 | 446.6285 | 445.3617 | 444.2089 | 444 | 460 | 3.608% | 441.5487 | 444.6 | 444.1
CE185-CE180 | 461 | 461 | 464.046 | 467 | 458.3877 | 460.255 | 458.3596 | 458.3596 | 467 | 1.873% | 461.9737 | 461.1 | 461
CE190-CE180 | -919 | -918 | -916.89 | -920 | -917.6654 | -917.2731 | -914.9174 | -920 | -914.9174 | 0.5538% | -917.493 | -918.2 | -917.7
CE190-CE140 | 96 | 95 | 95.211 | 94 | 96.4318 | 96.2334 | 96.4774 | 94 | 96.4774 | 2.584% | 96.1777 | 95.6 | 95.9
CE195-CE190 | 86 | 86 | 84.7 | 86 | 85.8951 | 85.7346 | 86.4597 | 84.7 | 86.4597 | 2.041% | 86.9875 | 85.9 | 85.8
CE195-CE185 | -1294 | -1293 | -1296.236 | -1301 | -1290.158 | -1291.7935 | -1286.8173 | -1301 | -1286.8173 | 1.097% | -1292.4792 | -1293.4 | -1292.9
CE195-CE130 | 140 | 141 | 139.5 | 140 | 141.6336 | 141.0075 | 141.4638 | 139.5 | 141.6336 | 1.515% | 141.5788 | 140.5 | 140.5
CE200-CE100 | -54 | -66 | -52.603 | -79 | -55.4338 | -42.2735 | -31.9443 | -79 | -31.9443 | 87.34% | -54.7376 | -53.4 | -53.5
Del Qcomp (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | -430 | -419 | -441.592 | -428 |  | -431.8474 | -426.8936 | -441.592 | -419 | 5.253% | -430.9138 | -429.8 | -429.5
CE120-CE110 | -49 | -59 | -15.798 | -45 |  | -43.4717 | -43.903 | -59 | -15.798 | 87.95% | -47.0715 | -50.1 | -50.2
CE120-CE100 | -479 | -478 | -457.39 | -473 |  | -475.319 | -470.7965 | -479 | -457.39 | 4.51% | -477.9853 | -479.9 | -479.7
CE130-CE100 | -1224 | -1224 | -1214.26 | -1218 |  | -1217.5188 | -1207.8769 | -1224 | -1207.8769 | 1.317% | -1223.5648 | -1224.6 | -1224.6
CE140-CE130 | -38 | -37 | -38.399 | -37 |  | -37.8005 | -38.2753 | -38.399 | -37 | 3.676% | -38.3628 | -37.9 | -37.9
CE140-CE110 | -832 | -842 | -811.067 | -827 |  | -823.472 | -819.2586 | -842 | -811.067 | 3.717% | -831.0138 | -832.7 | -833
CE150-CE110 | 111 | 100 | 141.228 | 99 |  | 112.7146 | 110.9181 | 99 | 141.228 | 38.29% | 111.0199 | 110 | 109.8
CE160-CE150 | -50 | -50 | -44.419 | -56 |  | -45.0374 | -42.3919 | -56 | -42.3919 | 27.5% | -48.5466 | -49.8 | -50.1
CE165-CE160 | 333 | 332 | 328.567 | 330 |  | 333.2246 | 328.108 | 328.108 | 333.2246 | 1.55% | 328.3094 | 330.8 | 331.1
CE170-CE150 | -469 | -469 | -468.135 | -459 |  | -463.6356 | -458.1666 | -469 | -458.1666 | 2.314% | -465.9883 | -469.2 | -469.1
CE180-CE150 | -91 | -91 | -92.832 | -70 |  | -84.887 | -80.3105 | -92.832 | -70 | 25.04% | -90.836 | -91.2 | -91.5
CE180-CE170 | 378 | 378 | 375.303 | 389 |  | 378.7486 | 377.8561 | 375.303 | 389 | 3.634% | 375.1523 | 378 | 377.6
CE185-CE180 | 431 | 431 | 428.419 | 432 |  | 429.7507 | 427.9509 | 427.9509 | 432 | 0.9396% | 431.6779 | 430.6 | 430.5
CE190-CE180 | -771 | -770 | -774.839 | -774 |  | -769.6356 | -767.9826 | -774.839 | -767.9826 | 0.8904% | -769.6508 | -770.4 | -770
CE190-CE140 | 81 | 81 | 84.624 | 82 |  | 81.6639 | 81.8837 | 81 | 84.624 | 4.457% | 81.5469 | 81.1 | 81.3
CE195-CE190 | 79 | 79 | 79.444 | 79 |  | 78.9721 | 79.6337 | 78.9721 | 79.6337 | 0.8323% | 80.1527 | 79.2 | 79.1
CE195-CE185 | -1123 | -1122 | -1123.814 | -1127 |  | -1120.4142 | -1116.2999 | -1127 | -1116.2999 | 0.9541% | -1121.176 | -1121.8 | -1121.4
CE195-CE130 | 122 | 123 | 125.669 | 124 |  | 122.8356 | 123.242 | 122 | 125.669 | 2.989% | 123.3368 | 122.4 | 122.5
CE200-CE100 | -69 | -79 | -58.431 | -93 |  | -58.3094 | -49.8691 | -93 | -49.8691 | 62.29% | -70.0317 | -68.8 | -68.9
Del Q IDfan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | -16 | -15 | -12.268 | -19 | -16.0147 | -15.9627 | -15.7035 | -19 | -12.268 | 41.88% | -15.9226 | -16.2 | -16.1
CE120-CE110 | -11 | -12 | -23.336 | -12 | -11.154 | -11.0148 | -11.1592 | -23.336 | -11 | 111.4% | -11.2183 | -11 | -11
CE120-CE100 | -27 | -27 | -35.604 | -31 | -27.1687 | -26.9774 | -26.8627 | -35.604 | -26.8627 | 32.2% | -27.1409 | -27.2 | -27.1
CE130-CE100 | -134 | -134 | -136.869 | -133 | -133.2976 | -133.3883 | -131.9736 | -136.869 | -131.9736 | 3.661% | -133.646 | -133.8 | -133.7
CE140-CE130 | -2 | -2 | -1.369 | -2 | -2.1553 | -2.1503 | -2.1761 | -2.1761 | -1.369 | 36.72% | -2.1936 | -2.2 | -2.2
CE140-CE110 | -120 | -121 | -125.97 | -116 | -119.4381 | -119.5759 | -118.4462 | -125.97 | -116 | 8.319% | -119.917 | -119.8 | -119.8
CE150-CE110 | 13 | 12 | 0 | 14 | 12.711 | 13.1873 | 12.7446 | 0 | 14 | 106.4% | 13.0891 | 13.2 | 13.2
CE160-CE150 | -12 | -12 | -13.865 | -15 | -11.9732 | -11.7613 | -11.1173 | -15 | -11.1173 | 32.62% | -11.9106 | -11.9 | -11.9
CE165-CE160 | 20 | 21 | 22.626 | 24 | 20.2603 | 20.246 | 19.6897 | 19.6897 | 24 | 21.56% | 19.7887 | 20.1 | 20.1
CE170-CE150 | -68 | -68 | -71.595 | -73 | -67.2399 | -67.7141 | -66.4261 | -73 | -66.4261 | 9.695% | -67.6284 | -67.9 | -67.9
CE180-CE150 | -23 | -22 | -22.104 | -24 | -21.8663 | -22.3857 | -21.2749 | -24 | -21.2749 | 12.1% | -22.4474 | -22.5 | -22.6
CE180-CE170 | 45 | 46 | 49.491 | 49 | 45.3736 | 45.3284 | 45.1513 | 45 | 49.491 | 9.915% | 45.181 | 45.4 | 45.3
CE185-CE180 | 21 | 20 | 24.243 | 25 | 20.7271 | 20.7574 | 20.6923 | 20 | 25 | 24.11% | 20.6154 | 20.8 | 20.8
CE190-CE180 | -100 | -101 | -96.662 | -98 | -100.3495 | -100.4635 | -99.9852 | -101 | -96.662 | 4.314% | -100.6027 | -100.6 | -100.5
CE190-CE140 | 10 | 10 | 7.204 | 8 | 9.9333 | 9.9142 | 9.9306 | 7.204 | 10 | 28.19% | 9.9559 | 9.9 | 9.9
CE195-CE190 | 5 | 5 | 3.577 | 4 | 4.627 | 4.6017 | 4.6449 | 3.577 | 5 | 30.82% | 4.6509 | 4.6 | 4.6
CE195-CE185 | -116 | -116 | -117.328 | -119 | -116.4496 | -116.6191 | -116.0326 | -119 | -116 | 2.571% | -116.5672 | -116.8 | -116.7
CE195-CE130 | 13 | 13 | 9.412 | 10 | 12.405 | 12.3655 | 12.3994 | 9.412 | 13 | 29.08% | 12.4132 | 12.3 | 12.3
CE200-CE100 | 10 | 9 | 3.966 | 10 | 9.8015 | 10.9119 | 12.1975 | 3.966 | 12.1975 | 78.38% | 10.4073 | 10.5 | 10.6
Del Q ODfan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | -8 | -7 | -5.761 | -7 |  | -7.4954 | -7.374 | -8 | -5.761 | 29.88% | -7.4767 | -7.5 | -7.5
CE120-CE110 | -5 | -6 | -10.958 | -5 |  | -5.172 | -5.24 | -10.958 | -5 | 114.1% | -5.2677 | -5.2 | -5.2
CE120-CE100 | -13 | -13 | -16.719 | -12 |  | -12.6674 | -12.6139 | -16.719 | -12 | 37.11% | -12.7444 | -12.7 | -12.7
CE130-CE100 | -63 | -63 | -64.269 | -62 |  | -62.6344 | -61.9703 | -64.269 | -61.9703 | 3.661% | -62.7555 | -62.8 | -62.8
CE140-CE130 | -1 | -1 | -0.643 | -1 |  | -1.0097 | -1.0218 | -1.0218 | -0.643 | 37.51% | -1.03 | -1 | -1
CE140-CE110 | -56 | -57 | -59.151 | -56 |  | -56.1487 | -55.6182 | -59.151 | -55.6182 | 6.275% | -56.3088 | -56.3 | -56.3
CE150-CE110 | 6 | 5 | 0 | 5 |  | 6.1925 | 5.9844 | 0 | 6.1925 | 100.7% | 6.1462 | 6.2 | 6.1
CE160-CE150 | -5 | -5 | -6.51 | -5 |  | -5.5228 | -5.2203 | -6.51 | -5 | 27.14% | -5.5928 | -5.6 | -5.5
CE165-CE160 | 9 | 9 | 10.624 | 9 |  | 9.5064 | 9.2456 | 9 | 10.624 | 17.34% | 9.2921 | 9.4 | 9.4
CE170-CE150 | -32 | -32 | -33.618 | -31 |  | -31.7964 | -31.1915 | -33.618 | -31 | 8.228% | -31.756 | -31.9 | -31.8
CE180-CE150 | -10 | -10 | -10.379 | -9 |  | -10.5117 | -9.99 | -10.5117 | -9 | 14.33% | -10.5405 | -10.6 | -10.5
CE180-CE170 | 22 | 22 | 23.239 | 22 |  | 21.2847 | 21.2015 | 21.2015 | 23.239 | 9.578% | 21.2154 | 21.3 | 21.3
CE185-CE180 | 9 | 9 | 11.384 | 10 |  | 9.7468 | 9.7164 | 9 | 11.384 | 24.59% | 9.6803 | 9.7 | 9.7
CE190-CE180 | -48 | -47 | -45.389 | -48 |  | -47.1741 | -46.9496 | -48 | -45.389 | 5.53% | -47.2395 | -47.2 | -47.2
CE190-CE140 | 4 | 5 | 3.383 | 4 |  | 4.6553 | 4.6631 | 3.383 | 5 | 34.47% | 4.6749 | 4.7 | 4.7
CE195-CE190 | 3 | 2 | 1.679 | 3 |  | 2.1608 | 2.1811 | 1.679 | 3 | 62.08% | 2.1839 | 2.1 | 2.1
CE195-CE185 | -54 | -54 | -55.094 | -55 |  | -54.7601 | -54.4849 | -55.094 | -54 | 1.997% | -54.7359 | -54.8 | -54.8
CE195-CE130 | 6 | 6 | 4.419 | 6 |  | 5.8064 | 5.8223 | 4.419 | 6 | 27.21% | 5.8288 | 5.8 | 5.8
CE200-CE100 | 5 | 4 | 1.862 | 4 |  | 5.124 | 5.7274 | 1.862 | 5.7274 | 77.9% | 4.8869 | 5 | 5
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]

## Q-Prt6
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.1-8. Sensitivities for COP and Coil Loads
Delta COP (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | 0.99 | 0.953 | 1.0285 | 1.0082 | 0.99667 | 1.0069 | 1.0087 | 0.953 | 1.0285 | 7.625% | 0.99059 | 0.99 | 0.99
CE120-CE110 | 0.21 | 0.248 | 0.155 | 0.20837 | 0.20683 | 0.19677 | 0.20416 | 0.155 | 0.248 | 44.49% | 0.20704 | 0.21 | 0.21
CE120-CE100 | 1.2 | 1.201 | 1.1835 | 1.2166 | 1.2035 | 1.2037 | 1.2129 | 1.1835 | 1.2166 | 2.759% | 1.1976 | 1.2 | 1.2
CE130-CE100 | -0.48 | -0.48 | -0.4552 | -0.45341 | -0.50017 | -0.48198 | -0.50212 | -0.50212 | -0.45341 | 10.01% | -0.49937 | -0.48 | -0.48
CE140-CE130 | 0.86 | 0.825 | 0.9399 | 0.901 | 0.86754 | 0.87767 | 0.88334 | 0.825 | 0.9399 | 13.36% | 0.86071 | 0.86 | 0.86
CE140-CE110 | -0.61 | -0.608 | -0.5438 | -0.56063 | -0.6293 | -0.61124 | -0.6275 | -0.6293 | -0.5438 | 13.87% | -0.62925 | -0.61 | -0.61
CE150-CE110 | 0.24 | 0.288 | 0.2086 | 0.28537 | 0.25377 | 0.24097 | 0.24631 | 0.2086 | 0.288 | 31.85% | 0.24783 | 0.25 | 0.25
CE160-CE150 | 0.22 | 0.21 | 0.1983 | 0.25 | 0.20665 | 0.19555 | 0.18654 | 0.18654 | 0.25 | 30.43% | 0.20563 | 0.21 | 0.21
CE165-CE160 | -0.92 | -0.92 | -0.9144 | -0.96474 | -0.91963 | -0.91948 | -0.91505 | -0.96474 | -0.9144 | 5.545% | -0.90343 | -0.91 | -0.91
CE170-CE150 | -0.24 | -0.24 | -0.2252 | -0.223 | -0.25935 | -0.25525 | -0.27013 | -0.27013 | -0.223 | 19.1% | -0.26014 | -0.24 | -0.24
CE180-CE150 | 0.42 | 0.41 | 0.4167 | 0.326 | 0.38877 | 0.39757 | 0.38162 | 0.326 | 0.42 | 22.83% | 0.41502 | 0.41 | 0.41
CE180-CE170 | 0.66 | 0.65 | 0.6419 | 0.549 | 0.64811 | 0.65282 | 0.65175 | 0.549 | 0.66 | 16.86% | 0.67516 | 0.65 | 0.65
CE185-CE180 | -1.19 | -1.19 | -1.2098 | -1.203 | -1.1911 | -1.196 | -1.1976 | -1.2098 | -1.19 | 1.661% | -1.1965 | -1.19 | -1.19
CE190-CE180 | -0.63 | -0.63 | -0.5977 | -0.569 | -0.64902 | -0.63762 | -0.65027 | -0.65027 | -0.569 | 12.73% | -0.65583 | -0.63 | -0.63
CE190-CE140 | 0.64 | 0.676 | 0.5714 | 0.603 | 0.62282 | 0.61216 | 0.60515 | 0.5714 | 0.676 | 16.38% | 0.63627 | 0.64 | 0.64
CE195-CE190 | -1.1 | -1.1 | -1.1267 | -1.12 | -1.0909 | -1.0938 | -1.0994 | -1.1267 | -1.0909 | 3.262% | -1.0921 | -1.1 | -1.1
CE195-CE185 | -0.54 | -0.54 | -0.5146 | -0.48603 | -0.54881 | -0.53547 | -0.55209 | -0.55209 | -0.48603 | 12.15% | -0.55141 | -0.54 | -0.54
CE195-CE130 | 0.4 | 0.401 | 0.3846 | 0.384 | 0.39945 | 0.39602 | 0.3891 | 0.384 | 0.401 | 4.233% | 0.40487 | 0.4 | 0.4
CE200-CE100 | 1.23 | 1.221 | 1.2373 | 1.3016 | 1.2431 | 1.2084 | 1.1918 | 1.1918 | 1.3016 | 8.923% | 1.2317 | 1.23 | 1.23
Del Q coil,t (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | -35 | -34 | -37.89 | -38.3939 | -34.5809 | -35.1254 | -34.7129 | -38.3939 | -34 | 12.48% | -35.1161 | -35.4 | -35.1
CE120-CE110 | -16 | -17 | -40.1 | -16.4127 | -16.1629 | -16.1818 | -16.4257 | -40.1 | -16 | 146.5% | -16.3418 | -16.2 | -16.8
CE120-CE100 | -51 | -51 | -77.99 | -54.8066 | -50.7438 | -51.3072 | -51.1386 | -77.99 | -50.7438 | 52.75% | -51.4579 | -51.6 | -51.9
CE130-CE100 | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.6485 | -3580.7513 | -3578.1796 | -3625.692 | -3578.1796 | 1.327% | -3581.0058 | -3581.1 | -3581.2
CE140-CE130 | -21 | -21 | -20.248 | -20.5158 | -20.7191 | -21.3105 | -21.2052 | -21.3105 | -20.248 | 4.927% | -21.387 | -21.4 | -21.9
CE140-CE110 | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.7867 | -3566.9364 | -3564.6719 | -3608.05 | -3560.9613 | 1.32% | -3567.2767 | -3567.1 | -3568
CE150-CE110 | 752 | 751 | 739.2 | 771.9812 | 745.6537 | 752.3846 | 751.7923 | 739.2 | 771.9812 | 4.356% | 752.2836 | 752.4 | 753
CE160-CE150 | -16 | -17 | -26.402 | -19.0504 | -17.6739 | -16.9277 | -16.1469 | -26.402 | -16 | 59.46% | -16.9825 | -17.1 | -18.4
CE165-CE160 | 37 | 38 | 51.08 | 40.4455 | 37.6106 | 37.0003 | 36.2193 | 36.2193 | 51.08 | 40% | 36.4531 | 37 | 38
CE170-CE150 | -2284 | -2285 | -2316.723 | -2291.0317 | -2283.8549 | -2285.3107 | -2283.394 | -2316.723 | -2283.394 | 1.458% | -2285.1847 | -2285.5 | -2285.8
CE180-CE150 | -22 | -22 | -32.796 | 7.034 | -27.5145 | -22.3843 | -20.9286 | -32.796 | 7.034 | 172.5% | -22.2623 | -22.5 | -24.5
CE180-CE170 | 2262 | 2263 | 2283.927 | 2298.0657 | 2256.3404 | 2262.9264 | 2262.4654 | 2256.3404 | 2298.0657 | 1.844% | 2262.9224 | 2263 | 2261.3
CE185-CE180 | 12 | 40 | 54.91 | 48.0657 | 41.3818 | 39.9168 | 39.8433 | 12 | 54.91 | 107.3% | 39.858 | 40 | 40.1
CE190-CE180 | -3917 | -3918 | -3937.377 | -3956.0375 | -3906.9062 | -3917.4227 | -3916.4296 | -3956.0375 | -3906.9062 | 1.254% | -3917.7372 | -3917.6 | -3916.1
CE190-CE140 | 380 | 379 | 377.077 | 383.939 | 378.0197 | 379.514 | 379.106 | 377.077 | 383.939 | 1.807% | 379.5607 | 379.4 | 380.4
CE195-CE190 | 24 | 24 | 22.633 | 23.1536 | 23.4 | 23.7619 | 23.6687 | 22.633 | 24 | 5.756% | 23.8465 | 23.9 | 23.5
CE195-CE185 | -3905 | -3934 | -3969.654 | -3980.9496 | -3924.888 | -3933.5775 | -3932.6042 | -3980.9496 | -3905 | 1.931% | -3933.7487 | -3933.7 | -3932.7
CE195-CE130 | 383 | 382 | 379.462 | 386.5768 | 380.7006 | 381.9655 | 381.5695 | 379.462 | 386.5768 | 1.863% | 382.0203 | 381.9 | 382
CE200-CE100 | 1698 | 1636 | 1692.73 | 1728.0188 | 1686.8281 | 1697.8282 | 1699.6157 | 1636 | 1728.0188 | 5.421% | 1697.4409 | 1697.4 | 1697.4
Del Q coil,s (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | -35 | -34 | -37.89 | -38.3939 | -34.5797 | -35.1254 | -34.7129 | -38.3939 | -34 | 12.48% | -35.1161 | -35.4 | -35.1
CE120-CE110 | -16 | -17 | -40.1 | -16.4127 | -16.1635 | -16.1818 | -16.4257 | -40.1 | -16 | 146.5% | -16.3418 | -16.2 | -16.8
CE120-CE100 | -51 | -51 | -77.99 | -54.8066 | -50.7431 | -51.3072 | -51.1386 | -77.99 | -50.7431 | 52.75% | -51.4579 | -51.6 | -51.9
CE130-CE100 | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.6444 | -3580.7513 | -3578.1796 | -3625.692 | -3578.1796 | 1.327% | -3581.0058 | -3581.1 | -3581.2
CE140-CE130 | -21 | -21 | -20.248 | -20.5158 | -20.719 | -21.3105 | -21.2052 | -21.3105 | -20.248 | 4.927% | -21.387 | -21.4 | -21.9
CE140-CE110 | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.7837 | -3566.9364 | -3564.6719 | -3608.05 | -3560.9613 | 1.32% | -3567.2767 | -3567.1 | -3568
CE150-CE110 | 13 | 12 | 0 | 30.4807 | 12.9618 | 13.1846 | 12.5854 | 0 | 30.4807 | 228.7% | 13.088 | 13.2 | 13.7
CE160-CE150 | -17 | -17 | -26.402 | -16.9988 | -16.9902 | -16.9277 | -16.1348 | -26.402 | -16.1348 | 58.86% | -17.0265 | -17.1 | -18.2
CE165-CE160 | 37 | 37 | 51.08 | 39.5662 | 36.4558 | 37.0003 | 36.2248 | 36.2248 | 51.08 | 40.06% | 36.4472 | 37 | 37.8
CE170-CE150 | -2285 | -2285 | -2316.723 | -2288.3939 | -2284.806 | -2285.3107 | -2283.3986 | -2316.723 | -2283.3986 | 1.458% | -2285.3048 | -2285.5 | -2285.9
CE180-CE150 | -2241 | -2240 | -2250.396 | -2179.3669 | -2238.6808 | -2239.9843 | -2238.5215 | -2250.396 | -2179.3669 | 3.17% | -2240.5379 | -2240.1 | -2241.3
CE180-CE170 | 44 | 45 | 66.327 | 109.027 | 46.1251 | 45.3264 | 44.8771 | 44 | 109.027 | 144.8% | 44.7669 | 45.4 | 44.6
CE185-CE180 | 11 | 40 | 54.91 | 46.0141 | 39.2553 | 39.9168 | 39.8232 | 11 | 54.91 | 110% | 39.8069 | 40 | 40
CE190-CE180 | -1329 | -1330 | -1350.177 | -1394.49 | -1330.9807 | -1330.2227 | -1329.2766 | -1394.49 | -1329 | 4.924% | -1329.9815 | -1330.4 | -1329.8
CE190-CE140 | 10 | 10 | 7.477 | 17.585 | 10.0839 | 9.914 | 9.4592 | 7.477 | 17.585 | 100.3% | 9.8452 | 9.8 | 10.6
CE195-CE190 | 24 | 24 | 22.633 | 22.8605 | 23.1909 | 23.7619 | 23.71 | 22.633 | 24 | 5.741% | 23.8326 | 23.9 | 23.7
CE195-CE185 | -1316 | -1346 | -1382.454 | -1417.6436 | -1347.0452 | -1346.3775 | -1345.3897 | -1417.6436 | -1316 | 7.55% | -1345.9558 | -1346.5 | -1346.1
CE195-CE130 | 13 | 13 | 9.862 | 19.9297 | 12.5558 | 12.3655 | 11.964 | 9.862 | 19.9297 | 81.65% | 12.2909 | 12.3 | 12.4
CE200-CE100 | 476 | 415 | 471.706 | 508.7925 | 476.6119 | 476.8042 | 478.5917 | 415 | 508.7925 | 19.69% | 476.3346 | 476.4 | 476.4
Del Qcoil,lat (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) | Analytical |  |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE110-CE100 | 0 | 0 | 0 | 0 | -0.0012361 | 0 | -3.0447e-14 | -0.0012361 | 0 | ---- | 0 | 0 | 0
CE120-CE110 | 0 | 0 | 0 | 0 | 0.00051944 | 0 | 1.1191e-15 | 0 | 0.00051944 | ---- | 0 | 0 | 0
CE120-CE100 | 0 | 0 | 0 | 0 | -0.00071667 | 0 | -2.9328e-14 | -0.00071667 | 0 | ---- | 0 | 0 | 0
CE130-CE100 | 0 | 0 | 0 | 0 | -0.0041511 | 0 | -1.7231e-15 | -0.0041511 | 0 | ---- | 0 | 0 | 0
CE140-CE130 | 0 | 0 | 0 | 0 | -0.00011694 | 0 | -3.169e-14 | -0.00011694 | 0 | ---- | 0 | 0 | 0
CE140-CE110 | 0 | 0 | 0 | 0 | -0.0030319 | 0 | -2.9665e-15 | -0.0030319 | 0 | ---- | 0 | 0 | 0
CE150-CE110 | 739 | 739 | 739.2 | 741.5006 | 732.6919 | 739.2 | 739.2069 | 732.6919 | 741.5006 | 1.192% | 739.1956 | 739.2 | 739.4
CE160-CE150 | 1 | 0 | 0 | -2.0516 | -0.68366 | 0 | -0.01221 | -2.0516 | 1 | ---- | 0.043984 | 0 | -0.3
CE165-CE160 | 0 | 0 | 0 | 0.87925 | 1.1548 | 0 | -0.00548 | -0.00548 | 1.1548 | ---- | 0.005862 | 0 | 0.2
CE170-CE150 | 1 | 0 | 0 | -2.6377 | 0.95111 | 0 | 0.00465 | -2.6377 | 1 | ---- | 0.12011 | 0 | 0
CE180-CE150 | 2219 | 2218 | 2217.6 | 2186.4009 | 2211.1664 | 2217.6 | 2217.5924 | 2186.4009 | 2219 | 1.47% | 2218.2757 | 2217.6 | 2216.7
CE180-CE170 | 2218 | 2218 | 2217.6 | 2189.0387 | 2210.2153 | 2217.6 | 2217.5877 | 2189.0387 | 2218 | 1.306% | 2218.1556 | 2217.6 | 2216.7
CE185-CE180 | 1 | 0 | 0 | 2.0516 | 2.1265 | 0 | 0.02022 | 0 | 2.1265 | ---- | 0.051109 | 0 | 0.1
CE190-CE180 | -2588 | -2587 | -2587.2 | -2561.5475 | -2575.9255 | -2587.2 | -2587.1524 | -2588 | -2561.5475 | ---- | -2587.7557 | -2587.2 | -2586.3
CE190-CE140 | 370 | 370 | 369.6 | 366.354 | 367.9358 | 369.6 | 369.6468 | 366.354 | 370 | 0.9862% | 369.7156 | 369.6 | 369.8
CE195-CE190 | 0 | 0 | 0 | 0.29308 | 0.20914 | 0 | -0.041346 | -0.041346 | 0.29308 | ---- | 0.013833 | 0 | -0.2
CE195-CE185 | -2589 | -2587 | -2587.2 | -2563.306 | -2577.8429 | -2587.2 | -2587.214 | -2589 | -2563.306 | ---- | -2587.793 | -2587.2 | -2586.6
CE195-CE130 | 370 | 370 | 369.6 | 366.6471 | 368.1448 | 369.6 | 369.6055 | 366.6471 | 370 | 0.9071% | 369.7294 | 369.6 | 369.6
CE200-CE100 | 1222 | 1221 | 1221 | 1219.2263 | 1210.2163 | 1221.024 | 1221.024 | 1210.2163 | 1222 | 0.9651% | 1221.1063 | 1221 | 1221
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]

## Q-Prt7
ASHRAE Standard 140-2014, Informative Annex B16, Section B16.5.1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE100-CE200
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.1-9. Indoor Drybulb Temperature: Mean and (Max-Min)/Mean
Mean IDB (°C) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6346 | 22.1999 | 22.6346 | 1.958% | 22.2 | 22.2 | 22.216
CE110 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.1999 | 22.2 | 22.5242 | 22.1999 | 22.5242 | 1.46% | 22.2 | 22.2 | 22.214
CE120 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.7 | 26.7 | 27.0785 | 26.7 | 27.0785 | 1.417% | 26.7 | 26.7 | 26.712
CE130 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.6377 | 21.6377 | 22.2 | 2.533% | 22.2 | 22.2 | 22.187
CE140 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.5097 | 21.5097 | 22.2 | 3.11% | 22.2 | 22.2 | 22.185
CE150 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6771 | 22.1999 | 22.6771 | 2.149% | 22.2 | 22.2 | 22.216
CE160 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.6999 | 26.7 | 26.9948 | 26.6999 | 26.9948 | 1.104% | 26.7 | 26.7 | 26.714
CE165 | 23.3 | 23.3 | 23.4 | 23.4444 | 23.2999 | 23.3 | 23.7805 | 23.2999 | 23.7805 | 2.062% | 23.3 | 23.3 | 23.317
CE170 | 22.2 | 22.2 | 22.2 | 22.2222 | 22.1999 | 22.2 | 22.1169 | 22.1169 | 22.2222 | 0.4746% | 22.2 | 22.2 | 22.199
CE180 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.2 | 22.2 | 22.3344 | 22.2 | 22.3344 | 0.6054% | 22.2 | 22.2 | 22.205
CE185 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.2 | 22.2 | 22.3682 | 22.2 | 22.3682 | 0.7576% | 22.2 | 22.2 | 22.206
CE190 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.9469 | 21.9469 | 22.2 | 1.14% | 22.2 | 22.2 | 22.194
CE195 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 22.0113 | 22.0113 | 22.2 | 0.8502% | 22.2 | 22.2 | 22.195
CE200 | 26.7 | 26.7 | 26.8 | 26.7778 | 26.6999 | 26.7339 | 26.7339 | 26.6999 | 26.8 | 0.3749% | 26.7 | 26.7 | 26.713
(Max - Min)/Mean IDB (°C) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 0 | 0 | 0 | 0 | 1.9369e-05 | 0 | 0.049482 | 0 | 0.049482 | ---- | 0 |  | 0.0017105
CE110 | 0 | 0 | 0 | 0 | 2.4324e-05 | 0 | 0.047948 | 0 | 0.047948 | ---- | 0 |  | 0.0018907
CE120 | 0 | 0 | 0 | 0 | 1.4232e-05 | 0 | 0.077183 | 0 | 0.077183 | ---- | 0 |  | 0.0017221
CE130 | 0 | 0 | 0 | 0 | 2.2523e-06 | 0 | 0.056383 | 0 | 0.056383 | ---- | 0 |  | 0.0013521
CE140 | 0 | 0 | 0 | 0 | 1.3514e-06 | 0 | 0.069271 | 0 | 0.069271 | ---- | 0 |  | 0.0015326
CE150 | 0 | 0 | 0 | 0 | 2.7027e-05 | 0 | 0.053799 | 0 | 0.053799 | ---- | 0 |  | 0.0017105
CE160 | 0 | 0 | 0 | 0 | 4.2697e-05 | 0 | 0.045194 | 0 | 0.045194 | ---- | 0 |  | 0.0015722
CE165 | 0 | 0 | 0 | 0 | 4.3777e-05 | 0 | 0.051303 | 0 | 0.051303 | ---- | 0 |  | 0.0015439
CE170 | 0 | 0 | 0 | 0 | 2.3423e-05 | 0 | 0.049736 | 0 | 0.049736 | ---- | 0 |  | 0.0013064
CE180 | 0 | 0 | 0 | 0 | 2.027e-05 | 0 | 0.034924 | 0 | 0.034924 | ---- | 0 |  | 0.00081063
CE185 | 0 | 0 | 0 | 0 | 1.4865e-05 | 0 | 0.021459 | 0 | 0.021459 | ---- | 0 |  | 0.00072053
CE190 | 0 | 0 | 0 | 0 | 4.0541e-06 | 0 | 0.02825 | 0 | 0.02825 | ---- | 0 |  | 0.00072092
CE195 | 0 | 0 | 0 | 0 | 4.0541e-06 | 0 | 0.022716 | 0 | 0.022716 | ---- | 0 |  | 0.00063077
CE200 | 0 | 0 | 0 | 0 | 4.2322e-05 | 0 | 0 | 0 | 4.2322e-05 | ---- | 0 |  | 0
* ABS[(Max-Min)/(Mean of Analytical Solutions)]
Table B16.5.1-10. Humidity Ratio: Mean and (Max-Min)/Mean
Mean Humidity Ratio | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 0.0075 | 0.00691 | 0.0076 | 0.0074 | 0.0074745 | 0.0075036 | 0.0075088 | 0.00691 | 0.0076 | 9.364% | 0.0074274 | 0.00734 | 0.007339
CE110 | 0.0066 | 0.00692 | 0.0070296 | 0.0064 | 0.0065835 | 0.0065938 | 0.0066309 | 0.0064 | 0.0070296 | 9.772% | 0.0065187 | 0.0064 | 0.006411
CE120 | 0.008 | 0.007 | 0.0078 | 0.0078 | 0.0080402 | 0.0079506 | 0.0079517 | 0.007 | 0.0080402 | 13.22% | 0.0078783 | 0.00786 | 0.007873
CE130 | 0.0075 | 0.00691 | 0.0076 | 0.0073 | 0.0074769 | 0.0075036 | 0.0075194 | 0.00691 | 0.0076 | 9.364% | 0.0074274 | 0.00734 | 0.007339
CE140 | 0.0065 | 0.00692 | 0.0070601 | 0.0064 | 0.0065863 | 0.0065938 | 0.0065941 | 0.0064 | 0.0070601 | 10.25% | 0.0065187 | 0.0064 | 0.006402
CE150 | 0.0083 | 0.00853 | 0.0082 | 0.0083 | 0.0084223 | 0.0083236 | 0.0085152 | 0.0082 | 0.00853 | 4.018% | 0.0082272 | 0.0082 | 0.00821
CE160 | 0.0102 | 0.0101 | 0.009701 | 0.0099 | 0.010278 | 0.010069 | 0.010236 | 0.009701 | 0.010278 | 5.796% | 0.009969 | 0.00994 | 0.009946
CE165 | 0.0093 | 0.00985 | 0.0090039 | 0.0092 | 0.0093948 | 0.0093021 | 0.0095112 | 0.0090039 | 0.00985 | 9.171% | 0.0092694 | 0.0092 | 0.009208
CE170 | 0.0106 | 0.0107 | 0.010494 | 0.0105 | 0.010571 | 0.010471 | 0.010525 | 0.010471 | 0.0107 | 2.199% | 0.010367 | 0.01045 | 0.010451
CE180 | 0.0164 | 0.0164 | 0.016614 | 0.0164 | 0.016193 | 0.01631 | 0.016404 | 0.016193 | 0.016614 | 2.596% | 0.01619 | 0.01623 | 0.01623
CE185 | 0.0162 | 0.0171 | 0.016441 | 0.0162 | 0.016067 | 0.016151 | 0.016279 | 0.016067 | 0.0171 | 6.435% | 0.016056 | 0.01605 | 0.016059
CE190 | 0.016 | 0.0161 | 0.016254 | 0.0159 | 0.015855 | 0.015921 | 0.015707 | 0.015707 | 0.016254 | 3.451% | 0.015796 | 0.0159 | 0.015891
CE195 | 0.0156 | 0.0164 | 0.015764 | 0.0155 | 0.015446 | 0.01547 | 0.015326 | 0.015326 | 0.0164 | 6.967% | 0.015368 | 0.01544 | 0.015439
CE200 | 0.0114 | 0.0115 | 0.010933 | 0.0111 | 0.011461 | 0.011281 | 0.011281 | 0.010933 | 0.0115 | 5.106% | 0.011129 | 0.01109 | 0.011099
(Max - Min)/Mean Humidity Ratio | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
Case | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical* | TUD | HTAL1 | HTAL2 | NREL
CE100 | 0 | 0.021708 | 0 | 0 | 0.00051398 | 0 | 0 | 0 | 0.021708 | ---- | 0 |  | 0
CE110 | 0 | 0.021676 | 0.014226 | 0 | 0.00049972 | 0 | 0 | 0 | 0.021676 | ---- | 0 |  | 0
CE120 | 0 | 0 | 0 | 0 | 0.00052403 | 0 | 0 | 0 | 0.00052403 | ---- | 0 |  | 0
CE130 | 0 | 0.01013 | 0 | 0 | 0.00061108 | 0 | 0 | 0 | 0.01013 | ---- | 0 |  | 0
CE140 | 0 | 0.011561 | 0.014164 | 0 | 0.00064275 | 0 | 0 | 0 | 0.014164 | ---- | 0 |  | 0
CE150 | 0.012048 | 0 | 0 | 0 | 0.013105 | 0 | 0.013153 | 0 | 0.013153 | ---- | 0 |  | 0.00036541
CE160 | 0.019608 | 0 | 0.010308 | 0.010101 | 0.013391 | 0 | 0.010747 | 0 | 0.019608 | ---- | 0 |  | 0.00040217
CE165 | 0.010753 | 0.0010152 | 0.011106 | 0 | 0.013116 | 0 | 0.012512 | 0 | 0.013116 | ---- | 0 |  | 0.0003258
CE170 | 0 | 0 | 0.0095289 | 0 | 0.011456 | 0 | 0.023752 | 0 | 0.023752 | ---- | 0 |  | 0.00057411
CE180 | 0.018293 | 0 | 0.012038 | 0.012195 | 0.010319 | 0 | 0.040234 | 0 | 0.040234 | ---- | 0 |  | 0.00092421
CE185 | 0.012346 | 0.005848 | 0.018247 | 0.012346 | 0.010816 | 0 | 0.024571 | 0 | 0.024571 | ---- | 0 |  | 0.00080951
CE190 | 0 | 0 | 0.018457 | 0.018868 | 0.0145 | 0 | 0.031196 | 0 | 0.031196 | ---- | 0 |  | 0.00075514
CE195 | 0 | 0.0060976 | 0.01903 | 0.019355 | 0.013755 | 0 | 0.024142 | 0 | 0.024142 | ---- | 0 |  | 0.00064771
CE200 | 0.017544 | 0 | 0.0091467 | 0.009009 | 0.012859 | 0 | 0 | 0 | 0.017544 | ---- | 0 |  | 0
* ABS[ (Max-Min) / (Mean of Analytical Solutions) ]

## A
RESULTS5-3A.XLS
Output spreadsheet for Section 5.3 - Cooling Equipment Tests CE100-CE200
DO NOT INSERT or DELETE ROWS or COLUMNS ON THIS SHEET!
Raw (absolute) data presentation starts at row 17
Sensitivity (delta) data starts at row 400
START OF RAW DATA SUMMARY
Energy Consumption, Total (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-0500 | US-0401 | NREL
CE100 | 1519 | 1520.817 | 1530 | 1522.2661 | 1511.9369 | 1530.548 | 1530.8 | 1530.6 | 1531 | 1520.0282
CE110 | 1065 | 1061.196 | 1089 | 1066.9607 | 1061.9658 | 1076.2349 | 1077.2 | 1077.4 | 1077 | 1069.0685
CE120 | 1003 | 1011.104 | 1012 | 1007.3023 | 1001.6637 | 1012.6774 | 1011 | 1011 | 1012 | 1006.3903
CE130 | 106 | 105.419 | 109 | 108.7246 | 110.1161 | 110.5818 | 109.5 | 109.5 | 110 | 108.5963
CE140 | 66 | 65.008 | 69 | 67.7641 | 68.6428 | 68.9953 | 68.5 | 68.3 | 68 | 67.903
CE150 | 1183 | 1202.424 | 1207 | 1199.055 | 1191.613 | 1206.49 | 1206.5 | 1206.5 | 1208 | 1197.1085
CE160 | 1107 | 1137.63 | 1139 | 1136.7334 | 1132.8835 | 1140.44 | 1139.3 | 1138.9 | 1140 | 1131.7342
CE165 | 1470 | 1499.447 | 1501 | 1499.7105 | 1489.9268 | 1497.8302 | 1499.7 | 1499.6 | 1502 | 1491.0755
CE170 | 620 | 629.076 | 638 | 635.909 | 635.8287 | 641.1173 | 637.7 | 637.8 | 638 | 635.3716
CE180 | 1080 | 1077.109 | 1082 | 1081.2706 | 1080.0377 | 1082.666 | 1082.3 | 1081.9 | 1083 | 1082.0002
CE185 | 1547 | 1541.155 | 1543 | 1541.5256 | 1538.3972 | 1544.6397 | 1543.4 | 1542.9 | 1544 | 1540.3879
CE190 | 160 | 160.219 | 164 | 163.9975 | 165.1202 | 165.173 | 164.1 | 164.2 | 164 | 164.3348
CE195 | 246 | 244.919 | 250 | 249.7321 | 251.5799 | 252.1605 | 250 | 250 | 250 | 250.2299
CE200 | 1440 | 1468.214 | 1464 | 1479.9926 | 1479.9926 | 1475.8104 | 1477.4 | 1477.1 | 1477 | 1464.5945
Energy Consumption, Compressor (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-0500 | US-0401 | NREL
CE100 | 1311 | 1307.458 | 1318 | 1311.1661 | 1302.7258 | 1318.8515 | 1319 | 1318.9 | 1319
CE110 | 883 | 865.866 | 899 | 879.3187 | 875.8322 | 887.9378 | 889.2 | 889.4 | 889
CE120 | 838 | 850.068 | 840 | 835.847 | 831.9292 | 840.8662 | 839.1 | 839.2 | 840
CE130 | 93 | 93.198 | 94 | 93.6472 | 94.8489 | 95.2867 | 94.4 | 94.3 | 95
CE140 | 56 | 54.799 | 57 | 55.8468 | 56.5735 | 56.924 | 56.5 | 56.4 | 57
CE150 | 982 | 1007.094 | 999 | 992.0333 | 986.7503 | 998.9576 | 999.2 | 999.2 | 1000
CE160 | 926 | 962.675 | 949 | 946.9958 | 944.3585 | 950.4111 | 949.4 | 949.1 | 950
CE165 | 1256 | 1291.242 | 1281 | 1280.2205 | 1272.4664 | 1278.7205 | 1280.2 | 1280.2 | 1283
CE170 | 523 | 538.959 | 530 | 528.3976 | 528.5837 | 532.9693 | 530 | 530.1 | 531
CE180 | 912 | 914.262 | 908 | 907.1462 | 906.4398 | 908.1216 | 908 | 907.7 | 909
CE185 | 1344 | 1342.681 | 1339 | 1336.897 | 1334.3908 | 1339.7996 | 1338.6 | 1338.2 | 1340
CE190 | 138 | 139.423 | 138 | 137.5107 | 138.4572 | 138.4708 | 137.6 | 137.7 | 138
CE195 | 217 | 218.867 | 217 | 216.4828 | 218.0909 | 218.6235 | 216.8 | 216.8 | 217
CE200 | 1218 | 1249.027 | 1239 | 1252.8566 | 1252.8566 | 1248.8198 | 1250.2 | 1250 | 1250
Energy Consumption, Supply Fan (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-0500 | US-0401 | NREL
CE100 | 141 | 145.185 | 144 | 143.6481 | 142.3625 | 144.0538 | 144.1 | 144 | 144 | 143.5533
CE110 | 122 | 132.917 | 129 | 127.6854 | 126.659 | 128.1312 | 127.9 | 127.9 | 128 | 127.5385
CE120 | 110 | 109.581 | 117 | 116.6706 | 115.4998 | 116.9129 | 116.9 | 116.9 | 117 | 116.3845
CE130 | 8 | 8.316 | 10 | 10.2598 | 10.3889 | 10.4079 | 10.3 | 10.3 | 10 | 10.2557
CE140 | 6 | 6.947 | 8 | 8.1094 | 8.2128 | 8.2142 | 8.1 | 8.1 | 8 | 8.1004
CE150 | 136 | 132.917 | 141 | 140.8727 | 139.4036 | 141.2203 | 141.1 | 141.1 | 141 | 140.2495
CE160 | 121 | 119.052 | 129 | 129.1114 | 128.2863 | 129.3096 | 129.2 | 129.2 | 129 | 128.2763
CE165 | 145 | 141.678 | 150 | 149.3574 | 147.976 | 149.0983 | 149.3 | 149.3 | 149 | 148.5366
CE170 | 63 | 61.322 | 73 | 73.1586 | 72.9774 | 73.5918 | 73.2 | 73.2 | 73 | 73.0096
CE180 | 112 | 110.813 | 119 | 118.487 | 118.1287 | 118.7728 | 118.6 | 118.5 | 118 | 118.3832
CE185 | 137 | 135.056 | 139 | 139.2444 | 138.821 | 139.3882 | 139.4 | 139.3 | 139 | 139.1103
CE190 | 14 | 14.151 | 18 | 18.0236 | 18.1435 | 18.1701 | 18 | 18 | 18 | 18.0337
CE195 | 18 | 17.728 | 23 | 22.6253 | 22.7884 | 22.821 | 22.6 | 22.6 | 23 | 22.6607
CE200 | 151 | 149.151 | 153 | 154.56 | 154.56 | 154.4611 | 154.6 | 154.6 | 154 | 153.3548
Energy Consumption, Condenser Fan (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 67 | 68.174 | 68 | 67.452 | 66.8486 | 67.6427 | 67.6 | 67.6 | 68
CE110 | 60 | 62.413 | 61 | 59.9566 | 59.4747 | 60.166 | 60.1 | 60.1 | 60
CE120 | 55 | 51.455 | 55 | 54.7846 | 54.2347 | 54.8982 | 54.9 | 54.9 | 55
CE130 | 5 | 3.905 | 5 | 4.8176 | 4.8783 | 4.8872 | 4.8 | 4.8 | 5
CE140 | 4 | 3.262 | 4 | 3.8079 | 3.8565 | 3.8571 | 3.8 | 3.8 | 4
CE150 | 65 | 62.413 | 66 | 66.1491 | 65.4591 | 66.3121 | 66.3 | 66.2 | 66
CE160 | 60 | 55.903 | 61 | 60.6262 | 60.2388 | 60.7193 | 60.7 | 60.7 | 61
CE165 | 69 | 66.527 | 70 | 70.1326 | 69.4843 | 70.0114 | 70.1 | 70.1 | 70
CE170 | 34 | 28.795 | 34 | 34.3527 | 34.2676 | 34.5562 | 34.4 | 34.4 | 34
CE180 | 56 | 52.034 | 56 | 55.6374 | 55.4691 | 55.7716 | 55.7 | 55.7 | 56
CE185 | 66 | 63.418 | 65 | 65.3842 | 65.1855 | 65.4519 | 65.4 | 65.4 | 65
CE190 | 8 | 6.645 | 9 | 8.4632 | 8.5195 | 8.5321 | 8.5 | 8.5 | 8
CE195 | 11 | 8.324 | 11 | 10.6241 | 10.7006 | 10.716 | 10.6 | 10.6 | 11
CE200 | 71 | 70.036 | 72 | 72.576 | 72.576 | 72.5296 | 72.6 | 72.6 | 73
Coil Load, Total (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 3793.9625 | 3841.47 | 3800 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4 | 3800 | 3797.6497
CE110 | 3755.5686 | 3803.58 | 3766 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3 | 3765 | 3763.0688
CE120 | 3739.1559 | 3763.48 | 3749 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5 | 3749 | 3746.9059
CE130 | 215.1231 | 215.778 | 219 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2 | 219 | 217.0012
CE140 | 194.6073 | 195.53 | 198 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3 | 198 | 196.2821
CE150 | 4527.5498 | 4542.78 | 4517 | 4516.9958 | 4515.0285 | 4517.5274 | 4517.4 | 4518.3 | 4517 | 4508.7225
CE160 | 4508.4994 | 4516.378 | 4500 | 4500.0682 | 4498.8816 | 4500.5449 | 4500.3 | 4499.9 | 4501 | 4491.0487
CE165 | 4548.9449 | 4567.458 | 4538 | 4537.0685 | 4535.1008 | 4536.998 | 4537.3 | 4537.9 | 4538 | 4528.6592
CE170 | 2236.5182 | 2226.057 | 2232 | 2231.6851 | 2231.6345 | 2232.3427 | 2231.9 | 2232.5 | 2233 | 2224.8677
CE180 | 4534.5838 | 4509.984 | 4495 | 4494.6115 | 4494.0999 | 4495.2651 | 4494.9 | 4493.8 | 4495 | 4481.208
CE185 | 4582.6495 | 4564.894 | 4535 | 4534.5283 | 4533.9432 | 4535.1231 | 4534.9 | 4533.9 | 4507 | 4522.5899
CE190 | 578.5463 | 572.607 | 577 | 577.1889 | 577.6703 | 577.5279 | 577.3 | 577.7 | 578 | 574.3018
CE195 | 601.6999 | 595.24 | 601 | 600.9508 | 601.339 | 601.3744 | 601.2 | 601.2 | 602 | 597.7018
CE200 | 5521.9812 | 5534.2 | 5436 | 5497.5648 | 5497.5648 | 5497.8008 | 5497.8 | 5497.8 | 5498 | 5484.4779
Coil Load, Sensible (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
CE100 | NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE110 | 3793.9625 | 3841.47 | 3800 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4 | 3800 | 3797.6448
CE120 | 3755.5686 | 3803.58 | 3766 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3 | 3765 | 3763.0651
CE130 | 3739.1559 | 3763.48 | 3749 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5 | 3749 | 3746.9017
CE140 | 215.1231 | 215.778 | 219 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2 | 219 | 217.0004
CE150 | 194.6073 | 195.53 | 198 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3 | 198 | 196.2815
CE160 | 3786.0492 | 3803.58 | 3778 | 3777.7958 | 3775.8216 | 3778.3318 | 3778.2 | 3779 | 3778 | 3776.027
CE165 | 3769.0504 | 3777.178 | 3761 | 3760.8682 | 3759.6868 | 3761.3053 | 3761.1 | 3760.8 | 3761 | 3759.0367
CE170 | 3808.6166 | 3828.258 | 3798 | 3797.8685 | 3795.9117 | 3797.7525 | 3798.1 | 3798.6 | 3798 | 3795.4926
CE180 | 1497.6553 | 1486.857 | 1493 | 1492.4851 | 1492.423 | 1493.027 | 1492.7 | 1493.1 | 1493 | 1491.221
CE185 | 1606.6823 | 1553.184 | 1538 | 1537.8115 | 1537.3001 | 1537.7939 | 1538.1 | 1537.7 | 1537 | 1537.3461
CE190 | 1652.6964 | 1608.094 | 1578 | 1577.7283 | 1577.1233 | 1577.6007 | 1578.1 | 1577.7 | 1548 | 1576.6014
CE195 | 212.1923 | 203.007 | 208 | 207.5889 | 208.0235 | 207.8123 | 207.7 | 207.9 | 208 | 206.3654
CE200 | 235.0528 | 225.64 | 232 | 231.3508 | 231.7335 | 231.645 | 231.6 | 231.6 | 232 | 229.5563
| 4302.755 | 4313.176 | 4215 | 4276.5408 | 4276.5408 | 4276.6945 | 4276.8 | 4276.8 | 4276 | 4274.2567
Coil Load, Latent (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 0 | 0 | 0 | 0.0049461
CE110 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 0 | 0 | 0 | 0.00371
CE120 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 0 | 0 | 0 | 0.0042294
CE130 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 0 | 0 | 0 | 0.000795
CE140 | 0 | 0 | 0 | 0 | -2.7533e-16 | 0 | 0 | 0 | 0 | 0.00067806
CE150 | 741.5006 | 739.2 | 739 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4 | 739 | 732.6956
CE160 | 739.449 | 739.2 | 739 | 739.2 | 739.1947 | 739.2396 | 739.2 | 739.1 | 740 | 732.0119
CE165 | 740.3283 | 739.2 | 739 | 739.2 | 739.1892 | 739.2454 | 739.2 | 739.3 | 740 | 733.1667
CE170 | 738.8628 | 739.2 | 739 | 739.2 | 739.2115 | 739.3157 | 739.2 | 739.4 | 740 | 733.6467
CE180 | 2927.9015 | 2956.8 | 2957 | 2956.8 | 2956.7992 | 2957.4713 | 2956.8 | 2956.1 | 2958 | 2943.8619
CE185 | 2929.9531 | 2956.8 | 2957 | 2956.8 | 2956.8195 | 2957.5224 | 2956.8 | 2956.2 | 2959 | 2945.9884
CE190 | 366.354 | 369.6 | 370 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8 | 370 | 367.9364
CE195 | 366.6471 | 369.6 | 370 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6 | 370 | 368.1456
CE200 | 1219.2263 | 1221 | 1221 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221 | 1222 | 1210.2212
Envelope Load, Total (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 3655.3341 | 3654.42 | 3656 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3 | 3656 | 3654.1272
CE110 | 3636.5768 | 3635.601 | 3637 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1 | 3637 | 3635.5345
CE120 | 3631.5944 | 3630.472 | 3632 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9 | 3632 | 3630.5353
CE130 | 207.5029 | 207.344 | 209 | 208.7252 | 209.371 | 208.9462 | 209 | 209 | 209 | 206.7475
CE140 | 188.4525 | 188.503 | 190 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7 | 190 | 188.1832
CE150 | 4376.0258 | 4374.801 | 4376 | 4376.1245 | 4375.5775 | 4376.3129 | 4376.3 | 4376.3 | 4376 | 4374.7468
CE160 | 4371.0434 | 4369.652 | 4371 | 4370.9568 | 4370.6181 | 4371.1893 | 4371.1 | 4371.1 | 4371 | 4369.7196
CE165 | 4387.456 | 4386.071 | 4388 | 4387.7098 | 4387.1605 | 4387.8381 | 4387.9 | 4387.9 | 4388 | 4385.9248
CE170 | 2157.9719 | 2157.351 | 2159 | 2158.5245 | 2158.621 | 2158.7129 | 2158.7 | 2158.7 | 2159 | 2157.1388
CE180 | 4376.0258 | 4374.852 | 4376 | 4376.1245 | 4375.9707 | 4376.3129 | 4376.3 | 4376.3 | 4376 | 4374.7389
CE185 | 4394.7831 | 4393.649 | 4396 | 4395.2832 | 4395.0925 | 4395.5062 | 4395.5 | 4395.5 | 4396 | 4393.3107
CE190 | 558.0305 | 558.09 | 559 | 559.1652 | 559.4558 | 559.3529 | 559.3 | 559.3 | 557 | 557.7813
CE195 | 577.0809 | 576.926 | 579 | 578.3252 | 578.542 | 578.5462 | 578.6 | 578.6 | 576 | 576.347
CE200 | 5342.9074 | 5341.526 | 5283 | 5343.0048 | 5343.0048 | 5343.2549 | 5343.2 | 5343.2 | 5343 | 5341.5034
Envelope Load, Sensible (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 3655.3341 | 3654.42 | 3656 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3 | 3656 | 3654.1272
CE110 | 3636.5768 | 3635.601 | 3637 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1 | 3637 | 3635.5345
CE120 | 3631.5944 | 3630.472 | 3632 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9 | 3632 | 3630.5353
CE130 | 207.5029 | 207.344 | 209 | 208.7252 | 209.371 | 208.9462 | 209 | 209 | 209 | 206.7475
CE140 | 188.4525 | 188.503 | 190 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7 | 190 | 188.1832
CE150 | 3636.5768 | 3635.601 | 3637 | 3636.9245 | 3636.3775 | 3637.1129 | 3637.1 | 3637.1 | 3637 | 3635.5501
CE160 | 3631.5944 | 3630.452 | 3632 | 3631.7568 | 3631.4181 | 3631.9893 | 3631.9 | 3631.9 | 3632 | 3630.5229
CE165 | 3648.007 | 3646.871 | 3649 | 3648.5098 | 3647.9605 | 3648.6381 | 3648.7 | 3648.7 | 3649 | 3646.7281
CE170 | 1418.5229 | 1418.151 | 1420 | 1419.3245 | 1419.421 | 1419.5129 | 1419.5 | 1419.5 | 1420 | 1417.9388
CE180 | 1418.5229 | 1418.052 | 1420 | 1419.3245 | 1419.1707 | 1419.5129 | 1419.5 | 1419.5 | 1420 | 1417.9523
CE185 | 1437.2802 | 1436.849 | 1439 | 1438.4832 | 1438.2925 | 1438.7062 | 1438.7 | 1438.7 | 1439 | 1436.5241
CE190 | 188.4525 | 188.49 | 190 | 189.5652 | 189.8558 | 189.7529 | 189.7 | 189.7 | 190 | 188.1822
CE195 | 207.5029 | 207.326 | 209 | 208.7252 | 208.942 | 208.9462 | 209 | 209 | 209 | 206.7479
CE200 | 4121.6295 | 4120.502 | 4062 | 4121.9808 | 4121.9808 | 4122.2309 | 4122.2 | 4122.2 | 4122 | 4120.521
Envelope Load, Latent (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE150 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.1966
CE160 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.1966
CE165 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.1966
CE170 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.2
CE180 | 2957.5029 | 2956.8 | 2957 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2957 | 2956.7866
CE185 | 2957.5029 | 2956.8 | 2957 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2957 | 2956.7866
CE190 | 369.578 | 369.6 | 370 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6 | 367 | 369.5991
CE195 | 369.578 | 369.6 | 370 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6 | 367 | 369.5991
CE200 | 1221.2778 | 1221.024 | 1221 | 1221.024 | 1221.024 | 1221.024 | 1221 | 1221 | 1221 | 1220.9824
Mean COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 2.4064 | 2.4304 | 2.389 | 2.4017 | 2.4184 | 2.3889 | 2.39 | 2.39 | 2.39 | 2.404
CE110 | 3.4146 | 3.4589 | 3.342 | 3.4087 | 3.4271 | 3.3795 | 3.38 | 3.38 | 3.38 | 3.4007
CE120 | 3.623 | 3.6139 | 3.59 | 3.6054 | 3.6313 | 3.5865 | 3.59 | 3.59 | 3.59 | 3.6075
CE130 | 1.953 | 1.9752 | 1.909 | 1.9198 | 1.9163 | 1.8895 | 1.91 | 1.91 | 1.91 | 1.9038
CE140 | 2.854 | 2.9151 | 2.734 | 2.7974 | 2.7996 | 2.7502 | 2.77 | 2.77 | 2.77 | 2.7714
CE150 | 3.7 | 3.6675 | 3.63 | 3.6496 | 3.6734 | 3.6273 | 3.63 | 3.63 | 3.62 | 3.6544
CE160 | 3.95 | 3.8658 | 3.84 | 3.8452 | 3.8599 | 3.8329 | 3.84 | 3.84 | 3.84 | 3.8611
CE165 | 2.9853 | 2.9514 | 2.92 | 2.9257 | 2.9449 | 2.9295 | 2.93 | 2.93 | 2.92 | 2.9415
CE170 | 3.477 | 3.4423 | 3.39 | 3.3944 | 3.4033 | 3.3672 | 3.39 | 3.39 | 3.38 | 3.3951
CE180 | 4.026 | 4.0842 | 4.04 | 4.0472 | 4.055 | 4.0423 | 4.04 | 4.04 | 4.04 | 4.0432
CE185 | 2.823 | 2.8744 | 2.85 | 2.8512 | 2.8574 | 2.8458 | 2.85 | 2.85 | 2.85 | 2.8521
CE190 | 3.457 | 3.4865 | 3.41 | 3.4096 | 3.4048 | 3.3865 | 3.41 | 3.41 | 3.41 | 3.3942
CE195 | 2.337 | 2.3598 | 2.31 | 2.3158 | 2.3054 | 2.2944 | 2.31 | 2.31 | 2.31 | 2.3033
CE200 | 3.708 | 3.6677 | 3.61 | 3.6102 | 3.6102 | 3.6206 | 3.62 | 3.62 | 3.62 | 3.6471
Mean IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.6346 | 22.2 | 22.2 | 22.216 | 22.2 | 22.1999
CE110 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.5242 | 22.2 | 22.2 | 22.214 | 22.2 | 22.1999
CE120 | 26.7222 | 26.8 | 26.7 | 26.7 | 27.0785 | 26.7 | 26.7 | 26.712 | 26.7 | 26.7
CE130 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.6377 | 22.2 | 22.2 | 22.187 | 22.2 | 22.2
CE140 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.5097 | 22.2 | 22.2 | 22.185 | 22.2 | 22.2
CE150 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.6771 | 22.2 | 22.2 | 22.216 | 22.2 | 22.1999
CE160 | 26.7222 | 26.8 | 26.7 | 26.7 | 26.9948 | 26.7 | 26.7 | 26.714 | 26.7 | 26.6999
CE165 | 23.4444 | 23.4 | 23.3 | 23.3 | 23.7805 | 23.3 | 23.3 | 23.317 | 23.3 | 23.2999
CE170 | 22.2222 | 22.2 | 22.2 | 22.2 | 22.1169 | 22.2 | 22.2 | 22.199 | 22.2 | 22.1999
CE180 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.3344 | 22.2 | 22.2 | 22.205 | 22.2 | 22.2
CE185 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.3682 | 22.2 | 22.2 | 22.206 | 22.2 | 22.2
CE190 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.9469 | 22.2 | 22.2 | 22.194 | 22.2 | 22.2
CE195 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.0113 | 22.2 | 22.2 | 22.195 | 22.2 | 22.2
CE200 | 26.7778 | 26.8 | 26.7 | 26.7339 | 26.7339 | 26.7 | 26.7 | 26.713 | 26.7 | 26.6999
Mean Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 0.0074 | 0.0076 | 0.00691 | 0.0075036 | 0.0075088 | 0.0074274 | 0.00734 | 0.007339 | 0.0075 | 0.0074745
CE110 | 0.0064 | 0.0070296 | 0.00692 | 0.0065938 | 0.0066309 | 0.0065187 | 0.0064 | 0.006411 | 0.0066 | 0.0065835
CE120 | 0.0078 | 0.0078 | 0.007 | 0.0079506 | 0.0079517 | 0.0078783 | 0.00786 | 0.007873 | 0.008 | 0.0080402
CE130 | 0.0073 | 0.0076 | 0.00691 | 0.0075036 | 0.0075194 | 0.0074274 | 0.00734 | 0.007339 | 0.0075 | 0.0074769
CE140 | 0.0064 | 0.0070601 | 0.00692 | 0.0065938 | 0.0065941 | 0.0065187 | 0.0064 | 0.006402 | 0.0065 | 0.0065863
CE150 | 0.0083 | 0.0082 | 0.00853 | 0.0083236 | 0.0085152 | 0.0082272 | 0.0082 | 0.00821 | 0.0083 | 0.0084223
CE160 | 0.0099 | 0.009701 | 0.0101 | 0.010069 | 0.010236 | 0.009969 | 0.00994 | 0.009946 | 0.0102 | 0.010278
CE165 | 0.0092 | 0.0090039 | 0.00985 | 0.0093021 | 0.0095112 | 0.0092694 | 0.0092 | 0.009208 | 0.0093 | 0.0093948
CE170 | 0.0105 | 0.010494 | 0.0107 | 0.010471 | 0.010525 | 0.010367 | 0.01045 | 0.010451 | 0.0106 | 0.010571
CE180 | 0.0164 | 0.016614 | 0.0164 | 0.01631 | 0.016404 | 0.01619 | 0.01623 | 0.01623 | 0.0164 | 0.016193
CE185 | 0.0162 | 0.016441 | 0.0171 | 0.016151 | 0.016279 | 0.016056 | 0.01605 | 0.016059 | 0.0162 | 0.016067
CE190 | 0.0159 | 0.016254 | 0.0161 | 0.015921 | 0.015707 | 0.015796 | 0.0159 | 0.015891 | 0.016 | 0.015855
CE195 | 0.0155 | 0.015764 | 0.0164 | 0.01547 | 0.015326 | 0.015368 | 0.01544 | 0.015439 | 0.0156 | 0.015446
CE200 | 0.0111 | 0.010933 | 0.0115 | 0.011281 | 0.011281 | 0.011129 | 0.01109 | 0.011099 | 0.0114 | 0.011461
Maximum COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 2.407 | 2.4324 | 2.392 | 2.4017 | 2.4184 | 2.3889 |  | 2.3893 | 2.39 | 2.4067
CE110 | 3.417 | 3.4626 | 3.357 | 3.4087 | 3.4553 | 3.3795 |  | 3.3783 | 3.38 | 3.4049
CE120 | 3.625 | 3.6153 | 3.596 | 3.6054 | 3.6541 | 3.5865 |  | 3.5941 | 3.59 | 3.6118
CE130 | 1.961 | 1.9809 | 1.923 | 1.9198 | 2.0033 | 1.8895 |  | 1.9079 | 1.91 | 1.907
CE140 | 2.882 | 2.9278 | 2.833 | 2.7974 | 2.8848 | 2.7502 |  | 2.7701 | 2.77 | 2.7761
CE150 | 3.709 | 3.6706 | 3.63 | 3.6496 | 3.6952 | 3.6273 |  | 3.6295 | 3.63 | 3.6756
CE160 | 3.957 | 3.8682 | 3.85 | 3.8452 | 3.8606 | 3.8329 |  | 3.838 | 3.84 | 3.8843
CE165 | 2.989 | 2.9533 | 2.93 | 2.9257 | 2.9584 | 2.9295 |  | 2.9269 | 2.94 | 2.9606
CE170 | 3.485 | 3.446 | 3.4 | 3.3944 | 3.4645 | 3.3672 |  | 3.3859 | 3.38 | 3.4229
CE180 | 4.053 | 4.0893 | 4.05 | 4.0472 | 4.0754 | 4.0423 |  | 4.0442 | 4.05 | 4.1051
CE185 | 2.844 | 2.8778 | 2.85 | 2.8512 | 2.8622 | 2.8458 |  | 2.8485 | 2.86 | 2.9025
CE190 | 3.489 | 3.5 | 3.45 | 3.4096 | 3.508 | 3.3865 |  | 3.4087 | 3.41 | 3.4525
CE195 | 2.36 | 2.3681 | 2.33 | 2.3158 | 2.4571 | 2.2944 |  | 2.3143 | 2.31 | 2.3495
CE200 | 3.717 | 3.6716 | 3.61 | 3.6102 | 3.6102 | 3.6206 |  | 3.6173 | 3.63 | 3.6707
Max IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 22.3333 | 22.3 | 22.2 | 22.2 | 23.21 | 22.2 |  | 22.235 | 22.2 | 22.2001
CE110 | 22.2778 | 22.3 | 22.2 | 22.2 | 23.06 | 22.2 |  | 22.235 | 22.2 | 22.2002
CE120 | 26.7222 | 26.8 | 26.7 | 26.7 | 28.26 | 26.7 |  | 26.735 | 26.7 | 26.7001
CE130 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.25 | 22.2 |  | 22.202 | 22.2 | 22.2
CE140 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.25 | 22.2 |  | 22.202 | 22.2 | 22.2
CE150 | 22.3333 | 22.3 | 22.2 | 22.2 | 23.28 | 22.2 |  | 22.235 | 22.2 | 22.2002
CE160 | 26.7222 | 26.8 | 26.7 | 26.7 | 27.61 | 26.7 |  | 26.735 | 26.7 | 26.7005
CE165 | 23.4444 | 23.4 | 22.2 | 23.3 | 24.48 | 23.3 |  | 23.335 | 23.3 | 23.3004
CE170 | 22.2222 | 22.2 | 22.2 | 22.2 | 22.67 | 22.2 |  | 22.214 | 22.2 | 22.2002
CE180 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.79 | 22.2 |  | 22.214 | 22.2 | 22.2002
CE185 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.61 | 22.2 |  | 22.214 | 22.2 | 22.2001
CE190 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.25 | 22.2 |  | 22.202 | 22.2 | 22.2
CE195 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.26 | 22.2 |  | 22.202 | 22.2 | 22.2
CE200 | 26.7778 | 26.8 | 26.7 | 26.7339 | 26.73 | 26.7 |  | 26.713 | 26.7 | 26.7005
Max Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 0.0074 | 0.0076 | 0.00699 | 0.0075036 | 0.007509 | 0.0074274 |  | 0.007339 | 0.0075 | 0.0074747
CE110 | 0.0064 | 0.0071 | 0.00699 | 0.0065938 | 0.006631 | 0.0065187 |  | 0.006411 | 0.0066 | 0.0065837
CE120 | 0.0078 | 0.0078 | 0.007 | 0.0079506 | 0.007952 | 0.0078783 |  | 0.007873 | 0.008 | 0.0080404
CE130 | 0.0073 | 0.0076 | 0.00691 | 0.0075036 | 0.007519 | 0.0074274 |  | 0.007339 | 0.0075 | 0.0074771
CE140 | 0.0064 | 0.0071 | 0.00692 | 0.0065938 | 0.006594 | 0.0065187 |  | 0.006402 | 0.0065 | 0.0065865
CE150 | 0.0083 | 0.0082 | 0.00853 | 0.0083236 | 0.008566 | 0.0082272 |  | 0.008212 | 0.0084 | 0.0084444
CE160 | 0.0099 | 0.0098 | 0.0101 | 0.010069 | 0.01029 | 0.009969 |  | 0.009948 | 0.0103 | 0.010307
CE165 | 0.0092 | 0.0091 | 0.00985 | 0.0093021 | 0.009553 | 0.0092694 |  | 0.00921 | 0.0094 | 0.0094184
CE170 | 0.0105 | 0.0105 | 0.0107 | 0.010471 | 0.01065 | 0.010367 |  | 0.010454 | 0.106 | 0.010593
CE180 | 0.0165 | 0.0167 | 0.0164 | 0.01631 | 0.01679 | 0.01619 |  | 0.016237 | 0.0165 | 0.016224
CE185 | 0.0163 | 0.0166 | 0.0171 | 0.016151 | 0.01648 | 0.016056 |  | 0.016065 | 0.0163 | 0.016096
CE190 | 0.0161 | 0.0164 | 0.0161 | 0.015921 | 0.01595 | 0.015796 |  | 0.015897 | 0.016 | 0.015913
CE195 | 0.0156 | 0.0159 | 0.0165 | 0.01547 | 0.01551 | 0.015368 |  | 0.015444 | 0.0156 | 0.015494
CE200 | 0.0111 | 0.011 | 0.0115 | 0.011281 | 0.01128 | 0.011129 |  | 0.011099 | 0.0115 | 0.01149
Minimum COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 2.404 | 2.4287 | 2.39 | 2.4017 | 2.4184 | 2.3889 |  | 2.389 | 2.39 | 2.4005
CE110 | 3.413 | 3.4566 | 3.322 | 3.4087 | 3.419 | 3.3795 |  | 3.377 | 3.38 | 3.3954
CE120 | 3.621 | 3.6124 | 3.583 | 3.6054 | 3.6095 | 3.5865 |  | 3.593 | 3.59 | 3.6019
CE130 | 1.944 | 1.956 | 1.85 | 1.9198 | 1.6737 | 1.8895 |  | 1.908 | 1.91 | 1.8999
CE140 | 2.828 | 2.8958 | 2.68 | 2.7974 | 2.3127 | 2.7502 |  | 2.77 | 2.77 | 2.7656
CE150 | 3.691 | 3.6652 | 3.62 | 3.6496 | 3.6611 | 3.6273 |  | 3.626 | 3.62 | 3.637
CE160 | 3.944 | 3.8641 | 3.83 | 3.8452 | 3.8212 | 3.8329 |  | 3.837 | 3.83 | 3.8417
CE165 | 2.981 | 2.9498 | 2.92 | 2.9257 | 2.9336 | 2.9295 |  | 2.926 | 2.91 | 2.9255
CE170 | 3.471 | 3.4386 | 3.38 | 3.3944 | 3.3167 | 3.3672 |  | 3.385 | 3.38 | 3.3713
CE180 | 4.014 | 4.0798 | 4.04 | 4.0472 | 4.028 | 4.0423 |  | 4.044 | 4.03 | 3.9865
CE185 | 2.815 | 2.871 | 2.84 | 2.8512 | 2.8362 | 2.8458 |  | 2.848 | 2.84 | 2.8049
CE190 | 3.424 | 3.475 | 3.37 | 3.4096 | 3.1652 | 3.3865 |  | 3.409 | 3.41 | 3.3182
CE195 | 2.321 | 2.3497 | 2.29 | 2.3158 | 2.2587 | 2.2944 |  | 2.314 | 2.31 | 2.2496
CE200 | 3.698 | 3.6716 | 3.61 | 3.6102 | 3.6102 | 3.6206 |  | 3.617 | 3.61 | 3.6271
Min IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.09 | 22.2 |  | 22.197 | 22.2 | 22.1997
CE110 | 22.2778 | 22.3 | 22.2 | 22.2 | 21.98 | 22.2 |  | 22.193 | 22.2 | 22.1997
CE120 | 26.7222 | 26.8 | 26.7 | 26.7 | 26.17 | 26.7 |  | 26.689 | 26.7 | 26.6997
CE130 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.03 | 22.2 |  | 22.172 | 22.2 | 22.2
CE140 | 22.1111 | 22.1 | 22.2 | 22.2 | 20.76 | 22.2 |  | 22.168 | 22.2 | 22.2
CE150 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.06 | 22.2 |  | 22.197 | 22.2 | 22.1996
CE160 | 26.7222 | 26.8 | 26.7 | 26.7 | 26.39 | 26.7 |  | 26.693 | 26.7 | 26.6993
CE165 | 23.4444 | 23.4 | 22.2 | 23.3 | 23.26 | 23.3 |  | 23.299 | 23.3 | 23.2994
CE170 | 22.2222 | 22.2 | 22.2 | 22.2 | 21.57 | 22.2 |  | 22.185 | 22.2 | 22.1997
CE180 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.01 | 22.2 |  | 22.196 | 22.2 | 22.1997
CE185 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.13 | 22.2 |  | 22.198 | 22.2 | 22.1998
CE190 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.63 | 22.2 |  | 22.186 | 22.2 | 22.2
CE195 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.76 | 22.2 |  | 22.188 | 22.2 | 22.2
CE200 | 26.7778 | 26.8 | 26.7 | 26.7339 | 26.73 | 26.7 |  | 26.713 | 26.7 | 26.6993
Min Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
CE100 | 0.0074 | 0.0076 | 0.00684 | 0.0075036 | 0.007509 | 0.0074274 |  | 0.007339 | 0.0075 | 0.0074708
CE110 | 0.0064 | 0.007 | 0.00684 | 0.0065938 | 0.006631 | 0.0065187 |  | 0.006411 | 0.0066 | 0.0065804
CE120 | 0.0078 | 0.0078 | 0.007 | 0.0079506 | 0.007952 | 0.0078783 |  | 0.007873 | 0.008 | 0.0080362
CE130 | 0.0073 | 0.0076 | 0.00684 | 0.0075036 | 0.007519 | 0.0074274 |  | 0.007339 | 0.0075 | 0.0074725
CE140 | 0.0064 | 0.007 | 0.00684 | 0.0065938 | 0.006594 | 0.0065187 |  | 0.006402 | 0.0065 | 0.0065822
CE150 | 0.0083 | 0.0082 | 0.00853 | 0.0083236 | 0.008454 | 0.0082272 |  | 0.008209 | 0.0083 | 0.0083341
CE160 | 0.0098 | 0.0097 | 0.0101 | 0.010069 | 0.01018 | 0.009969 |  | 0.009944 | 0.0101 | 0.010169
CE165 | 0.0092 | 0.009 | 0.00984 | 0.0093021 | 0.009434 | 0.0092694 |  | 0.009207 | 0.0093 | 0.0092952
CE170 | 0.0105 | 0.0104 | 0.0107 | 0.010471 | 0.0104 | 0.010367 |  | 0.010448 | 0.106 | 0.010472
CE180 | 0.0163 | 0.0165 | 0.0164 | 0.01631 | 0.01613 | 0.01619 |  | 0.016222 | 0.0162 | 0.016057
CE185 | 0.0161 | 0.0163 | 0.017 | 0.016151 | 0.01608 | 0.016056 |  | 0.016052 | 0.0161 | 0.015922
CE190 | 0.0158 | 0.0161 | 0.0161 | 0.015921 | 0.01546 | 0.015796 |  | 0.015885 | 0.016 | 0.015683
CE195 | 0.0153 | 0.0156 | 0.0164 | 0.01547 | 0.01514 | 0.015368 |  | 0.015434 | 0.0156 | 0.015281
CE200 | 0.011 | 0.0109 | 0.0115 | 0.011281 | 0.01128 | 0.011129 |  | 0.011099 | 0.0113 | 0.011342
Delta Calcs
(Max - Min)/Mean COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
E100 | 0.0012467 | 0.0015062 | 0.00083717 | 0 | 0 | 0 |  | 0.00012552 | 0 | 0.0026072
E110 | 0.0011714 | 0.0017378 | 0.010473 | 0 | 0.010592 | 0 |  | 0.00038462 | 0 | 0.0027731
E120 | 0.0011041 | 0.00079758 | 0.0036212 | 0 | 0.012271 | 0 |  | 0.00030641 | 0 | 0.0027415
E130 | 0.0087046 | 0.012602 | 0.03824 | 0 | 0.17198 | 0 |  | -5.2356e-05 | 0 | 0.0037428
E140 | 0.018921 | 0.010989 | 0.055962 | 0 | 0.20433 | 0 |  | 3.6101e-05 | 0 | 0.0038004
E150 | 0.0048649 | 0.0014674 | 0.0027548 | 0 | 0.0092759 | 0 |  | 0.00096419 | 0.0027624 | 0.010553
E160 | 0.0032911 | 0.0010614 | 0.0052083 | 0 | 0.010193 | 0 |  | 0.00026042 | 0.0026042 | 0.011024
E165 | 0.0026798 | 0.0012002 | 0.0034247 | 0 | 0.0084429 | 0 |  | 0.00030717 | 0.010274 | 0.011921
E170 | 0.0040265 | 0.0021466 | 0.0058997 | 0 | 0.043444 | 0 |  | 0.00026549 | 0 | 0.015183
E180 | 0.009687 | 0.0023307 | 0.0024752 | 0 | 0.011687 | 0 |  | 4.9505e-05 | 0.0049505 | 0.029331
E185 | 0.010273 | 0.0023597 | 0.0035088 | 0 | 0.0091078 | 0 |  | 0.00017544 | 0.0070175 | 0.034252
E190 | 0.018802 | 0.0071705 | 0.02346 | 0 | 0.10066 | 0 |  | -8.7977e-05 | 0 | 0.039563
E195 | 0.016688 | 0.0078108 | 0.017316 | 0 | 0.08606 | 0 |  | 0.00012987 | 0 | 0.043389
E200 | 0.0051241 | -1.2839e-05 | 0 | 0 | 0 | 0 |  | 8.2873e-05 | 0.0055249 | 0.011968
(Max - Min)/Mean IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
E100 | 0 | 0 | 0 | 0 | 0.049482 | 0 |  | 0.0017105 | 0 | 1.9369e-05
E110 | 0 | 0 | 0 | 0 | 0.047948 | 0 |  | 0.0018907 | 0 | 2.4324e-05
E120 | 0 | 0 | 0 | 0 | 0.077183 | 0 |  | 0.0017221 | 0 | 1.4232e-05
E130 | 0 | 0 | 0 | 0 | 0.056383 | 0 |  | 0.0013521 | 0 | 2.2523e-06
E140 | 0 | 0 | 0 | 0 | 0.069271 | 0 |  | 0.0015326 | 0 | 1.3514e-06
E150 | 0 | 0 | 0 | 0 | 0.053799 | 0 |  | 0.0017105 | 0 | 2.7027e-05
E160 | 0 | 0 | 0 | 0 | 0.045194 | 0 |  | 0.0015722 | 0 | 4.2697e-05
E165 | 0 | 0 | 0 | 0 | 0.051303 | 0 |  | 0.0015439 | 0 | 4.3777e-05
E170 | 0 | 0 | 0 | 0 | 0.049736 | 0 |  | 0.0013064 | 0 | 2.3423e-05
E180 | 0 | 0 | 0 | 0 | 0.034924 | 0 |  | 0.00081063 | 0 | 2.027e-05
E185 | 0 | 0 | 0 | 0 | 0.021459 | 0 |  | 0.00072053 | 0 | 1.4865e-05
E190 | 0 | 0 | 0 | 0 | 0.02825 | 0 |  | 0.00072092 | 0 | 4.0541e-06
E195 | 0 | 0 | 0 | 0 | 0.022716 | 0 |  | 0.00063077 | 0 | 4.0541e-06
E200 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4.2322e-05
(Max - Min)/Mean Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
E100 | 0 | 0 | 0.021708 | 0 | 0 | 0 |  | 0 | 0 | 0.00051398
E110 | 0 | 0.014226 | 0.021676 | 0 | 0 | 0 |  | 0 | 0 | 0.00049972
E120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.00052403
E130 | 0 | 0 | 0.01013 | 0 | 0 | 0 |  | 0 | 0 | 0.00061108
E140 | 0 | 0.014164 | 0.011561 | 0 | 0 | 0 |  | 0 | 0 | 0.00064275
E150 | 0 | 0 | 0 | 0 | 0.013153 | 0 |  | 0.00036541 | 0.012048 | 0.013105
E160 | 0.010101 | 0.010308 | 0 | 0 | 0.010747 | 0 |  | 0.00040217 | 0.019608 | 0.013391
E165 | 0 | 0.011106 | 0.0010152 | 0 | 0.012512 | 0 |  | 0.0003258 | 0.010753 | 0.013116
E170 | 0 | 0.0095289 | 0 | 0 | 0.023752 | 0 |  | 0.00057411 | 0 | 0.011456
E180 | 0.012195 | 0.012038 | 0 | 0 | 0.040234 | 0 |  | 0.00092421 | 0.018293 | 0.010319
E185 | 0.012346 | 0.018247 | 0.005848 | 0 | 0.024571 | 0 |  | 0.00080951 | 0.012346 | 0.010816
E190 | 0.018868 | 0.018457 | 0 | 0 | 0.031196 | 0 |  | 0.00075514 | 0 | 0.0145
E195 | 0.019355 | 0.01903 | 0.0060976 | 0 | 0.024142 | 0 |  | 0.00064771 | 0 | 0.013755
E200 | 0.009009 | 0.0091467 | 0 | 0 | 0 | 0 |  | 0 | 0.017544 | 0.012859
Delta COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
E110-E100 | 1.0082 | 1.0285 | 0.953 | 1.0069 | 1.0087 | 0.99059 | 0.99 | 0.99 | 0.99 | 0.99667
E120-E110 | 0.20837 | 0.155 | 0.248 | 0.19677 | 0.20416 | 0.20704 | 0.21 | 0.21 | 0.21 | 0.20683
E120-E100 | 1.2166 | 1.1835 | 1.201 | 1.2037 | 1.2129 | 1.1976 | 1.2 | 1.2 | 1.2 | 1.2035
E130-E100 | -0.45341 | -0.4552 | -0.48 | -0.48198 | -0.50212 | -0.49937 | -0.48 | -0.48 | -0.48 | -0.50017
E140-E130 | 0.901 | 0.9399 | 0.825 | 0.87767 | 0.88334 | 0.86071 | 0.86 | 0.86 | 0.86 | 0.86754
E140-E110 | -0.56063 | -0.5438 | -0.608 | -0.61124 | -0.6275 | -0.62925 | -0.61 | -0.61 | -0.61 | -0.6293
E150-E110 | 0.28537 | 0.2086 | 0.288 | 0.24097 | 0.24631 | 0.24783 | 0.25 | 0.25 | 0.24 | 0.25377
E160-E150 | 0.25 | 0.1983 | 0.21 | 0.19555 | 0.18654 | 0.20563 | 0.21 | 0.21 | 0.22 | 0.20665
E165-E160 | -0.96474 | -0.9144 | -0.92 | -0.91948 | -0.91505 | -0.90343 | -0.91 | -0.91 | -0.92 | -0.91963
E170-E150 | -0.223 | -0.2252 | -0.24 | -0.25525 | -0.27013 | -0.26014 | -0.24 | -0.24 | -0.24 | -0.25935
E180-E150 | 0.326 | 0.4167 | 0.41 | 0.39757 | 0.38162 | 0.41502 | 0.41 | 0.41 | 0.42 | 0.38877
E180-E170 | 0.549 | 0.6419 | 0.65 | 0.65282 | 0.65175 | 0.67516 | 0.65 | 0.65 | 0.66 | 0.64811
E185-E180 | -1.203 | -1.2098 | -1.19 | -1.196 | -1.1976 | -1.1965 | -1.19 | -1.19 | -1.19 | -1.1911
E190-E180 | -0.569 | -0.5977 | -0.63 | -0.63762 | -0.65027 | -0.65583 | -0.63 | -0.63 | -0.63 | -0.64902
E190-E140 | 0.603 | 0.5714 | 0.676 | 0.61216 | 0.60515 | 0.63627 | 0.64 | 0.64 | 0.64 | 0.62282
E195-E190 | -1.12 | -1.1267 | -1.1 | -1.0938 | -1.0994 | -1.0921 | -1.1 | -1.1 | -1.1 | -1.0909
E195-E185 | -0.48603 | -0.5146 | -0.54 | -0.53547 | -0.55209 | -0.55141 | -0.54 | -0.54 | -0.54 | -0.54881
E195-E130 | 0.384 | 0.3846 | 0.401 | 0.39602 | 0.3891 | 0.40487 | 0.4 | 0.4 | 0.4 | 0.39945
E200-E100 | 1.3016 | 1.2373 | 1.221 | 1.2084 | 1.1918 | 1.2317 | 1.23 | 1.23 | 1.23 | 1.2431
Delta Qtot
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | E+
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | NREL
E110-E100 | -454 | -459.621 | -441 | -455.3055 | -449.9711 | -454.3131 | -453.6 | -453.2 | -454 | -450.9597
E120-E110 | -62 | -50.092 | -77 | -59.6584 | -60.3021 | -63.5575 | -66.2 | -66.4 | -65 | -62.6782
E120-E100 | -516 | -509.713 | -518 | -514.9639 | -510.2732 | -517.8706 | -519.8 | -519.6 | -519 | -513.638
E130-E100 | -1413 | -1415.398 | -1421 | -1413.5415 | -1401.8208 | -1419.9663 | -1421.3 | -1421.1 | -1421 | -1411.4319
E140-E130 | -40 | -40.411 | -40 | -40.9605 | -41.4733 | -41.5864 | -41 | -41.2 | -42 | -40.6934
E140-E110 | -999 | -996.188 | -1020 | -999.1966 | -993.323 | -1007.2396 | -1008.7 | -1009.1 | -1009 | -1001.1655
E150-E110 | 118 | 141.228 | 118 | 132.0944 | 129.6472 | 130.2551 | 129.3 | 129.1 | 131 | 128.04
E160-E150 | -76 | -64.794 | -68 | -62.3216 | -58.7295 | -66.05 | -67.2 | -67.6 | -68 | -65.3743
E165-E160 | 363 | 361.817 | 362 | 362.977 | 357.0433 | 357.3902 | 360.4 | 360.7 | 362 | 359.3413
E170-E150 | -563 | -573.348 | -569 | -563.1461 | -555.7842 | -565.3727 | -568.8 | -568.7 | -570 | -561.7369
E180-E150 | -103 | -125.315 | -125 | -117.7844 | -111.5753 | -123.824 | -124.2 | -124.6 | -125 | -115.1083
E180-E170 | 460 | 448.033 | 444 | 445.3617 | 444.2089 | 441.5487 | 444.6 | 444.1 | 445 | 446.6285
E185-E180 | 467 | 464.046 | 461 | 460.255 | 458.3596 | 461.9737 | 461.1 | 461 | 461 | 458.3877
E190-E180 | -920 | -916.89 | -918 | -917.2731 | -914.9174 | -917.493 | -918.2 | -917.7 | -919 | -917.6654
E190-E140 | 94 | 95.211 | 95 | 96.2334 | 96.4774 | 96.1777 | 95.6 | 95.9 | 96 | 96.4318
E195-E190 | 86 | 84.7 | 86 | 85.7346 | 86.4597 | 86.9875 | 85.9 | 85.8 | 86 | 85.8951
E195-E185 | -1301 | -1296.236 | -1293 | -1291.7935 | -1286.8173 | -1292.4792 | -1293.4 | -1292.9 | -1294 | -1290.158
E195-E130 | 140 | 139.5 | 141 | 141.0075 | 141.4638 | 141.5788 | 140.5 | 140.5 | 140 | 141.6336
E200-E100 | -79 | -52.603 | -66 | -42.2735 | -31.9443 | -54.7376 | -53.4 | -53.5 | -54 | -55.4338
Del Qcomp | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | E+
E110-E100 | -428 | -441.592 | -419 | -431.8474 | -426.8936 | -430.9138 | -429.8 | -429.5 | -430
E120-E110 | -45 | -15.798 | -59 | -43.4717 | -43.903 | -47.0715 | -50.1 | -50.2 | -49
E120-E100 | -473 | -457.39 | -478 | -475.319 | -470.7965 | -477.9853 | -479.9 | -479.7 | -479
E130-E100 | -1218 | -1214.26 | -1224 | -1217.5188 | -1207.8769 | -1223.5648 | -1224.6 | -1224.6 | -1224
E140-E130 | -37 | -38.399 | -37 | -37.8005 | -38.2753 | -38.3628 | -37.9 | -37.9 | -38
E140-E110 | -827 | -811.067 | -842 | -823.472 | -819.2586 | -831.0138 | -832.7 | -833 | -832
E150-E110 | 99 | 141.228 | 100 | 112.7146 | 110.9181 | 111.0199 | 110 | 109.8 | 111
E160-E150 | -56 | -44.419 | -50 | -45.0374 | -42.3919 | -48.5466 | -49.8 | -50.1 | -50
E165-E160 | 330 | 328.567 | 332 | 333.2246 | 328.108 | 328.3094 | 330.8 | 331.1 | 333
E170-E150 | -459 | -468.135 | -469 | -463.6356 | -458.1666 | -465.9883 | -469.2 | -469.1 | -469
E180-E150 | -70 | -92.832 | -91 | -84.887 | -80.3105 | -90.836 | -91.2 | -91.5 | -91
E180-E170 | 389 | 375.303 | 378 | 378.7486 | 377.8561 | 375.1523 | 378 | 377.6 | 378
E185-E180 | 432 | 428.419 | 431 | 429.7507 | 427.9509 | 431.6779 | 430.6 | 430.5 | 431
E190-E180 | -774 | -774.839 | -770 | -769.6356 | -767.9826 | -769.6508 | -770.4 | -770 | -771
E190-E140 | 82 | 84.624 | 81 | 81.6639 | 81.8837 | 81.5469 | 81.1 | 81.3 | 81
E195-E190 | 79 | 79.444 | 79 | 78.9721 | 79.6337 | 80.1527 | 79.2 | 79.1 | 79
E195-E185 | -1127 | -1123.814 | -1122 | -1120.4142 | -1116.2999 | -1121.176 | -1121.8 | -1121.4 | -1123
E195-E130 | 124 | 125.669 | 123 | 122.8356 | 123.242 | 123.3368 | 122.4 | 122.5 | 122
E200-E100 | -93 | -58.431 | -79 | -58.3094 | -49.8691 | -70.0317 | -68.8 | -68.9 | -69
Del Q IDfan | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | E+
E110-E100 | -19 | -12.268 | -15 | -15.9627 | -15.7035 | -15.9226 | -16.2 | -16.1 | -16 | -16.0147
E120-E110 | -12 | -23.336 | -12 | -11.0148 | -11.1592 | -11.2183 | -11 | -11 | -11 | -11.154
E120-E100 | -31 | -35.604 | -27 | -26.9774 | -26.8627 | -27.1409 | -27.2 | -27.1 | -27 | -27.1687
E130-E100 | -133 | -136.869 | -134 | -133.3883 | -131.9736 | -133.646 | -133.8 | -133.7 | -134 | -133.2976
E140-E130 | -2 | -1.369 | -2 | -2.1503 | -2.1761 | -2.1936 | -2.2 | -2.2 | -2 | -2.1553
E140-E110 | -116 | -125.97 | -121 | -119.5759 | -118.4462 | -119.917 | -119.8 | -119.8 | -120 | -119.4381
E150-E110 | 14 | 0 | 12 | 13.1873 | 12.7446 | 13.0891 | 13.2 | 13.2 | 13 | 12.711
E160-E150 | -15 | -13.865 | -12 | -11.7613 | -11.1173 | -11.9106 | -11.9 | -11.9 | -12 | -11.9732
E165-E160 | 24 | 22.626 | 21 | 20.246 | 19.6897 | 19.7887 | 20.1 | 20.1 | 20 | 20.2603
E170-E150 | -73 | -71.595 | -68 | -67.7141 | -66.4261 | -67.6284 | -67.9 | -67.9 | -68 | -67.2399
E180-E150 | -24 | -22.104 | -22 | -22.3857 | -21.2749 | -22.4474 | -22.5 | -22.6 | -23 | -21.8663
E180-E170 | 49 | 49.491 | 46 | 45.3284 | 45.1513 | 45.181 | 45.4 | 45.3 | 45 | 45.3736
E185-E180 | 25 | 24.243 | 20 | 20.7574 | 20.6923 | 20.6154 | 20.8 | 20.8 | 21 | 20.7271
E190-E180 | -98 | -96.662 | -101 | -100.4635 | -99.9852 | -100.6027 | -100.6 | -100.5 | -100 | -100.3495
E190-E140 | 8 | 7.204 | 10 | 9.9142 | 9.9306 | 9.9559 | 9.9 | 9.9 | 10 | 9.9333
E195-E190 | 4 | 3.577 | 5 | 4.6017 | 4.6449 | 4.6509 | 4.6 | 4.6 | 5 | 4.627
E195-E185 | -119 | -117.328 | -116 | -116.6191 | -116.0326 | -116.5672 | -116.8 | -116.7 | -116 | -116.4496
E195-E130 | 10 | 9.412 | 13 | 12.3655 | 12.3994 | 12.4132 | 12.3 | 12.3 | 13 | 12.405
E200-E100 | 10 | 3.966 | 9 | 10.9119 | 12.1975 | 10.4073 | 10.5 | 10.6 | 10 | 9.8015
Del Q ODfan | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | E+
E110-E100 | -7 | -5.761 | -7 | -7.4954 | -7.374 | -7.4767 | -7.5 | -7.5 | -8
E120-E110 | -5 | -10.958 | -6 | -5.172 | -5.24 | -5.2677 | -5.2 | -5.2 | -5
E120-E100 | -12 | -16.719 | -13 | -12.6674 | -12.6139 | -12.7444 | -12.7 | -12.7 | -13
E130-E100 | -62 | -64.269 | -63 | -62.6344 | -61.9703 | -62.7555 | -62.8 | -62.8 | -63
E140-E130 | -1 | -0.643 | -1 | -1.0097 | -1.0218 | -1.03 | -1 | -1 | -1
E140-E110 | -56 | -59.151 | -57 | -56.1487 | -55.6182 | -56.3088 | -56.3 | -56.3 | -56
E150-E110 | 5 | 0 | 5 | 6.1925 | 5.9844 | 6.1462 | 6.2 | 6.1 | 6
E160-E150 | -5 | -6.51 | -5 | -5.5228 | -5.2203 | -5.5928 | -5.6 | -5.5 | -5
E165-E160 | 9 | 10.624 | 9 | 9.5064 | 9.2456 | 9.2921 | 9.4 | 9.4 | 9
E170-E150 | -31 | -33.618 | -32 | -31.7964 | -31.1915 | -31.756 | -31.9 | -31.8 | -32
E180-E150 | -9 | -10.379 | -10 | -10.5117 | -9.99 | -10.5405 | -10.6 | -10.5 | -10
E180-E170 | 22 | 23.239 | 22 | 21.2847 | 21.2015 | 21.2154 | 21.3 | 21.3 | 22
E185-E180 | 10 | 11.384 | 9 | 9.7468 | 9.7164 | 9.6803 | 9.7 | 9.7 | 9
E190-E180 | -48 | -45.389 | -47 | -47.1741 | -46.9496 | -47.2395 | -47.2 | -47.2 | -48
E190-E140 | 4 | 3.383 | 5 | 4.6553 | 4.6631 | 4.6749 | 4.7 | 4.7 | 4
E195-E190 | 3 | 1.679 | 2 | 2.1608 | 2.1811 | 2.1839 | 2.1 | 2.1 | 3
E195-E185 | -55 | -55.094 | -54 | -54.7601 | -54.4849 | -54.7359 | -54.8 | -54.8 | -54
E195-E130 | 6 | 4.419 | 6 | 5.8064 | 5.8223 | 5.8288 | 5.8 | 5.8 | 6
E200-E100 | 4 | 1.862 | 4 | 5.124 | 5.7274 | 4.8869 | 5 | 5 | 5
Del Q coil,t | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | E+
E110-E100 | -38.3939 | -37.89 | -34 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1 | -35 | -34.5809
E120-E110 | -16.4127 | -40.1 | -17 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8 | -16 | -16.1629
E120-E100 | -54.8066 | -77.99 | -51 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9 | -51 | -50.7438
E130-E100 | -3578.8394 | -3625.692 | -3581 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2 | -3581 | -3580.6485
E140-E130 | -20.5158 | -20.248 | -21 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9 | -21 | -20.7191
E140-E110 | -3560.9613 | -3608.05 | -3568 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568 | -3567 | -3566.7867
E150-E110 | 771.9812 | 739.2 | 751 | 752.3846 | 751.7923 | 752.2836 | 752.4 | 753 | 752 | 745.6537
E160-E150 | -19.0504 | -26.402 | -17 | -16.9277 | -16.1469 | -16.9825 | -17.1 | -18.4 | -16 | -17.6739
E165-E160 | 40.4455 | 51.08 | 38 | 37.0003 | 36.2193 | 36.4531 | 37 | 38 | 37 | 37.6106
E170-E150 | -2291.0317 | -2316.723 | -2285 | -2285.3107 | -2283.394 | -2285.1847 | -2285.5 | -2285.8 | -2284 | -2283.8549
E180-E150 | 7.034 | -32.796 | -22 | -22.3843 | -20.9286 | -22.2623 | -22.5 | -24.5 | -22 | -27.5145
E180-E170 | 2298.0657 | 2283.927 | 2263 | 2262.9264 | 2262.4654 | 2262.9224 | 2263 | 2261.3 | 2262 | 2256.3404
E185-E180 | 48.0657 | 54.91 | 40 | 39.9168 | 39.8433 | 39.858 | 40 | 40.1 | 12 | 41.3818
E190-E180 | -3956.0375 | -3937.377 | -3918 | -3917.4227 | -3916.4296 | -3917.7372 | -3917.6 | -3916.1 | -3917 | -3906.9062
E190-E140 | 383.939 | 377.077 | 379 | 379.514 | 379.106 | 379.5607 | 379.4 | 380.4 | 380 | 378.0197
E195-E190 | 23.1536 | 22.633 | 24 | 23.7619 | 23.6687 | 23.8465 | 23.9 | 23.5 | 24 | 23.4
E195-E185 | -3980.9496 | -3969.654 | -3934 | -3933.5775 | -3932.6042 | -3933.7487 | -3933.7 | -3932.7 | -3905 | -3924.888
E195-E130 | 386.5768 | 379.462 | 382 | 381.9655 | 381.5695 | 382.0203 | 381.9 | 382 | 383 | 380.7006
E200-E100 | 1728.0188 | 1692.73 | 1636 | 1697.8282 | 1699.6157 | 1697.4409 | 1697.4 | 1697.4 | 1698 | 1686.8281
Del Q coil,s | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | E+
E110-E100 | -38.3939 | -37.89 | -34 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1 | -35 | -34.5797
E120-E110 | -16.4127 | -40.1 | -17 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8 | -16 | -16.1635
E120-E100 | -54.8066 | -77.99 | -51 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9 | -51 | -50.7431
E130-E100 | -3578.8394 | -3625.692 | -3581 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2 | -3581 | -3580.6444
E140-E130 | -20.5158 | -20.248 | -21 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9 | -21 | -20.719
E140-E110 | -3560.9613 | -3608.05 | -3568 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568 | -3567 | -3566.7837
E150-E110 | 30.4807 | 0 | 12 | 13.1846 | 12.5854 | 13.088 | 13.2 | 13.7 | 13 | 12.9618
E160-E150 | -16.9988 | -26.402 | -17 | -16.9277 | -16.1348 | -17.0265 | -17.1 | -18.2 | -17 | -16.9902
E165-E160 | 39.5662 | 51.08 | 37 | 37.0003 | 36.2248 | 36.4472 | 37 | 37.8 | 37 | 36.4558
E170-E150 | -2288.3939 | -2316.723 | -2285 | -2285.3107 | -2283.3986 | -2285.3048 | -2285.5 | -2285.9 | -2285 | -2284.806
E180-E150 | -2179.3669 | -2250.396 | -2240 | -2239.9843 | -2238.5215 | -2240.5379 | -2240.1 | -2241.3 | -2241 | -2238.6808
E180-E170 | 109.027 | 66.327 | 45 | 45.3264 | 44.8771 | 44.7669 | 45.4 | 44.6 | 44 | 46.1251
E185-E180 | 46.0141 | 54.91 | 40 | 39.9168 | 39.8232 | 39.8069 | 40 | 40 | 11 | 39.2553
E190-E180 | -1394.49 | -1350.177 | -1330 | -1330.2227 | -1329.2766 | -1329.9815 | -1330.4 | -1329.8 | -1329 | -1330.9807
E190-E140 | 17.585 | 7.477 | 10 | 9.914 | 9.4592 | 9.8452 | 9.8 | 10.6 | 10 | 10.0839
E195-E190 | 22.8605 | 22.633 | 24 | 23.7619 | 23.71 | 23.8326 | 23.9 | 23.7 | 24 | 23.1909
E195-E185 | -1417.6436 | -1382.454 | -1346 | -1346.3775 | -1345.3897 | -1345.9558 | -1346.5 | -1346.1 | -1316 | -1347.0452
E195-E130 | 19.9297 | 9.862 | 13 | 12.3655 | 11.964 | 12.2909 | 12.3 | 12.4 | 13 | 12.5558
E200-E100 | 508.7925 | 471.706 | 415 | 476.8042 | 478.5917 | 476.3346 | 476.4 | 476.4 | 476 | 476.6119
Del Qcoil,lat | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | E+
E110-E100 | 0 | 0 | 0 | 0 | -3.0447e-14 | 0 | 0 | 0 | 0 | -0.0012361
E120-E110 | 0 | 0 | 0 | 0 | 1.1191e-15 | 0 | 0 | 0 | 0 | 0.00051944
E120-E100 | 0 | 0 | 0 | 0 | -2.9328e-14 | 0 | 0 | 0 | 0 | -0.00071667
E130-E100 | 0 | 0 | 0 | 0 | -1.7231e-15 | 0 | 0 | 0 | 0 | -0.0041511
E140-E130 | 0 | 0 | 0 | 0 | -3.169e-14 | 0 | 0 | 0 | 0 | -0.00011694
E140-E110 | 0 | 0 | 0 | 0 | -2.9665e-15 | 0 | 0 | 0 | 0 | -0.0030319
E150-E110 | 741.5006 | 739.2 | 739 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4 | 739 | 732.6919
E160-E150 | -2.0516 | 0 | 0 | 0 | -0.01221 | 0.043984 | 0 | -0.3 | 1 | -0.68366
E165-E160 | 0.87925 | 0 | 0 | 0 | -0.00548 | 0.005862 | 0 | 0.2 | 0 | 1.1548
E170-E150 | -2.6377 | 0 | 0 | 0 | 0.00465 | 0.12011 | 0 | 0 | 1 | 0.95111
E180-E150 | 2186.4009 | 2217.6 | 2218 | 2217.6 | 2217.5924 | 2218.2757 | 2217.6 | 2216.7 | 2219 | 2211.1664
E180-E170 | 2189.0387 | 2217.6 | 2218 | 2217.6 | 2217.5877 | 2218.1556 | 2217.6 | 2216.7 | 2218 | 2210.2153
E185-E180 | 2.0516 | 0 | 0 | 0 | 0.02022 | 0.051109 | 0 | 0.1 | 1 | 2.1265
E190-E180 | -2561.5475 | -2587.2 | -2587 | -2587.2 | -2587.1524 | -2587.7557 | -2587.2 | -2586.3 | -2588 | -2575.9255
E190-E140 | 366.354 | 369.6 | 370 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8 | 370 | 367.9358
E195-E190 | 0.29308 | 0 | 0 | 0 | -0.041346 | 0.013833 | 0 | -0.2 | 0 | 0.20914
E195-E185 | -2563.306 | -2587.2 | -2587 | -2587.2 | -2587.214 | -2587.793 | -2587.2 | -2586.6 | -2589 | -2577.8429
E195-E130 | 366.6471 | 369.6 | 370 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6 | 370 | 368.1448
E200-E100 | 1219.2263 | 1221 | 1221 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221 | 1222 | 1210.2163

## Q
RESULTS.XLS5-3, October 15, 2002 | [5 empty] | SEE SHEET 'A' FOR INSTRUCTIONS
Space Cooling Electricity Consumption
Energy Consumption, Total (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
CE100 | 1531 | 1530 | 1520.817 | 1519 | 1520.0282 | 1522.2661 | 1511.9369 | 1511.9369 | 1531 | 1.246% | 1530.548 | 1530.8 | 1530.6
CE110 | 1077 | 1089 | 1061.196 | 1065 | 1069.0685 | 1066.9607 | 1061.9658 | 1061.196 | 1089 | 2.583% | 1076.2349 | 1077.2 | 1077.4
CE120 | 1012 | 1012 | 1011.104 | 1003 | 1006.3903 | 1007.3023 | 1001.6637 | 1001.6637 | 1012 | 1.021% | 1012.6774 | 1011 | 1011
CE130 | 110 | 109 | 105.419 | 106 | 108.5963 | 108.7246 | 110.1161 | 105.419 | 110.1161 | 4.248% | 110.5818 | 109.5 | 109.5
CE140 | 68 | 69 | 65.008 | 66 | 67.903 | 67.7641 | 68.6428 | 65.008 | 69 | 5.786% | 68.9953 | 68.5 | 68.3
CE150 | 1208 | 1207 | 1202.424 | 1183 | 1197.1085 | 1199.055 | 1191.613 | 1183 | 1208 | 2.072% | 1206.49 | 1206.5 | 1206.5
CE160 | 1140 | 1139 | 1137.63 | 1107 | 1131.7342 | 1136.7334 | 1132.8835 | 1107 | 1140 | 2.894% | 1140.44 | 1139.3 | 1138.9
CE165 | 1502 | 1501 | 1499.447 | 1470 | 1491.0755 | 1499.7105 | 1489.9268 | 1470 | 1502 | 2.136% | 1497.8302 | 1499.7 | 1499.6
CE170 | 638 | 638 | 629.076 | 620 | 635.3716 | 635.909 | 635.8287 | 620 | 638 | 2.808% | 641.1173 | 637.7 | 637.8
CE180 | 1083 | 1082 | 1077.109 | 1080 | 1082.0002 | 1081.2706 | 1080.0377 | 1077.109 | 1083 | 0.5441% | 1082.666 | 1082.3 | 1081.9
CE185 | 1544 | 1543 | 1541.155 | 1547 | 1540.3879 | 1541.5256 | 1538.3972 | 1538.3972 | 1547 | 0.5569% | 1544.6397 | 1543.4 | 1542.9
CE190 | 164 | 164 | 160.219 | 160 | 164.3348 | 163.9975 | 165.1202 | 160 | 165.1202 | 3.1% | 165.173 | 164.1 | 164.2
CE195 | 250 | 250 | 244.919 | 246 | 250.2299 | 249.7321 | 251.5799 | 244.919 | 251.5799 | 2.642% | 252.1605 | 250 | 250
CE200 | 1477 | 1464 | 1468.214 | 1440 | 1464.5945 | 1479.9926 | 1479.9926 | 1440 | 1479.9926 | 2.71% | 1475.8104 | 1477.4 | 1477.1
Energy Consumption, Compressor (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
CE100 | 1319 | 1318 | 1307.458 | 1311 |  | 1311.1661 | 1302.7258 | 1302.7258 | 1319 | 1.234% | 1318.8515 | 1319 | 1318.9
CE110 | 889 | 899 | 865.866 | 883 |  | 879.3187 | 875.8322 | 865.866 | 899 | 3.732% | 887.9378 | 889.2 | 889.4
CE120 | 840 | 840 | 850.068 | 838 |  | 835.847 | 831.9292 | 831.9292 | 850.068 | 2.157% | 840.8662 | 839.1 | 839.2
CE130 | 95 | 94 | 93.198 | 93 |  | 93.6472 | 94.8489 | 93 | 95 | 2.099% | 95.2867 | 94.4 | 94.3
CE140 | 57 | 57 | 54.799 | 56 |  | 55.8468 | 56.5735 | 54.799 | 57 | 3.867% | 56.924 | 56.5 | 56.4
CE150 | 1000 | 999 | 1007.094 | 982 |  | 992.0333 | 986.7503 | 982 | 1007.094 | 2.512% | 998.9576 | 999.2 | 999.2
CE160 | 950 | 949 | 962.675 | 926 |  | 946.9958 | 944.3585 | 926 | 962.675 | 3.859% | 950.4111 | 949.4 | 949.1
CE165 | 1283 | 1281 | 1291.242 | 1256 |  | 1280.2205 | 1272.4664 | 1256 | 1291.242 | 2.756% | 1278.7205 | 1280.2 | 1280.2
CE170 | 531 | 530 | 538.959 | 523 |  | 528.3976 | 528.5837 | 523 | 538.959 | 2.994% | 532.9693 | 530 | 530.1
CE180 | 909 | 908 | 914.262 | 912 |  | 907.1462 | 906.4398 | 906.4398 | 914.262 | 0.8614% | 908.1216 | 908 | 907.7
CE185 | 1340 | 1339 | 1342.681 | 1344 |  | 1336.897 | 1334.3908 | 1334.3908 | 1344 | 0.7172% | 1339.7996 | 1338.6 | 1338.2
CE190 | 138 | 138 | 139.423 | 138 |  | 137.5107 | 138.4572 | 137.5107 | 139.423 | 1.381% | 138.4708 | 137.6 | 137.7
CE195 | 217 | 217 | 218.867 | 217 |  | 216.4828 | 218.0909 | 216.4828 | 218.867 | 1.091% | 218.6235 | 216.8 | 216.8
CE200 | 1250 | 1239 | 1249.027 | 1218 |  | 1252.8566 | 1252.8566 | 1218 | 1252.8566 | 2.791% | 1248.8198 | 1250.2 | 1250
Energy Consumption, Supply Fan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
CE100 | 144 | 144 | 145.185 | 141 | 143.5533 | 143.6481 | 142.3625 | 141 | 145.185 | 2.905% | 144.0538 | 144.1 | 144
CE110 | 128 | 129 | 132.917 | 122 | 127.5385 | 127.6854 | 126.659 | 122 | 132.917 | 8.52% | 128.1312 | 127.9 | 127.9
CE120 | 117 | 117 | 109.581 | 110 | 116.3845 | 116.6706 | 115.4998 | 109.581 | 117 | 6.346% | 116.9129 | 116.9 | 116.9
CE130 | 10 | 10 | 8.316 | 8 | 10.2557 | 10.2598 | 10.3889 | 8 | 10.3889 | 22.95% | 10.4079 | 10.3 | 10.3
CE140 | 8 | 8 | 6.947 | 6 | 8.1004 | 8.1094 | 8.2128 | 6 | 8.2128 | 26.94% | 8.2142 | 8.1 | 8.1
CE150 | 141 | 141 | 132.917 | 136 | 140.2495 | 140.8727 | 139.4036 | 132.917 | 141 | 5.724% | 141.2203 | 141.1 | 141.1
CE160 | 129 | 129 | 119.052 | 121 | 128.2763 | 129.1114 | 128.2863 | 119.052 | 129.1114 | 7.779% | 129.3096 | 129.2 | 129.2
CE165 | 149 | 150 | 141.678 | 145 | 148.5366 | 149.3574 | 147.976 | 141.678 | 150 | 5.582% | 149.0983 | 149.3 | 149.3
CE170 | 73 | 73 | 61.322 | 63 | 73.0096 | 73.1586 | 72.9774 | 61.322 | 73.1586 | 16.08% | 73.5918 | 73.2 | 73.2
CE180 | 118 | 119 | 110.813 | 112 | 118.3832 | 118.487 | 118.1287 | 110.813 | 119 | 6.893% | 118.7728 | 118.6 | 118.5
CE185 | 139 | 139 | 135.056 | 137 | 139.1103 | 139.2444 | 138.821 | 135.056 | 139.2444 | 3.005% | 139.3882 | 139.4 | 139.3
CE190 | 18 | 18 | 14.151 | 14 | 18.0337 | 18.0236 | 18.1435 | 14 | 18.1435 | 22.8% | 18.1701 | 18 | 18
CE195 | 23 | 23 | 17.728 | 18 | 22.6607 | 22.6253 | 22.7884 | 17.728 | 23 | 23.1% | 22.821 | 22.6 | 22.6
CE200 | 154 | 153 | 149.151 | 151 | 153.3548 | 154.56 | 154.56 | 149.151 | 154.56 | 3.502% | 154.4611 | 154.6 | 154.6
Energy Consumption, Condenser Fan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
CE100 | 68 | 68 | 68.174 | 67 |  | 67.452 | 66.8486 | 66.8486 | 68.174 | 1.959% | 67.6427 | 67.6 | 67.6
CE110 | 60 | 61 | 62.413 | 60 |  | 59.9566 | 59.4747 | 59.4747 | 62.413 | 4.884% | 60.166 | 60.1 | 60.1
CE120 | 55 | 55 | 51.455 | 55 |  | 54.7846 | 54.2347 | 51.455 | 55 | 6.457% | 54.8982 | 54.9 | 54.9
CE130 | 5 | 5 | 3.905 | 5 |  | 4.8176 | 4.8783 | 3.905 | 5 | 22.41% | 4.8872 | 4.8 | 4.8
CE140 | 4 | 4 | 3.262 | 4 |  | 3.8079 | 3.8565 | 3.262 | 4 | 19.13% | 3.8571 | 3.8 | 3.8
CE150 | 66 | 66 | 62.413 | 65 |  | 66.1491 | 65.4591 | 62.413 | 66.1491 | 5.634% | 66.3121 | 66.3 | 66.2
CE160 | 61 | 61 | 55.903 | 60 |  | 60.6262 | 60.2388 | 55.903 | 61 | 8.394% | 60.7193 | 60.7 | 60.7
CE165 | 70 | 70 | 66.527 | 69 |  | 70.1326 | 69.4843 | 66.527 | 70.1326 | 5.15% | 70.0114 | 70.1 | 70.1
CE170 | 34 | 34 | 28.795 | 34 |  | 34.3527 | 34.2676 | 28.795 | 34.3527 | 16.08% | 34.5562 | 34.4 | 34.4
CE180 | 56 | 56 | 52.034 | 56 |  | 55.6374 | 55.4691 | 52.034 | 56 | 7.111% | 55.7716 | 55.7 | 55.7
CE185 | 65 | 65 | 63.418 | 66 |  | 65.3842 | 65.1855 | 63.418 | 66 | 3.945% | 65.4519 | 65.4 | 65.4
CE190 | 8 | 9 | 6.645 | 8 |  | 8.4632 | 8.5195 | 6.645 | 9 | 27.6% | 8.5321 | 8.5 | 8.5
CE195 | 11 | 11 | 8.324 | 11 |  | 10.6241 | 10.7006 | 8.324 | 11 | 24.97% | 10.716 | 10.6 | 10.6
CE200 | 73 | 72 | 70.036 | 71 |  | 72.576 | 72.576 | 70.036 | 73 | 4.087% | 72.5296 | 72.6 | 72.6
results5-3.xls q:a06..p75; 10/15/02
[15 empty] | Coil Loads: Total, Sensible, and Latent | [14 empty] | Zone Loads: Total, Sensible, and Latent
[15 empty] | Coil Load, Total (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Zone Load, Total (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 3800 | 3800 | 3841.47 | 3793.9625 | 3797.6497 | 3799.7366 | 3797.9491 | 3793.9625 | 3841.47 | 1.25% | 3800.3599 | 3800.4 | 3800.4 |  | CE100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3654.1272 | 3656.0832 | 3655.5859 | 3654.1272 | 3656.0832 | 0.0535% | 3656.3062 | 3656.3 | 3656.3
[15 empty] | CE110 | 3765 | 3766 | 3803.58 | 3755.5686 | 3763.0688 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 1.275% | 3765.2438 | 3765 | 3765.3 |  | CE110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5345 | 3636.9245 | 3636.5534 | 3635.5345 | 3637 | 0.04029% | 3637.1129 | 3637.1 | 3637.1
[15 empty] | CE120 | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.9059 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 0.6488% | 3748.902 | 3748.8 | 3748.5 |  | CE120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3630.5353 | 3631.7568 | 3631.3216 | 3630.472 | 3632 | 0.04207% | 3631.9893 | 3631.9 | 3631.9
[15 empty] | CE130 | 219 | 219 | 215.778 | 215.1231 | 217.0012 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 2.118% | 219.3541 | 219.3 | 219.2 |  | CE130 | 209 | 209 | 207.344 | 207.5029 | 206.7475 | 208.7252 | 209.371 | 206.7475 | 209.371 | 1.256% | 208.9462 | 209 | 209
[15 empty] | CE140 | 198 | 198 | 195.53 | 194.6073 | 196.2821 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 1.999% | 197.9671 | 197.9 | 197.3 |  | CE140 | 190 | 190 | 188.503 | 188.4525 | 188.1832 | 189.5652 | 190.358 | 188.1832 | 190.358 | 1.146% | 189.7529 | 189.7 | 189.7
[15 empty] | CE150 | 4517 | 4517 | 4542.78 | 4527.5498 | 4508.7225 | 4516.9958 | 4515.0285 | 4508.7225 | 4542.78 | 0.7539% | 4517.5274 | 4517.4 | 4518.3 |  | CE150 | 4376 | 4376 | 4374.801 | 4376.0258 | 4374.7468 | 4376.1245 | 4375.5775 | 4374.7468 | 4376.1245 | 0.03148% | 4376.3129 | 4376.3 | 4376.3
[15 empty] | CE160 | 4501 | 4500 | 4516.378 | 4508.4994 | 4491.0487 | 4500.0682 | 4498.8816 | 4491.0487 | 4516.378 | 0.5628% | 4500.5449 | 4500.3 | 4499.9 |  | CE160 | 4371 | 4371 | 4369.652 | 4371.0434 | 4369.7196 | 4370.9568 | 4370.6181 | 4369.652 | 4371.0434 | 0.03183% | 4371.1893 | 4371.1 | 4371.1
[15 empty] | CE165 | 4538 | 4538 | 4567.458 | 4548.9449 | 4528.6592 | 4537.0685 | 4535.1008 | 4528.6592 | 4567.458 | 0.8552% | 4536.998 | 4537.3 | 4537.9 |  | CE165 | 4388 | 4388 | 4386.071 | 4387.456 | 4385.9248 | 4387.7098 | 4387.1605 | 4385.9248 | 4388 | 0.04729% | 4387.8381 | 4387.9 | 4387.9
[15 empty] | CE170 | 2233 | 2232 | 2226.057 | 2236.5182 | 2224.8677 | 2231.6851 | 2231.6345 | 2224.8677 | 2236.5182 | 0.5219% | 2232.3427 | 2231.9 | 2232.5 |  | CE170 | 2159 | 2159 | 2157.351 | 2157.9719 | 2157.1388 | 2158.5245 | 2158.621 | 2157.1388 | 2159 | 0.08622% | 2158.7129 | 2158.7 | 2158.7
[15 empty] | CE180 | 4495 | 4495 | 4509.984 | 4534.5838 | 4481.208 | 4494.6115 | 4494.0999 | 4481.208 | 4534.5838 | 1.187% | 4495.2651 | 4494.9 | 4493.8 |  | CE180 | 4376 | 4376 | 4374.852 | 4376.0258 | 4374.7389 | 4376.1245 | 4375.9707 | 4374.7389 | 4376.1245 | 0.03166% | 4376.3129 | 4376.3 | 4376.3
[15 empty] | CE185 | 4507 | 4535 | 4564.894 | 4582.6495 | 4522.5899 | 4534.5283 | 4533.9432 | 4507 | 4582.6495 | 1.668% | 4535.1231 | 4534.9 | 4533.9 |  | CE185 | 4396 | 4396 | 4393.649 | 4394.7831 | 4393.3107 | 4395.2832 | 4395.0925 | 4393.3107 | 4396 | 0.06118% | 4395.5062 | 4395.5 | 4395.5
[15 empty] | CE190 | 578 | 577 | 572.607 | 578.5463 | 574.3018 | 577.1889 | 577.6703 | 572.607 | 578.5463 | 1.028% | 577.5279 | 577.3 | 577.7 |  | CE190 | 557 | 559 | 558.09 | 558.0305 | 557.7813 | 559.1652 | 559.4558 | 557 | 559.4558 | 0.439% | 559.3529 | 559.3 | 559.3
[15 empty] | CE195 | 602 | 601 | 595.24 | 601.6999 | 597.7018 | 600.9508 | 601.339 | 595.24 | 602 | 1.124% | 601.3744 | 601.2 | 601.2 |  | CE195 | 576 | 579 | 576.926 | 577.0809 | 576.347 | 578.3252 | 578.542 | 576 | 579 | 0.5185% | 578.5462 | 578.6 | 578.6
[15 empty] | CE200 | 5498 | 5436 | 5534.2 | 5521.9812 | 5484.4779 | 5497.5648 | 5497.5648 | 5436 | 5534.2 | 1.786% | 5497.8008 | 5497.8 | 5497.8 |  | CE200 | 5343 | 5283 | 5341.526 | 5342.9074 | 5341.5034 | 5343.0048 | 5343.0048 | 5283 | 5343.0048 | 1.123% | 5343.2549 | 5343.2 | 5343.2
[15 empty] | Coil Load, Sensible (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Zone Load, Sensible (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 3800 | 3800 | 3841.47 | 3793.9625 | 3797.6448 | 3799.7366 | 3797.9491 | 3793.9625 | 3841.47 | 1.25% | 3800.3599 | 3800.4 | 3800.4 |  | CE100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3654.1272 | 3656.0832 | 3655.5859 | 3654.1272 | 3656.0832 | 0.0535% | 3656.3062 | 3656.3 | 3656.3
[15 empty] | CE110 | 3765 | 3766 | 3803.58 | 3755.5686 | 3763.0651 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 1.275% | 3765.2438 | 3765 | 3765.3 |  | CE110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5345 | 3636.9245 | 3636.5534 | 3635.5345 | 3637 | 0.04029% | 3637.1129 | 3637.1 | 3637.1
[15 empty] | CE120 | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.9017 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 0.6488% | 3748.902 | 3748.8 | 3748.5 |  | CE120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3630.5353 | 3631.7568 | 3631.3216 | 3630.472 | 3632 | 0.04207% | 3631.9893 | 3631.9 | 3631.9
[15 empty] | CE130 | 219 | 219 | 215.778 | 215.1231 | 217.0004 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 2.118% | 219.3541 | 219.3 | 219.2 |  | CE130 | 209 | 209 | 207.344 | 207.5029 | 206.7475 | 208.7252 | 209.371 | 206.7475 | 209.371 | 1.256% | 208.9462 | 209 | 209
[15 empty] | CE140 | 198 | 198 | 195.53 | 194.6073 | 196.2815 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 1.999% | 197.9671 | 197.9 | 197.3 |  | CE140 | 190 | 190 | 188.503 | 188.4525 | 188.1832 | 189.5652 | 190.358 | 188.1832 | 190.358 | 1.146% | 189.7529 | 189.7 | 189.7
[15 empty] | CE150 | 3778 | 3778 | 3803.58 | 3786.0492 | 3776.027 | 3777.7958 | 3775.8216 | 3775.8216 | 3803.58 | 0.7347% | 3778.3318 | 3778.2 | 3779 |  | CE150 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5501 | 3636.9245 | 3636.3775 | 3635.5501 | 3637 | 0.03986% | 3637.1129 | 3637.1 | 3637.1
[15 empty] | CE160 | 3761 | 3761 | 3777.178 | 3769.0504 | 3759.0367 | 3760.8682 | 3759.6868 | 3759.0367 | 3777.178 | 0.4823% | 3761.3053 | 3761.1 | 3760.8 |  | CE160 | 3632 | 3632 | 3630.452 | 3631.5944 | 3630.5229 | 3631.7568 | 3631.4181 | 3630.452 | 3632 | 0.04262% | 3631.9893 | 3631.9 | 3631.9
[15 empty] | CE165 | 3798 | 3798 | 3828.258 | 3808.6166 | 3795.4926 | 3797.8685 | 3795.9117 | 3795.4926 | 3828.258 | 0.8628% | 3797.7525 | 3798.1 | 3798.6 |  | CE165 | 3649 | 3649 | 3646.871 | 3648.007 | 3646.7281 | 3648.5098 | 3647.9605 | 3646.7281 | 3649 | 0.06227% | 3648.6381 | 3648.7 | 3648.7
[15 empty] | CE170 | 1493 | 1493 | 1486.857 | 1497.6553 | 1491.221 | 1492.4851 | 1492.423 | 1486.857 | 1497.6553 | 0.7233% | 1493.027 | 1492.7 | 1493.1 |  | CE170 | 1420 | 1420 | 1418.151 | 1418.5229 | 1417.9388 | 1419.3245 | 1419.421 | 1417.9388 | 1420 | 0.1452% | 1419.5129 | 1419.5 | 1419.5
[15 empty] | CE180 | 1537 | 1538 | 1553.184 | 1606.6823 | 1537.3461 | 1537.8115 | 1537.3001 | 1537 | 1606.6823 | 4.531% | 1537.7939 | 1538.1 | 1537.7 |  | CE180 | 1420 | 1420 | 1418.052 | 1418.5229 | 1417.9523 | 1419.3245 | 1419.1707 | 1417.9523 | 1420 | 0.1443% | 1419.5129 | 1419.5 | 1419.5
[15 empty] | CE185 | 1548 | 1578 | 1608.094 | 1652.6964 | 1576.6014 | 1577.7283 | 1577.1233 | 1548 | 1652.6964 | 6.636% | 1577.6007 | 1578.1 | 1577.7 |  | CE185 | 1439 | 1439 | 1436.849 | 1437.2802 | 1436.5241 | 1438.4832 | 1438.2925 | 1436.5241 | 1439 | 0.1721% | 1438.7062 | 1438.7 | 1438.7
[15 empty] | CE190 | 208 | 208 | 203.007 | 212.1923 | 206.3654 | 207.5889 | 208.0235 | 203.007 | 212.1923 | 4.42% | 207.8123 | 207.7 | 207.9 |  | CE190 | 190 | 190 | 188.49 | 188.4525 | 188.1822 | 189.5652 | 189.8558 | 188.1822 | 190 | 0.958% | 189.7529 | 189.7 | 189.7
[15 empty] | CE195 | 232 | 232 | 225.64 | 235.0528 | 229.5563 | 231.3508 | 231.7335 | 225.64 | 235.0528 | 4.063% | 231.645 | 231.6 | 231.6 |  | CE195 | 209 | 209 | 207.326 | 207.5029 | 206.7479 | 208.7252 | 208.942 | 206.7479 | 209 | 1.078% | 208.9462 | 209 | 209
[15 empty] | CE200 | 4276 | 4215 | 4313.176 | 4302.755 | 4274.2567 | 4276.5408 | 4276.5408 | 4215 | 4313.176 | 2.296% | 4276.6945 | 4276.8 | 4276.8 |  | CE200 | 4122 | 4062 | 4120.502 | 4121.6295 | 4120.521 | 4121.9808 | 4121.9808 | 4062 | 4122 | 1.456% | 4122.2309 | 4122.2 | 4122.2
[15 empty] | Coil Load, Latent (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Zone Load, Latent (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 0 | 0 | 0 | 0 | 0.0049461 | 0 | 3.3138e-14 | 0 | 0.0049461 |  | 0 | 0 | 0 |  | CE100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[15 empty] | CE110 | 0 | 0 | 0 | 0 | 0.00371 | 0 | 2.6912e-15 | 0 | 0.00371 |  | 0 | 0 | 0 |  | CE110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[15 empty] | CE120 | 0 | 0 | 0 | 0 | 0.0042294 | 0 | 3.8103e-15 | 0 | 0.0042294 |  | 0 | 0 | 0 |  | CE120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[15 empty] | CE130 | 0 | 0 | 0 | 0 | 0.000795 | 0 | 3.1415e-14 | 0 | 0.000795 |  | 0 | 0 | 0 |  | CE130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[15 empty] | CE140 | 0 | 0 | 0 | 0 | 0.00067806 | 0 | -2.7533e-16 | -2.7533e-16 | 0.00067806 |  | 0 | 0 | 0 |  | CE140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[15 empty] | CE150 | 739 | 739 | 739.2 | 741.5006 | 732.6956 | 739.2 | 739.2069 | 732.6956 | 741.5006 | 1.191% | 739.1956 | 739.2 | 739.4 |  | CE150 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
[15 empty] | CE160 | 740 | 739 | 739.2 | 739.449 | 732.0119 | 739.2 | 739.1947 | 732.0119 | 740 | 1.081% | 739.2396 | 739.2 | 739.1 |  | CE160 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
[15 empty] | CE165 | 740 | 739 | 739.2 | 740.3283 | 733.1667 | 739.2 | 739.1892 | 733.1667 | 740.3283 | 0.9688% | 739.2454 | 739.2 | 739.3 |  | CE165 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
[15 empty] | CE170 | 740 | 739 | 739.2 | 738.8628 | 733.6467 | 739.2 | 739.2115 | 733.6467 | 740 | 0.8594% | 739.3157 | 739.2 | 739.4 |  | CE170 | 739 | 739 | 739.2 | 739.449 | 739.2 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2
[15 empty] | CE180 | 2958 | 2957 | 2956.8 | 2927.9015 | 2943.8619 | 2956.8 | 2956.7992 | 2927.9015 | 2958 | 1.018% | 2957.4713 | 2956.8 | 2956.1 |  | CE180 | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.7866 | 2957.5029 | 0.02423% | 2956.8 | 2956.8 | 2956.8
[15 empty] | CE185 | 2959 | 2957 | 2956.8 | 2929.9531 | 2945.9884 | 2956.8 | 2956.8195 | 2929.9531 | 2959 | 0.9821% | 2957.5224 | 2956.8 | 2956.2 |  | CE185 | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.7866 | 2957.5029 | 0.02423% | 2956.8 | 2956.8 | 2956.8
[15 empty] | CE190 | 370 | 370 | 369.6 | 366.354 | 367.9364 | 369.6 | 369.6468 | 366.354 | 370 | 0.9862% | 369.7156 | 369.6 | 369.8 |  | CE190 | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 367 | 370 | 0.8117% | 369.6 | 369.6 | 369.6
[15 empty] | CE195 | 370 | 370 | 369.6 | 366.6471 | 368.1456 | 369.6 | 369.6055 | 366.6471 | 370 | 0.9068% | 369.7294 | 369.6 | 369.6 |  | CE195 | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 367 | 370 | 0.8117% | 369.6 | 369.6 | 369.6
[15 empty] | CE200 | 1222 | 1221 | 1221 | 1219.2263 | 1210.2212 | 1221.024 | 1221.024 | 1210.2212 | 1222 | 0.9646% | 1221.1063 | 1221 | 1221 |  | CE200 | 1221 | 1221 | 1221.024 | 1221.2778 | 1220.9824 | 1221.024 | 1221.024 | 1220.9824 | 1221.2778 | 0.0242% | 1221.024 | 1221 | 1221
[17 empty] | results5-3.xls q:bc77..br147; 10/15/02 | [14 empty] | results5-3.xls q:bt77..ch147; 10/15/02
[15 empty] | Sensible Coil - Zone Load, (Fan Heat) (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Latent Coil - Zone Load, (Should be 0) (kWh,thermal) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 144 | 144 | 187.05 | 138.6284 | 143.5176 | 143.6534 | 142.3632 | 138.6284 | 187.05 | 33.61% | 144.0536 | 144.1 | 144.1 |  | CE100 | 0 | 0 | 0 | 0 | 0.0049461 | 0 | 3.3138e-14 | 0 | 0.0049461 |  | 0 | 0 | 0
[15 empty] | CE110 | 128 | 129 | 167.979 | 118.9918 | 127.5306 | 127.6867 | 126.6828 | 118.9918 | 167.979 | 38.23% | 128.1309 | 127.9 | 128.2 |  | CE110 | 0 | 0 | 0 | 0 | 0.00371 | 0 | 2.6912e-15 | 0 | 0.00371 |  | 0 | 0 | 0
[15 empty] | CE120 | 117 | 117 | 133.008 | 107.5615 | 116.3664 | 116.6726 | 115.4889 | 107.5615 | 133.008 | 21.77% | 116.9127 | 116.9 | 116.6 |  | CE120 | 0 | 0 | 0 | 0 | 0.0042294 | 0 | 3.8103e-15 | 0 | 0.0042294 |  | 0 | 0 | 0
[15 empty] | CE130 | 10 | 10 | 8.434 | 7.6202 | 10.2529 | 10.2601 | 10.3985 | 7.6202 | 10.3985 | 26.69% | 10.4079 | 10.3 | 10.2 |  | CE130 | 0 | 0 | 0 | 0 | 0.000795 | 0 | 3.1415e-14 | 0 | 0.000795 |  | 0 | 0 | 0
[15 empty] | CE140 | 8 | 8 | 7.027 | 6.1547 | 8.0983 | 8.1097 | 8.2063 | 6.1547 | 8.2063 | 24.98% | 8.2142 | 8.2 | 7.6 |  | CE140 | 0 | 0 | 0 | 0 | 0.00067806 | 0 | -2.7533e-16 | -2.7533e-16 | 0.00067806 |  | 0 | 0 | 0
[15 empty] | CE150 | 141 | 141 | 167.979 | 149.4725 | 140.4768 | 140.8714 | 139.4441 | 139.4441 | 167.979 | 20.21% | 141.2189 | 141.1 | 141.9 |  | CE150 | 0 | 0 | 0 | 2.0516 | -6.5011 | 0 | 0.00687 | -6.5011 | 2.0516 |  | -0.0044111 | 0 | 0.2
[15 empty] | CE160 | 129 | 129 | 146.726 | 137.456 | 128.5138 | 129.1114 | 128.2687 | 128.2687 | 146.726 | 14.27% | 129.316 | 129.2 | 128.9 |  | CE160 | 1 | 0 | 0 | 0 | -7.1847 | 0 | -0.00534 | -7.1847 | 1 |  | 0.039573 | 0 | -0.1
[15 empty] | CE165 | 149 | 149 | 181.387 | 160.6096 | 148.7644 | 149.3587 | 147.9512 | 147.9512 | 181.387 | 22.42% | 149.1144 | 149.4 | 149.9 |  | CE165 | 1 | 0 | 0 | 0.87925 | -6.03 | 0 | -0.01082 | -6.03 | 1 |  | 0.045435 | 0 | 0.1
[15 empty] | CE170 | 73 | 73 | 68.706 | 79.1325 | 73.2822 | 73.1606 | 73.002 | 68.706 | 79.1325 | 14.18% | 73.5141 | 73.2 | 73.6 |  | CE170 | 1 | 0 | 0 | -0.58617 | -5.5533 | 0 | 0.01152 | -5.5533 | 1 |  | 0.1157 | 0 | 0.2
[15 empty] | CE180 | 117 | 118 | 135.132 | 188.1594 | 119.3938 | 118.487 | 118.1294 | 117 | 188.1594 | 60.16% | 118.281 | 118.6 | 118.2 |  | CE180 | 1 | 0 | 0 | -29.6014 | -12.9246 | 0 | -0.00076 | -29.6014 | 1 |  | 0.67126 | 0 | -0.7
[15 empty] | CE185 | 109 | 139 | 171.245 | 215.4162 | 140.0773 | 139.2451 | 138.8308 | 109 | 215.4162 | 76.62% | 138.8945 | 139.4 | 139 |  | CE185 | 2 | 0 | 0 | -27.5498 | -10.7981 | 0 | 0.01946 | -27.5498 | 2 |  | 0.72237 | 0 | -0.6
[15 empty] | CE190 | 18 | 18 | 14.517 | 23.7397 | 18.1832 | 18.0237 | 18.1676 | 14.517 | 23.7397 | 51.07% | 18.0594 | 18 | 18.2 |  | CE190 | 3 | 0 | 0 | -3.2239 | -1.6626 | 0 | 0.046846 | -3.2239 | 3 |  | 0.11557 | 0 | 0.2
[15 empty] | CE195 | 23 | 23 | 18.314 | 27.5498 | 22.8083 | 22.6256 | 22.7915 | 18.314 | 27.5498 | 40.69% | 22.6987 | 22.6 | 22.6 |  | CE195 | 3 | 0 | 0 | -2.9308 | -1.4535 | 0 | 0.0055 | -2.9308 | 3 |  | 0.1294 | 0 | 0
[15 empty] | CE200 | 154 | 153 | 192.674 | 181.1254 | 153.7356 | 154.56 | 154.56 | 153 | 192.674 | 25.69% | 154.4636 | 154.6 | 154.6 |  | CE200 | 1 | 0 | -0.024 | -2.0516 | -10.7612 | 0 | 0 | -10.7612 | 1 |  | 0.082262 | 0 | 0
Zone Loads: Total, Sensible, and Latent
COP: Mean, and (Max-Min)/Mean
Mean COP | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
E100 | 2.39 | 2.389 | 2.4304 | 2.4064 | 2.404 | 2.4017 | 2.4184 | 2.389 | 2.4304 | 1.733% | 2.3889 | 2.39 | 2.39
E110 | 3.38 | 3.342 | 3.4589 | 3.4146 | 3.4007 | 3.4087 | 3.4271 | 3.342 | 3.4589 | 3.459% | 3.3795 | 3.38 | 3.38
E120 | 3.59 | 3.59 | 3.6139 | 3.623 | 3.6075 | 3.6054 | 3.6313 | 3.59 | 3.6313 | 1.15% | 3.5865 | 3.59 | 3.59
E130 | 1.91 | 1.909 | 1.9752 | 1.953 | 1.9038 | 1.9198 | 1.9163 | 1.9038 | 1.9752 | 3.778% | 1.8895 | 1.91 | 1.91
E140 | 2.77 | 2.734 | 2.9151 | 2.854 | 2.7714 | 2.7974 | 2.7996 | 2.734 | 2.9151 | 6.585% | 2.7502 | 2.77 | 2.77
E150 | 3.62 | 3.63 | 3.6675 | 3.7 | 3.6544 | 3.6496 | 3.6734 | 3.62 | 3.7 | 2.205% | 3.6273 | 3.63 | 3.63
E160 | 3.84 | 3.84 | 3.8658 | 3.95 | 3.8611 | 3.8452 | 3.8599 | 3.84 | 3.95 | 2.87% | 3.8329 | 3.84 | 3.84
E165 | 2.92 | 2.92 | 2.9514 | 2.9853 | 2.9415 | 2.9257 | 2.9449 | 2.92 | 2.9853 | 2.228% | 2.9295 | 2.93 | 2.93
E170 | 3.38 | 3.39 | 3.4423 | 3.477 | 3.3951 | 3.3944 | 3.4033 | 3.38 | 3.477 | 2.881% | 3.3672 | 3.39 | 3.39
E180 | 4.04 | 4.04 | 4.0842 | 4.026 | 4.0432 | 4.0472 | 4.055 | 4.026 | 4.0842 | 1.44% | 4.0423 | 4.04 | 4.04
E185 | 2.85 | 2.85 | 2.8744 | 2.823 | 2.8521 | 2.8512 | 2.8574 | 2.823 | 2.8744 | 1.805% | 2.8458 | 2.85 | 2.85
E190 | 3.41 | 3.41 | 3.4865 | 3.457 | 3.3942 | 3.4096 | 3.4048 | 3.3942 | 3.4865 | 2.726% | 3.3865 | 3.41 | 3.41
E195 | 2.31 | 2.31 | 2.3598 | 2.337 | 2.3033 | 2.3158 | 2.3054 | 2.3033 | 2.3598 | 2.464% | 2.2944 | 2.31 | 2.31
E200 | 3.62 | 3.61 | 3.6677 | 3.708 | 3.6471 | 3.6102 | 3.6102 | 3.61 | 3.708 | 2.707% | 3.6206 | 3.62 | 3.62
(Max - Min)/Mean COP | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
E100 | 0 | 0.00083717 | 0.0015062 | 0.0012467 | 0.0026072 | 0 | 0 | 0 | 0.0026072 |  | 0 |  | 0.00012552
E110 | 0 | 0.010473 | 0.0017378 | 0.0011714 | 0.0027731 | 0 | 0.010592 | 0 | 0.010592 |  | 0 |  | 0.00038462
E120 | 0 | 0.0036212 | 0.00079758 | 0.0011041 | 0.0027415 | 0 | 0.012271 | 0 | 0.012271 |  | 0 |  | 0.00030641
E130 | 0 | 0.03824 | 0.012602 | 0.0087046 | 0.0037428 | 0 | 0.17198 | 0 | 0.17198 |  | 0 |  | -5.2356e-05
E140 | 0 | 0.055962 | 0.010989 | 0.018921 | 0.0038004 | 0 | 0.20433 | 0 | 0.20433 |  | 0 |  | 3.6101e-05
E150 | 0.0027624 | 0.0027548 | 0.0014674 | 0.0048649 | 0.010553 | 0 | 0.0092759 | 0 | 0.010553 |  | 0 |  | 0.00096419
E160 | 0.0026042 | 0.0052083 | 0.0010614 | 0.0032911 | 0.011024 | 0 | 0.010193 | 0 | 0.011024 |  | 0 |  | 0.00026042
E165 | 0.010274 | 0.0034247 | 0.0012002 | 0.0026798 | 0.011921 | 0 | 0.0084429 | 0 | 0.011921 |  | 0 |  | 0.00030717
E170 | 0 | 0.0058997 | 0.0021466 | 0.0040265 | 0.015183 | 0 | 0.043444 | 0 | 0.043444 |  | 0 |  | 0.00026549
E180 | 0.0049505 | 0.0024752 | 0.0023307 | 0.009687 | 0.029331 | 0 | 0.011687 | 0 | 0.029331 |  | 0 |  | 4.9505e-05
E185 | 0.0070175 | 0.0035088 | 0.0023597 | 0.010273 | 0.034252 | 0 | 0.0091078 | 0 | 0.034252 |  | 0 |  | 0.00017544
E190 | 0 | 0.02346 | 0.0071705 | 0.018802 | 0.039563 | 0 | 0.10066 | 0 | 0.10066 |  | 0 |  | -8.7977e-05
E195 | 0 | 0.017316 | 0.0078108 | 0.016688 | 0.043389 | 0 | 0.08606 | 0 | 0.08606 |  | 0 |  | 0.00012987
E200 | 0.0055249 | 0 | -1.2839e-05 | 0.0051241 | 0.011968 | 0 | 0 | -1.2839e-05 | 0.011968 |  | 0 |  | 8.2873e-05
results5-3.xls q:a185..p220; 10/15/02
Indoor Drybulb Temperature: Mean and (Max-Min)/Mean
[15 empty] | Mean IDB (°C) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6346 | 22.1999 | 22.6346 | 1.958% | 22.2 | 22.2 | 22.216
[15 empty] | CE110 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.1999 | 22.2 | 22.5242 | 22.1999 | 22.5242 | 1.461% | 22.2 | 22.2 | 22.214
[15 empty] | CE120 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.7 | 26.7 | 27.0785 | 26.7 | 27.0785 | 1.418% | 26.7 | 26.7 | 26.712
[15 empty] | CE130 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.6377 | 21.6377 | 22.2 | 2.533% | 22.2 | 22.2 | 22.187
[15 empty] | CE140 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.5097 | 21.5097 | 22.2 | 3.11% | 22.2 | 22.2 | 22.185
[15 empty] | CE150 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6771 | 22.1999 | 22.6771 | 2.15% | 22.2 | 22.2 | 22.216
[15 empty] | CE160 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.6999 | 26.7 | 26.9948 | 26.6999 | 26.9948 | 1.104% | 26.7 | 26.7 | 26.714
[15 empty] | CE165 | 23.3 | 23.3 | 23.4 | 23.4444 | 23.2999 | 23.3 | 23.7805 | 23.2999 | 23.7805 | 2.063% | 23.3 | 23.3 | 23.317
[15 empty] | CE170 | 22.2 | 22.2 | 22.2 | 22.2222 | 22.1999 | 22.2 | 22.1169 | 22.1169 | 22.2222 | 0.4746% | 22.2 | 22.2 | 22.199
[15 empty] | CE180 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.2 | 22.2 | 22.3344 | 22.2 | 22.3344 | 0.6055% | 22.2 | 22.2 | 22.205
[15 empty] | CE185 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.2 | 22.2 | 22.3682 | 22.2 | 22.3682 | 0.7576% | 22.2 | 22.2 | 22.206
[15 empty] | CE190 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.9469 | 21.9469 | 22.2 | 1.14% | 22.2 | 22.2 | 22.194
[15 empty] | CE195 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 22.0113 | 22.0113 | 22.2 | 0.8501% | 22.2 | 22.2 | 22.195
[15 empty] | CE200 | 26.7 | 26.7 | 26.8 | 26.7778 | 26.6999 | 26.7339 | 26.7339 | 26.6999 | 26.8 | 0.375% | 26.7 | 26.7 | 26.713
[15 empty] | (Max - Min)/Mean IDB (°C) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 0 | 0 | 0 | 0 | 1.9369e-05 | 0 | 0.049482 | 0 | 0.049482 |  | 0 |  | 0.0017105
[15 empty] | CE110 | 0 | 0 | 0 | 0 | 2.4324e-05 | 0 | 0.047948 | 0 | 0.047948 |  | 0 |  | 0.0018907
[15 empty] | CE120 | 0 | 0 | 0 | 0 | 1.4232e-05 | 0 | 0.077183 | 0 | 0.077183 |  | 0 |  | 0.0017221
[15 empty] | CE130 | 0 | 0 | 0 | 0 | 2.2523e-06 | 0 | 0.056383 | 0 | 0.056383 |  | 0 |  | 0.0013521
[15 empty] | CE140 | 0 | 0 | 0 | 0 | 1.3514e-06 | 0 | 0.069271 | 0 | 0.069271 |  | 0 |  | 0.0015326
[15 empty] | CE150 | 0 | 0 | 0 | 0 | 2.7027e-05 | 0 | 0.053799 | 0 | 0.053799 |  | 0 |  | 0.0017105
[15 empty] | CE160 | 0 | 0 | 0 | 0 | 4.2697e-05 | 0 | 0.045194 | 0 | 0.045194 |  | 0 |  | 0.0015722
[15 empty] | CE165 | 0 | 0 | 0 | 0 | 4.3777e-05 | 0 | 0.051303 | 0 | 0.051303 |  | 0 |  | 0.0015439
[15 empty] | CE170 | 0 | 0 | 0 | 0 | 2.3423e-05 | 0 | 0.049736 | 0 | 0.049736 |  | 0 |  | 0.0013064
[15 empty] | CE180 | 0 | 0 | 0 | 0 | 2.027e-05 | 0 | 0.034924 | 0 | 0.034924 |  | 0 |  | 0.00081063
[15 empty] | CE185 | 0 | 0 | 0 | 0 | 1.4865e-05 | 0 | 0.021459 | 0 | 0.021459 |  | 0 |  | 0.00072053
[15 empty] | CE190 | 0 | 0 | 0 | 0 | 4.0541e-06 | 0 | 0.02825 | 0 | 0.02825 |  | 0 |  | 0.00072092
[15 empty] | CE195 | 0 | 0 | 0 | 0 | 4.0541e-06 | 0 | 0.022716 | 0 | 0.022716 |  | 0 |  | 0.00063077
[15 empty] | CE200 | 0 | 0 | 0 | 0 | 4.2322e-05 | 0 | 0 | 0 | 4.2322e-05 |  | 0 |  | 0
Humidity Ratio: Mean and (Max-Min)/Mean
[15 empty] | Mean Humidity Ratio | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 0.0075 | 0.00691 | 0.0076 | 0.0074 | 0.0074745 | 0.0075036 | 0.0075088 | 0.00691 | 0.0076 | 9.29% | 0.0074274 | 0.00734 | 0.007339
[15 empty] | CE110 | 0.0066 | 0.00692 | 0.0070296 | 0.0064 | 0.0065835 | 0.0065938 | 0.0066309 | 0.0064 | 0.0070296 | 9.659% | 0.0065187 | 0.0064 | 0.006411
[15 empty] | CE120 | 0.008 | 0.007 | 0.0078 | 0.0078 | 0.0080402 | 0.0079506 | 0.0079517 | 0.007 | 0.0080402 | 13.2% | 0.0078783 | 0.00786 | 0.007873
[15 empty] | CE130 | 0.0075 | 0.00691 | 0.0076 | 0.0073 | 0.0074769 | 0.0075036 | 0.0075194 | 0.00691 | 0.0076 | 9.29% | 0.0074274 | 0.00734 | 0.007339
[15 empty] | CE140 | 0.0065 | 0.00692 | 0.0070601 | 0.0064 | 0.0065863 | 0.0065938 | 0.0065941 | 0.0064 | 0.0070601 | 10.13% | 0.0065187 | 0.0064 | 0.006402
[15 empty] | CE150 | 0.0083 | 0.00853 | 0.0082 | 0.0083 | 0.0084223 | 0.0083236 | 0.0085152 | 0.0082 | 0.00853 | 4.011% | 0.0082272 | 0.0082 | 0.00821
[15 empty] | CE160 | 0.0102 | 0.0101 | 0.009701 | 0.0099 | 0.010278 | 0.010069 | 0.010236 | 0.009701 | 0.010278 | 5.786% | 0.009969 | 0.00994 | 0.009946
[15 empty] | CE165 | 0.0093 | 0.00985 | 0.0090039 | 0.0092 | 0.0093948 | 0.0093021 | 0.0095112 | 0.0090039 | 0.00985 | 9.128% | 0.0092694 | 0.0092 | 0.009208
[15 empty] | CE170 | 0.0106 | 0.0107 | 0.010494 | 0.0105 | 0.010571 | 0.010471 | 0.010525 | 0.010471 | 0.0107 | 2.211% | 0.010367 | 0.01045 | 0.010451
[15 empty] | CE180 | 0.0164 | 0.0164 | 0.016614 | 0.0164 | 0.016193 | 0.01631 | 0.016404 | 0.016193 | 0.016614 | 2.6% | 0.01619 | 0.01623 | 0.01623
[15 empty] | CE185 | 0.0162 | 0.0171 | 0.016441 | 0.0162 | 0.016067 | 0.016151 | 0.016279 | 0.016067 | 0.0171 | 6.435% | 0.016056 | 0.01605 | 0.016059
[15 empty] | CE190 | 0.016 | 0.0161 | 0.016254 | 0.0159 | 0.015855 | 0.015921 | 0.015707 | 0.015707 | 0.016254 | 3.465% | 0.015796 | 0.0159 | 0.015891
[15 empty] | CE195 | 0.0156 | 0.0164 | 0.015764 | 0.0155 | 0.015446 | 0.01547 | 0.015326 | 0.015326 | 0.0164 | 6.988% | 0.015368 | 0.01544 | 0.015439
[15 empty] | CE200 | 0.0114 | 0.0115 | 0.010933 | 0.0111 | 0.011461 | 0.011281 | 0.011281 | 0.010933 | 0.0115 | 5.096% | 0.011129 | 0.01109 | 0.011099
[15 empty] | (Max - Min)/Mean Humidity Ratio | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | E+
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | NREL
[15 empty] | CE100 | 0 | 0.021708 | 0 | 0 | 0.00051398 | 0 | 0 | 0 | 0.021708 |  | 0 |  | 0
[15 empty] | CE110 | 0 | 0.021676 | 0.014226 | 0 | 0.00049972 | 0 | 0 | 0 | 0.021676 |  | 0 |  | 0
[15 empty] | CE120 | 0 | 0 | 0 | 0 | 0.00052403 | 0 | 0 | 0 | 0.00052403 |  | 0 |  | 0
[15 empty] | CE130 | 0 | 0.01013 | 0 | 0 | 0.00061108 | 0 | 0 | 0 | 0.01013 |  | 0 |  | 0
[15 empty] | CE140 | 0 | 0.011561 | 0.014164 | 0 | 0.00064275 | 0 | 0 | 0 | 0.014164 |  | 0 |  | 0
[15 empty] | CE150 | 0.012048 | 0 | 0 | 0 | 0.013105 | 0 | 0.013153 | 0 | 0.013153 |  | 0 |  | 0.00036541
[15 empty] | CE160 | 0.019608 | 0 | 0.010308 | 0.010101 | 0.013391 | 0 | 0.010747 | 0 | 0.019608 |  | 0 |  | 0.00040217
[15 empty] | CE165 | 0.010753 | 0.0010152 | 0.011106 | 0 | 0.013116 | 0 | 0.012512 | 0 | 0.013116 |  | 0 |  | 0.0003258
[15 empty] | CE170 | 0 | 0 | 0.0095289 | 0 | 0.011456 | 0 | 0.023752 | 0 | 0.023752 |  | 0 |  | 0.00057411
[15 empty] | CE180 | 0.018293 | 0 | 0.012038 | 0.012195 | 0.010319 | 0 | 0.040234 | 0 | 0.040234 |  | 0 |  | 0.00092421
[15 empty] | CE185 | 0.012346 | 0.005848 | 0.018247 | 0.012346 | 0.010816 | 0 | 0.024571 | 0 | 0.024571 |  | 0 |  | 0.00080951
[15 empty] | CE190 | 0 | 0 | 0.018457 | 0.018868 | 0.0145 | 0 | 0.031196 | 0 | 0.031196 |  | 0 |  | 0.00075514
[15 empty] | CE195 | 0 | 0.0060976 | 0.01903 | 0.019355 | 0.013755 | 0 | 0.024142 | 0 | 0.024142 |  | 0 |  | 0.00064771
[15 empty] | CE200 | 0.017544 | 0 | 0.0091467 | 0.009009 | 0.012859 | 0 | 0 | 0 | 0.017544 |  | 0 |  | 0
results5-3.xls q:bc233..br304; 10/15/02
Sensitivities for COP and Coil Loads
[45 empty] | Sensitivities for Space Cooling Electricity Consumption | [14 empty] | Sensitivities for COP and Coil Loads
[45 empty] | Delta Qtot (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Delta COP (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL
[45 empty] | CE110-CE100 | -454 | -441 | -459.621 | -454 | -450.9597 | -455.3055 | -449.9711 | -459.621 | -441 | 4.099% | -454.3131 | -453.6 | -453.2 |  | E110-E100 | 0.99 | 0.953 | 1.0285 | 1.0082 | 0.99667 | 1.0069 | 1.0087 | 0.953 | 1.0285 | 7.622% | 0.99059 | 0.99 | 0.99
[45 empty] | CE120-CE110 | -65 | -77 | -50.092 | -62 | -62.6782 | -59.6584 | -60.3021 | -77 | -50.092 | 42.34% | -63.5575 | -66.2 | -66.4 |  | E120-E110 | 0.21 | 0.248 | 0.155 | 0.20837 | 0.20683 | 0.19677 | 0.20416 | 0.155 | 0.248 | 44.92% | 0.20704 | 0.21 | 0.21
[45 empty] | CE120-CE100 | -519 | -518 | -509.713 | -516 | -513.638 | -514.9639 | -510.2732 | -519 | -509.713 | 1.793% | -517.8706 | -519.8 | -519.6 |  | E120-E100 | 1.2 | 1.201 | 1.1835 | 1.2166 | 1.2035 | 1.2037 | 1.2129 | 1.1835 | 1.2166 | 2.763% | 1.1976 | 1.2 | 1.2
[45 empty] | CE130-CE100 | -1421 | -1421 | -1415.398 | -1413 | -1411.4319 | -1413.5415 | -1401.8208 | -1421 | -1401.8208 | 1.351% | -1419.9663 | -1421.3 | -1421.1 |  | E130-E100 | -0.48 | -0.48 | -0.4552 | -0.45341 | -0.50017 | -0.48198 | -0.50212 | -0.50212 | -0.45341 | 9.754% | -0.49937 | -0.48 | -0.48
[45 empty] | CE140-CE130 | -42 | -40 | -40.411 | -40 | -40.6934 | -40.9605 | -41.4733 | -42 | -40 | 4.809% | -41.5864 | -41 | -41.2 |  | E140-E130 | 0.86 | 0.825 | 0.9399 | 0.901 | 0.86754 | 0.87767 | 0.88334 | 0.825 | 0.9399 | 13.35% | 0.86071 | 0.86 | 0.86
[45 empty] | CE140-CE110 | -1009 | -1020 | -996.188 | -999 | -1001.1655 | -999.1966 | -993.323 | -1020 | -993.323 | 2.649% | -1007.2396 | -1008.7 | -1009.1 |  | E140-E110 | -0.61 | -0.608 | -0.5438 | -0.56063 | -0.6293 | -0.61124 | -0.6275 | -0.6293 | -0.5438 | 13.59% | -0.62925 | -0.61 | -0.61
[45 empty] | CE150-CE110 | 131 | 118 | 141.228 | 118 | 128.04 | 132.0944 | 129.6472 | 118 | 141.228 | 17.83% | 130.2551 | 129.3 | 129.1 |  | E150-E110 | 0.24 | 0.288 | 0.2086 | 0.28537 | 0.25377 | 0.24097 | 0.24631 | 0.2086 | 0.288 | 32.04% | 0.24783 | 0.25 | 0.25
[45 empty] | CE160-CE150 | -68 | -68 | -64.794 | -76 | -65.3743 | -62.3216 | -58.7295 | -76 | -58.7295 | 26.15% | -66.05 | -67.2 | -67.6 |  | E160-E150 | 0.22 | 0.21 | 0.1983 | 0.25 | 0.20665 | 0.19555 | 0.18654 | 0.18654 | 0.25 | 30.86% | 0.20563 | 0.21 | 0.21
[45 empty] | CE165-CE160 | 362 | 362 | 361.817 | 363 | 359.3413 | 362.977 | 357.0433 | 357.0433 | 363 | 1.667% | 357.3902 | 360.4 | 360.7 |  | E165-E160 | -0.92 | -0.92 | -0.9144 | -0.96474 | -0.91963 | -0.91948 | -0.91505 | -0.96474 | -0.9144 | 5.572% | -0.90343 | -0.91 | -0.91
[45 empty] | CE170-CE150 | -570 | -569 | -573.348 | -563 | -561.7369 | -563.1461 | -555.7842 | -573.348 | -555.7842 | 3.107% | -565.3727 | -568.8 | -568.7 |  | E170-E150 | -0.24 | -0.24 | -0.2252 | -0.223 | -0.25935 | -0.25525 | -0.27013 | -0.27013 | -0.223 | 18.12% | -0.26014 | -0.24 | -0.24
[45 empty] | CE180-CE150 | -125 | -125 | -125.315 | -103 | -115.1083 | -117.7844 | -111.5753 | -125.315 | -103 | 18.02% | -123.824 | -124.2 | -124.6 |  | E180-E150 | 0.42 | 0.41 | 0.4167 | 0.326 | 0.38877 | 0.39757 | 0.38162 | 0.326 | 0.42 | 22.65% | 0.41502 | 0.41 | 0.41
[45 empty] | CE180-CE170 | 445 | 444 | 448.033 | 460 | 446.6285 | 445.3617 | 444.2089 | 444 | 460 | 3.624% | 441.5487 | 444.6 | 444.1 |  | E180-E170 | 0.66 | 0.65 | 0.6419 | 0.549 | 0.64811 | 0.65282 | 0.65175 | 0.549 | 0.66 | 16.44% | 0.67516 | 0.65 | 0.65
[45 empty] | CE185-CE180 | 461 | 461 | 464.046 | 467 | 458.3877 | 460.255 | 458.3596 | 458.3596 | 467 | 1.87% | 461.9737 | 461.1 | 461 |  | E185-E180 | -1.19 | -1.19 | -1.2098 | -1.203 | -1.1911 | -1.196 | -1.1976 | -1.2098 | -1.19 | 1.655% | -1.1965 | -1.19 | -1.19
[45 empty] | CE190-CE180 | -919 | -918 | -916.89 | -920 | -917.6654 | -917.2731 | -914.9174 | -920 | -914.9174 | 0.554% | -917.493 | -918.2 | -917.7 |  | E190-E180 | -0.63 | -0.63 | -0.5977 | -0.569 | -0.64902 | -0.63762 | -0.65027 | -0.65027 | -0.569 | 12.39% | -0.65583 | -0.63 | -0.63
[45 empty] | CE190-CE140 | 96 | 95 | 95.211 | 94 | 96.4318 | 96.2334 | 96.4774 | 94 | 96.4774 | 2.576% | 96.1777 | 95.6 | 95.9 |  | E190-E140 | 0.64 | 0.676 | 0.5714 | 0.603 | 0.62282 | 0.61216 | 0.60515 | 0.5714 | 0.676 | 16.44% | 0.63627 | 0.64 | 0.64
[45 empty] | CE195-CE190 | 86 | 86 | 84.7 | 86 | 85.8951 | 85.7346 | 86.4597 | 84.7 | 86.4597 | 2.023% | 86.9875 | 85.9 | 85.8 |  | E195-E190 | -1.1 | -1.1 | -1.1267 | -1.12 | -1.0909 | -1.0938 | -1.0994 | -1.1267 | -1.0909 | 3.277% | -1.0921 | -1.1 | -1.1
[45 empty] | CE195-CE185 | -1294 | -1293 | -1296.236 | -1301 | -1290.158 | -1291.7935 | -1286.8173 | -1301 | -1286.8173 | 1.097% | -1292.4792 | -1293.4 | -1292.9 |  | E195-E185 | -0.54 | -0.54 | -0.5146 | -0.48603 | -0.54881 | -0.53547 | -0.55209 | -0.55209 | -0.48603 | 11.98% | -0.55141 | -0.54 | -0.54
[45 empty] | CE195-CE130 | 140 | 141 | 139.5 | 140 | 141.6336 | 141.0075 | 141.4638 | 139.5 | 141.6336 | 1.507% | 141.5788 | 140.5 | 140.5 |  | E195-E130 | 0.4 | 0.401 | 0.3846 | 0.384 | 0.39945 | 0.39602 | 0.3891 | 0.384 | 0.401 | 4.199% | 0.40487 | 0.4 | 0.4
[45 empty] | CE200-CE100 | -54 | -66 | -52.603 | -79 | -55.4338 | -42.2735 | -31.9443 | -79 | -31.9443 | 85.97% | -54.7376 | -53.4 | -53.5 |  | E200-E100 | 1.23 | 1.221 | 1.2373 | 1.3016 | 1.2431 | 1.2084 | 1.1918 | 1.1918 | 1.3016 | 8.915% | 1.2317 | 1.23 | 1.23
[45 empty] | Del Qcomp (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Del Q coil,t (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL
[45 empty] | CE110-CE100 | -430 | -419 | -441.592 | -428 |  | -431.8474 | -426.8936 | -441.592 | -419 | 5.243% | -430.9138 | -429.8 | -429.5 |  | E110-E100 | -35 | -34 | -37.89 | -38.3939 | -34.5809 | -35.1254 | -34.7129 | -38.3939 | -34 | 12.51% | -35.1161 | -35.4 | -35.1
[45 empty] | CE120-CE110 | -49 | -59 | -15.798 | -45 |  | -43.4717 | -43.903 | -59 | -15.798 | 91.78% | -47.0715 | -50.1 | -50.2 |  | E120-E110 | -16 | -17 | -40.1 | -16.4127 | -16.1629 | -16.1818 | -16.4257 | -40.1 | -16 | 147.5% | -16.3418 | -16.2 | -16.8
[45 empty] | CE120-CE100 | -479 | -478 | -457.39 | -473 |  | -475.319 | -470.7965 | -479 | -457.39 | 4.521% | -477.9853 | -479.9 | -479.7 |  | E120-E100 | -51 | -51 | -77.99 | -54.8066 | -50.7438 | -51.3072 | -51.1386 | -77.99 | -50.7438 | 52.95% | -51.4579 | -51.6 | -51.9
[45 empty] | CE130-CE100 | -1224 | -1224 | -1214.26 | -1218 |  | -1217.5188 | -1207.8769 | -1224 | -1207.8769 | 1.318% | -1223.5648 | -1224.6 | -1224.6 |  | E130-E100 | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.6485 | -3580.7513 | -3578.1796 | -3625.692 | -3578.1796 | 1.327% | -3581.0058 | -3581.1 | -3581.2
[45 empty] | CE140-CE130 | -38 | -37 | -38.399 | -37 |  | -37.8005 | -38.2753 | -38.399 | -37 | 3.647% | -38.3628 | -37.9 | -37.9 |  | E140-E130 | -21 | -21 | -20.248 | -20.5158 | -20.7191 | -21.3105 | -21.2052 | -21.3105 | -20.248 | 4.968% | -21.387 | -21.4 | -21.9
[45 empty] | CE140-CE110 | -832 | -842 | -811.067 | -827 |  | -823.472 | -819.2586 | -842 | -811.067 | 3.722% | -831.0138 | -832.7 | -833 |  | E140-E110 | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.7867 | -3566.9364 | -3564.6719 | -3608.05 | -3560.9613 | 1.32% | -3567.2767 | -3567.1 | -3568
[45 empty] | CE150-CE110 | 111 | 100 | 141.228 | 99 |  | 112.7146 | 110.9181 | 99 | 141.228 | 38.04% | 111.0199 | 110 | 109.8 |  | E150-E110 | 752 | 751 | 739.2 | 771.9812 | 745.6537 | 752.3846 | 751.7923 | 739.2 | 771.9812 | 4.358% | 752.2836 | 752.4 | 753
[45 empty] | CE160-CE150 | -50 | -50 | -44.419 | -56 |  | -45.0374 | -42.3919 | -56 | -42.3919 | 28.03% | -48.5466 | -49.8 | -50.1 |  | E160-E150 | -16 | -17 | -26.402 | -19.0504 | -17.6739 | -16.9277 | -16.1469 | -26.402 | -16 | 61.25% | -16.9825 | -17.1 | -18.4
[45 empty] | CE165-CE160 | 333 | 332 | 328.567 | 330 |  | 333.2246 | 328.108 | 328.108 | 333.2246 | 1.558% | 328.3094 | 330.8 | 331.1 |  | E165-E160 | 37 | 38 | 51.08 | 40.4455 | 37.6106 | 37.0003 | 36.2193 | 36.2193 | 51.08 | 40.77% | 36.4531 | 37 | 38
[45 empty] | CE170-CE150 | -469 | -469 | -468.135 | -459 |  | -463.6356 | -458.1666 | -469 | -458.1666 | 2.325% | -465.9883 | -469.2 | -469.1 |  | E170-E150 | -2284 | -2285 | -2316.723 | -2291.0317 | -2283.8549 | -2285.3107 | -2283.394 | -2316.723 | -2283.394 | 1.458% | -2285.1847 | -2285.5 | -2285.8
[45 empty] | CE180-CE150 | -91 | -91 | -92.832 | -70 |  | -84.887 | -80.3105 | -92.832 | -70 | 25.14% | -90.836 | -91.2 | -91.5 |  | E180-E150 | -22 | -22 | -32.796 | 7.034 | -27.5145 | -22.3843 | -20.9286 | -32.796 | 7.034 | 178.9% | -22.2623 | -22.5 | -24.5
[45 empty] | CE180-CE170 | 378 | 378 | 375.303 | 389 |  | 378.7486 | 377.8561 | 375.303 | 389 | 3.651% | 375.1523 | 378 | 377.6 |  | E180-E170 | 2262 | 2263 | 2283.927 | 2298.0657 | 2256.3404 | 2262.9264 | 2262.4654 | 2256.3404 | 2298.0657 | 1.844% | 2262.9224 | 2263 | 2261.3
[45 empty] | CE185-CE180 | 431 | 431 | 428.419 | 432 |  | 429.7507 | 427.9509 | 427.9509 | 432 | 0.938% | 431.6779 | 430.6 | 430.5 |  | E185-E180 | 12 | 40 | 54.91 | 48.0657 | 41.3818 | 39.9168 | 39.8433 | 12 | 54.91 | 107.7% | 39.858 | 40 | 40.1
[45 empty] | CE190-CE180 | -771 | -770 | -774.839 | -774 |  | -769.6356 | -767.9826 | -774.839 | -767.9826 | 0.8908% | -769.6508 | -770.4 | -770 |  | E190-E180 | -3917 | -3918 | -3937.377 | -3956.0375 | -3906.9062 | -3917.4227 | -3916.4296 | -3956.0375 | -3906.9062 | 1.254% | -3917.7372 | -3917.6 | -3916.1
[45 empty] | CE190-CE140 | 81 | 81 | 84.624 | 82 |  | 81.6639 | 81.8837 | 81 | 84.624 | 4.444% | 81.5469 | 81.1 | 81.3 |  | E190-E140 | 380 | 379 | 377.077 | 383.939 | 378.0197 | 379.514 | 379.106 | 377.077 | 383.939 | 1.808% | 379.5607 | 379.4 | 380.4
[45 empty] | CE195-CE190 | 79 | 79 | 79.444 | 79 |  | 78.9721 | 79.6337 | 78.9721 | 79.6337 | 0.8254% | 80.1527 | 79.2 | 79.1 |  | E195-E190 | 24 | 24 | 22.633 | 23.1536 | 23.4 | 23.7619 | 23.6687 | 22.633 | 24 | 5.733% | 23.8465 | 23.9 | 23.5
[45 empty] | CE195-CE185 | -1123 | -1122 | -1123.814 | -1127 |  | -1120.4142 | -1116.2999 | -1127 | -1116.2999 | 0.9544% | -1121.176 | -1121.8 | -1121.4 |  | E195-E185 | -3905 | -3934 | -3969.654 | -3980.9496 | -3924.888 | -3933.5775 | -3932.6042 | -3980.9496 | -3905 | 1.931% | -3933.7487 | -3933.7 | -3932.7
[45 empty] | CE195-CE130 | 122 | 123 | 125.669 | 124 |  | 122.8356 | 123.242 | 122 | 125.669 | 2.975% | 123.3368 | 122.4 | 122.5 |  | E195-E130 | 383 | 382 | 379.462 | 386.5768 | 380.7006 | 381.9655 | 381.5695 | 379.462 | 386.5768 | 1.862% | 382.0203 | 381.9 | 382
[45 empty] | CE200-CE100 | -69 | -79 | -58.431 | -93 |  | -58.3094 | -49.8691 | -93 | -49.8691 | 61.59% | -70.0317 | -68.8 | -68.9 |  | E200-E100 | 1698 | 1636 | 1692.73 | 1728.0188 | 1686.8281 | 1697.8282 | 1699.6157 | 1636 | 1728.0188 | 5.421% | 1697.4409 | 1697.4 | 1697.4
[45 empty] | Del Q IDfan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Del Q coil,s (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL
[45 empty] | CE110-CE100 | -16 | -15 | -12.268 | -19 | -16.0147 | -15.9627 | -15.7035 | -19 | -12.268 | 42.28% | -15.9226 | -16.2 | -16.1 |  | E110-E100 | -35 | -34 | -37.89 | -38.3939 | -34.5797 | -35.1254 | -34.7129 | -38.3939 | -34 | 12.51% | -35.1161 | -35.4 | -35.1
[45 empty] | CE120-CE110 | -11 | -12 | -23.336 | -12 | -11.154 | -11.0148 | -11.1592 | -23.336 | -11 | 110% | -11.2183 | -11 | -11 |  | E120-E110 | -16 | -17 | -40.1 | -16.4127 | -16.1635 | -16.1818 | -16.4257 | -40.1 | -16 | 147.5% | -16.3418 | -16.2 | -16.8
[45 empty] | CE120-CE100 | -27 | -27 | -35.604 | -31 | -27.1687 | -26.9774 | -26.8627 | -35.604 | -26.8627 | 32.21% | -27.1409 | -27.2 | -27.1 |  | E120-E100 | -51 | -51 | -77.99 | -54.8066 | -50.7431 | -51.3072 | -51.1386 | -77.99 | -50.7431 | 52.95% | -51.4579 | -51.6 | -51.9
[45 empty] | CE130-CE100 | -134 | -134 | -136.869 | -133 | -133.2976 | -133.3883 | -131.9736 | -136.869 | -131.9736 | 3.663% | -133.646 | -133.8 | -133.7 |  | E130-E100 | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.6444 | -3580.7513 | -3578.1796 | -3625.692 | -3578.1796 | 1.327% | -3581.0058 | -3581.1 | -3581.2
[45 empty] | CE140-CE130 | -2 | -2 | -1.369 | -2 | -2.1553 | -2.1503 | -2.1761 | -2.1761 | -1.369 | 36.79% | -2.1936 | -2.2 | -2.2 |  | E140-E130 | -21 | -21 | -20.248 | -20.5158 | -20.719 | -21.3105 | -21.2052 | -21.3105 | -20.248 | 4.968% | -21.387 | -21.4 | -21.9
[45 empty] | CE140-CE110 | -120 | -121 | -125.97 | -116 | -119.4381 | -119.5759 | -118.4462 | -125.97 | -116 | 8.314% | -119.917 | -119.8 | -119.8 |  | E140-E110 | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.7837 | -3566.9364 | -3564.6719 | -3608.05 | -3560.9613 | 1.32% | -3567.2767 | -3567.1 | -3568
[45 empty] | CE150-CE110 | 13 | 12 | 0 | 14 | 12.711 | 13.1873 | 12.7446 | 0 | 14 | 107% | 13.0891 | 13.2 | 13.2 |  | E150-E110 | 13 | 12 | 0 | 30.4807 | 12.9618 | 13.1846 | 12.5854 | 0 | 30.4807 | 232.9% | 13.088 | 13.2 | 13.7
[45 empty] | CE160-CE150 | -12 | -12 | -13.865 | -15 | -11.9732 | -11.7613 | -11.1173 | -15 | -11.1173 | 32.6% | -11.9106 | -11.9 | -11.9 |  | E160-E150 | -17 | -17 | -26.402 | -16.9988 | -16.9902 | -16.9277 | -16.1348 | -26.402 | -16.1348 | 60.3% | -17.0265 | -17.1 | -18.2
[45 empty] | CE165-CE160 | 20 | 21 | 22.626 | 24 | 20.2603 | 20.246 | 19.6897 | 19.6897 | 24 | 21.78% | 19.7887 | 20.1 | 20.1 |  | E165-E160 | 37 | 37 | 51.08 | 39.5662 | 36.4558 | 37.0003 | 36.2248 | 36.2248 | 51.08 | 40.76% | 36.4472 | 37 | 37.8
[45 empty] | CE170-CE150 | -68 | -68 | -71.595 | -73 | -67.2399 | -67.7141 | -66.4261 | -73 | -66.4261 | 9.721% | -67.6284 | -67.9 | -67.9 |  | E170-E150 | -2285 | -2285 | -2316.723 | -2288.3939 | -2284.806 | -2285.3107 | -2283.3986 | -2316.723 | -2283.3986 | 1.458% | -2285.3048 | -2285.5 | -2285.9
[45 empty] | CE180-CE150 | -23 | -22 | -22.104 | -24 | -21.8663 | -22.3857 | -21.2749 | -24 | -21.2749 | 12.14% | -22.4474 | -22.5 | -22.6 |  | E180-E150 | -2241 | -2240 | -2250.396 | -2179.3669 | -2238.6808 | -2239.9843 | -2238.5215 | -2250.396 | -2179.3669 | 3.17% | -2240.5379 | -2240.1 | -2241.3
[45 empty] | CE180-CE170 | 45 | 46 | 49.491 | 49 | 45.3736 | 45.3284 | 45.1513 | 45 | 49.491 | 9.94% | 45.181 | 45.4 | 45.3 |  | E180-E170 | 44 | 45 | 66.327 | 109.027 | 46.1251 | 45.3264 | 44.8771 | 44 | 109.027 | 145.3% | 44.7669 | 45.4 | 44.6
[45 empty] | CE185-CE180 | 21 | 20 | 24.243 | 25 | 20.7271 | 20.7574 | 20.6923 | 20 | 25 | 24.25% | 20.6154 | 20.8 | 20.8 |  | E185-E180 | 11 | 40 | 54.91 | 46.0141 | 39.2553 | 39.9168 | 39.8232 | 11 | 54.91 | 110.3% | 39.8069 | 40 | 40
[45 empty] | CE190-CE180 | -100 | -101 | -96.662 | -98 | -100.3495 | -100.4635 | -99.9852 | -101 | -96.662 | 4.312% | -100.6027 | -100.6 | -100.5 |  | E190-E180 | -1329 | -1330 | -1350.177 | -1394.49 | -1330.9807 | -1330.2227 | -1329.2766 | -1394.49 | -1329 | 4.924% | -1329.9815 | -1330.4 | -1329.8
[45 empty] | CE190-CE140 | 10 | 10 | 7.204 | 8 | 9.9333 | 9.9142 | 9.9306 | 7.204 | 10 | 28.08% | 9.9559 | 9.9 | 9.9 |  | E190-E140 | 10 | 10 | 7.477 | 17.585 | 10.0839 | 9.914 | 9.4592 | 7.477 | 17.585 | 102.7% | 9.8452 | 9.8 | 10.6
[45 empty] | CE195-CE190 | 5 | 5 | 3.577 | 4 | 4.627 | 4.6017 | 4.6449 | 3.577 | 5 | 30.6% | 4.6509 | 4.6 | 4.6 |  | E195-E190 | 24 | 24 | 22.633 | 22.8605 | 23.1909 | 23.7619 | 23.71 | 22.633 | 24 | 5.736% | 23.8326 | 23.9 | 23.7
[45 empty] | CE195-CE185 | -116 | -116 | -117.328 | -119 | -116.4496 | -116.6191 | -116.0326 | -119 | -116 | 2.574% | -116.5672 | -116.8 | -116.7 |  | E195-E185 | -1316 | -1346 | -1382.454 | -1417.6436 | -1347.0452 | -1346.3775 | -1345.3897 | -1417.6436 | -1316 | 7.552% | -1345.9558 | -1346.5 | -1346.1
[45 empty] | CE195-CE130 | 13 | 13 | 9.412 | 10 | 12.405 | 12.3655 | 12.3994 | 9.412 | 13 | 28.9% | 12.4132 | 12.3 | 12.3 |  | E195-E130 | 13 | 13 | 9.862 | 19.9297 | 12.5558 | 12.3655 | 11.964 | 9.862 | 19.9297 | 81.91% | 12.2909 | 12.3 | 12.4
[45 empty] | CE200-CE100 | 10 | 9 | 3.966 | 10 | 9.8015 | 10.9119 | 12.1975 | 3.966 | 12.1975 | 79.09% | 10.4073 | 10.5 | 10.6 |  | E200-E100 | 476 | 415 | 471.706 | 508.7925 | 476.6119 | 476.8042 | 478.5917 | 415 | 508.7925 | 19.69% | 476.3346 | 476.4 | 476.4
[45 empty] | Del Q ODfan (kWh,e) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016 | Del Qcoil,lat (kWh,t) | [7 empty] | Statistics, All Results | [5 empty] | 11/1/2016
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+ |  | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | E+
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | NREL
[45 empty] | CE110-CE100 | -8 | -7 | -5.761 | -7 |  | -7.4954 | -7.374 | -8 | -5.761 | 29.95% | -7.4767 | -7.5 | -7.5 |  | E110-E100 | 0 | 0 | 0 | 0 | -0.0012361 | 0 | -3.0447e-14 | -0.0012361 | 0 |  | 0 | 0 | 0
[45 empty] | CE120-CE110 | -5 | -6 | -10.958 | -5 |  | -5.172 | -5.24 | -10.958 | -5 | 113.1% | -5.2677 | -5.2 | -5.2 |  | E120-E110 | 0 | 0 | 0 | 0 | 0.00051944 | 0 | 1.1191e-15 | 0 | 0.00051944 |  | 0 | 0 | 0
[45 empty] | CE120-CE100 | -13 | -13 | -16.719 | -12 |  | -12.6674 | -12.6139 | -16.719 | -12 | 37.03% | -12.7444 | -12.7 | -12.7 |  | E120-E100 | 0 | 0 | 0 | 0 | -0.00071667 | 0 | -2.9328e-14 | -0.00071667 | 0 |  | 0 | 0 | 0
[45 empty] | CE130-CE100 | -63 | -63 | -64.269 | -62 |  | -62.6344 | -61.9703 | -64.269 | -61.9703 | 3.663% | -62.7555 | -62.8 | -62.8 |  | E130-E100 | 0 | 0 | 0 | 0 | -0.0041511 | 0 | -1.7231e-15 | -0.0041511 | 0 |  | 0 | 0 | 0
[45 empty] | CE140-CE130 | -1 | -1 | -0.643 | -1 |  | -1.0097 | -1.0218 | -1.0218 | -0.643 | 36.78% | -1.03 | -1 | -1 |  | E140-E130 | 0 | 0 | 0 | 0 | -0.00011694 | 0 | -3.169e-14 | -0.00011694 | 0 |  | 0 | 0 | 0
[45 empty] | CE140-CE110 | -56 | -57 | -59.151 | -56 |  | -56.1487 | -55.6182 | -59.151 | -55.6182 | 6.274% | -56.3088 | -56.3 | -56.3 |  | E140-E110 | 0 | 0 | 0 | 0 | -0.0030319 | 0 | -2.9665e-15 | -0.0030319 | 0 |  | 0 | 0 | 0
[45 empty] | CE150-CE110 | 6 | 5 | 0 | 5 |  | 6.1925 | 5.9844 | 0 | 6.1925 | 100.8% | 6.1462 | 6.2 | 6.1 |  | E150-E110 | 739 | 739 | 739.2 | 741.5006 | 732.6919 | 739.2 | 739.2069 | 732.6919 | 741.5006 | 1.192% | 739.1956 | 739.2 | 739.4
[45 empty] | CE160-CE150 | -5 | -5 | -6.51 | -5 |  | -5.5228 | -5.2203 | -6.51 | -5 | 27% | -5.5928 | -5.6 | -5.5 |  | E160-E150 | 1 | 0 | 0 | -2.0516 | -0.68366 | 0 | -0.01221 | -2.0516 | 1 |  | 0.043984 | 0 | -0.3
[45 empty] | CE165-CE160 | 9 | 9 | 10.624 | 9 |  | 9.5064 | 9.2456 | 9 | 10.624 | 17.48% | 9.2921 | 9.4 | 9.4 |  | E165-E160 | 0 | 0 | 0 | 0.87925 | 1.1548 | 0 | -0.00548 | -0.00548 | 1.1548 |  | 0.005862 | 0 | 0.2
[45 empty] | CE170-CE150 | -32 | -32 | -33.618 | -31 |  | -31.7964 | -31.1915 | -33.618 | -31 | 8.244% | -31.756 | -31.9 | -31.8 |  | E170-E150 | 1 | 0 | 0 | -2.6377 | 0.95111 | 0 | 0.00465 | -2.6377 | 1 |  | 0.12011 | 0 | 0
[45 empty] | CE180-CE150 | -10 | -10 | -10.379 | -9 |  | -10.5117 | -9.99 | -10.5117 | -9 | 14.34% | -10.5405 | -10.6 | -10.5 |  | E180-E150 | 2219 | 2218 | 2217.6 | 2186.4009 | 2211.1664 | 2217.6 | 2217.5924 | 2186.4009 | 2219 | 1.47% | 2218.2757 | 2217.6 | 2216.7
[45 empty] | CE180-CE170 | 22 | 22 | 23.239 | 22 |  | 21.2847 | 21.2015 | 21.2015 | 23.239 | 9.604% | 21.2154 | 21.3 | 21.3 |  | E180-E170 | 2218 | 2218 | 2217.6 | 2189.0387 | 2210.2153 | 2217.6 | 2217.5877 | 2189.0387 | 2218 | 1.306% | 2218.1556 | 2217.6 | 2216.7
[45 empty] | CE185-CE180 | 9 | 9 | 11.384 | 10 |  | 9.7468 | 9.7164 | 9 | 11.384 | 24.63% | 9.6803 | 9.7 | 9.7 |  | E185-E180 | 1 | 0 | 0 | 2.0516 | 2.1265 | 0 | 0.02022 | 0 | 2.1265 |  | 0.051109 | 0 | 0.1
[45 empty] | CE190-CE180 | -48 | -47 | -45.389 | -48 |  | -47.1741 | -46.9496 | -48 | -45.389 | 5.527% | -47.2395 | -47.2 | -47.2 |  | E190-E180 | -2588 | -2587 | -2587.2 | -2561.5475 | -2575.9255 | -2587.2 | -2587.1524 | -2588 | -2561.5475 | 1.022% | -2587.7557 | -2587.2 | -2586.3
[45 empty] | CE190-CE140 | 4 | 5 | 3.383 | 4 |  | 4.6553 | 4.6631 | 3.383 | 5 | 34.59% | 4.6749 | 4.7 | 4.7 |  | E190-E140 | 370 | 370 | 369.6 | 366.354 | 367.9358 | 369.6 | 369.6468 | 366.354 | 370 | 0.9862% | 369.7156 | 369.6 | 369.8
[45 empty] | CE195-CE190 | 3 | 2 | 1.679 | 3 |  | 2.1608 | 2.1811 | 1.679 | 3 | 60.49% | 2.1839 | 2.1 | 2.1 |  | E195-E190 | 0 | 0 | 0 | 0.29308 | 0.20914 | 0 | -0.041346 | -0.041346 | 0.29308 |  | 0.013833 | 0 | -0.2
[45 empty] | CE195-CE185 | -54 | -54 | -55.094 | -55 |  | -54.7601 | -54.4849 | -55.094 | -54 | 1.999% | -54.7359 | -54.8 | -54.8 |  | E195-E185 | -2589 | -2587 | -2587.2 | -2563.306 | -2577.8429 | -2587.2 | -2587.214 | -2589 | -2563.306 | 0.9929% | -2587.793 | -2587.2 | -2586.6
[45 empty] | CE195-CE130 | 6 | 6 | 4.419 | 6 |  | 5.8064 | 5.8223 | 4.419 | 6 | 27.12% | 5.8288 | 5.8 | 5.8 |  | E195-E130 | 370 | 370 | 369.6 | 366.6471 | 368.1448 | 369.6 | 369.6055 | 366.6471 | 370 | 0.9068% | 369.7294 | 369.6 | 369.6
[45 empty] | CE200-CE100 | 5 | 4 | 1.862 | 4 |  | 5.124 | 5.7274 | 1.862 | 5.7274 | 79.1% | 4.8869 | 5 | 5 |  | E200-E100 | 1222 | 1221 | 1221 | 1219.2263 | 1210.2163 | 1221.024 | 1221.024 | 1210.2163 | 1222 | 0.965% | 1221.1063 | 1221 | 1221
[47 empty] | results5-3.xls q:ck491..cz580; 10/15/02 | [12 empty] | results5-3.xls q:db491..dq580; 10/15/02

## Data-Electr
Space Cooling Electricity Consumption
Energy Consumption, Total (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 1531 | 1530 | 1520.817 | 1519 | 1520.0282 | 1522.2661 | 1511.9369 | 1530.548 | 1530.8 | 1530.6
CE110 as100 lo ODB | 1077 | 1089 | 1061.196 | 1065 | 1069.0685 | 1066.9607 | 1061.9658 | 1076.2349 | 1077.2 | 1077.4
CE120 as100 hiIDB | 1012 | 1012 | 1011.104 | 1003 | 1006.3903 | 1007.3023 | 1001.6637 | 1012.6774 | 1011 | 1011
CE130 as100 lo PLR | 110 | 109 | 105.419 | 106 | 108.5963 | 108.7246 | 110.1161 | 110.5818 | 109.5 | 109.5
CE140 as130 lo ODB | 68 | 69 | 65.008 | 66 | 67.903 | 67.7641 | 68.6428 | 68.9953 | 68.5 | 68.3
CE150 as110 hiSHR | 1208 | 1207 | 1202.424 | 1183 | 1197.1085 | 1199.055 | 1191.613 | 1206.49 | 1206.5 | 1206.5
CE160 as150 hiIDB | 1140 | 1139 | 1137.63 | 1107 | 1131.7342 | 1136.7334 | 1132.8835 | 1140.44 | 1139.3 | 1138.9
CE165 as150 mIDB mODB | 1502 | 1501 | 1499.447 | 1470 | 1491.0755 | 1499.7105 | 1489.9268 | 1497.8302 | 1499.7 | 1499.6
CE170 as150 mSHR mPLR | 638 | 638 | 629.076 | 620 | 635.3716 | 635.909 | 635.8287 | 641.1173 | 637.7 | 637.8
CE180 as150 loSHR | 1083 | 1082 | 1077.109 | 1080 | 1082.0002 | 1081.2706 | 1080.0377 | 1082.666 | 1082.3 | 1081.9
CE185 loSHR hiODB | 1544 | 1543 | 1541.155 | 1547 | 1540.3879 | 1541.5256 | 1538.3972 | 1544.6397 | 1543.4 | 1542.9
CE190 as180 loPLR | 164 | 164 | 160.219 | 160 | 164.3348 | 163.9975 | 165.1202 | 165.173 | 164.1 | 164.2
CE195 as185 loPLR | 250 | 250 | 244.919 | 246 | 250.2299 | 249.7321 | 251.5799 | 252.1605 | 250 | 250
CE200 ARI PLR=1 hiSHR | 1477 | 1464 | 1468.214 | 1440 | 1464.5945 | 1479.9926 | 1479.9926 | 1475.8104 | 1477.4 | 1477.1
Energy Consumption, Compressor (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 1319 | 1318 | 1307.458 | 1311 | 0 | 1311.1661 | 1302.7258 | 1318.8515 | 1319 | 1318.9
CE110 as100 lo ODB | 889 | 899 | 865.866 | 883 | 0 | 879.3187 | 875.8322 | 887.9378 | 889.2 | 889.4
CE120 as100 hiIDB | 840 | 840 | 850.068 | 838 | 0 | 835.847 | 831.9292 | 840.8662 | 839.1 | 839.2
CE130 as100 lo PLR | 95 | 94 | 93.198 | 93 | 0 | 93.6472 | 94.8489 | 95.2867 | 94.4 | 94.3
CE140 as130 lo ODB | 57 | 57 | 54.799 | 56 | 0 | 55.8468 | 56.5735 | 56.924 | 56.5 | 56.4
CE150 as110 hiSHR | 1000 | 999 | 1007.094 | 982 | 0 | 992.0333 | 986.7503 | 998.9576 | 999.2 | 999.2
CE160 as150 hiIDB | 950 | 949 | 962.675 | 926 | 0 | 946.9958 | 944.3585 | 950.4111 | 949.4 | 949.1
CE165 as150 mIDB mODB | 1283 | 1281 | 1291.242 | 1256 | 0 | 1280.2205 | 1272.4664 | 1278.7205 | 1280.2 | 1280.2
CE170 as150 mSHR mPLR | 531 | 530 | 538.959 | 523 | 0 | 528.3976 | 528.5837 | 532.9693 | 530 | 530.1
CE180 as150 loSHR | 909 | 908 | 914.262 | 912 | 0 | 907.1462 | 906.4398 | 908.1216 | 908 | 907.7
CE185 loSHR hiODB | 1340 | 1339 | 1342.681 | 1344 | 0 | 1336.897 | 1334.3908 | 1339.7996 | 1338.6 | 1338.2
CE190 as180 loPLR | 138 | 138 | 139.423 | 138 | 0 | 137.5107 | 138.4572 | 138.4708 | 137.6 | 137.7
CE195 as185 loPLR | 217 | 217 | 218.867 | 217 | 0 | 216.4828 | 218.0909 | 218.6235 | 216.8 | 216.8
CE200 ARI PLR=1 hiSHR | 1250 | 1239 | 1249.027 | 1218 | 0 | 1252.8566 | 1252.8566 | 1248.8198 | 1250.2 | 1250
Energy Consumption, Supply Fan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 144 | 144 | 145.185 | 141 | 143.5533 | 143.6481 | 142.3625 | 144.0538 | 144.1 | 144
CE110 as100 lo ODB | 128 | 129 | 132.917 | 122 | 127.5385 | 127.6854 | 126.659 | 128.1312 | 127.9 | 127.9
CE120 as100 hiIDB | 117 | 117 | 109.581 | 110 | 116.3845 | 116.6706 | 115.4998 | 116.9129 | 116.9 | 116.9
CE130 as100 lo PLR | 10 | 10 | 8.316 | 8 | 10.2557 | 10.2598 | 10.3889 | 10.4079 | 10.3 | 10.3
CE140 as130 lo ODB | 8 | 8 | 6.947 | 6 | 8.1004 | 8.1094 | 8.2128 | 8.2142 | 8.1 | 8.1
CE150 as110 hiSHR | 141 | 141 | 132.917 | 136 | 140.2495 | 140.8727 | 139.4036 | 141.2203 | 141.1 | 141.1
CE160 as150 hiIDB | 129 | 129 | 119.052 | 121 | 128.2763 | 129.1114 | 128.2863 | 129.3096 | 129.2 | 129.2
CE165 as150 mIDB mODB | 149 | 150 | 141.678 | 145 | 148.5366 | 149.3574 | 147.976 | 149.0983 | 149.3 | 149.3
CE170 as150 mSHR mPLR | 73 | 73 | 61.322 | 63 | 73.0096 | 73.1586 | 72.9774 | 73.5918 | 73.2 | 73.2
CE180 as150 loSHR | 118 | 119 | 110.813 | 112 | 118.3832 | 118.487 | 118.1287 | 118.7728 | 118.6 | 118.5
CE185 loSHR hiODB | 139 | 139 | 135.056 | 137 | 139.1103 | 139.2444 | 138.821 | 139.3882 | 139.4 | 139.3
CE190 as180 loPLR | 18 | 18 | 14.151 | 14 | 18.0337 | 18.0236 | 18.1435 | 18.1701 | 18 | 18
CE195 as185 loPLR | 23 | 23 | 17.728 | 18 | 22.6607 | 22.6253 | 22.7884 | 22.821 | 22.6 | 22.6
CE200 ARI PLR=1 hiSHR | 154 | 153 | 149.151 | 151 | 153.3548 | 154.56 | 154.56 | 154.4611 | 154.6 | 154.6
Energy Consumption, Condenser Fan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 68 | 68 | 68.174 | 67 | 0 | 67.452 | 66.8486 | 67.6427 | 67.6 | 67.6
CE110 as100 lo ODB | 60 | 61 | 62.413 | 60 | 0 | 59.9566 | 59.4747 | 60.166 | 60.1 | 60.1
CE120 as100 hiIDB | 55 | 55 | 51.455 | 55 | 0 | 54.7846 | 54.2347 | 54.8982 | 54.9 | 54.9
CE130 as100 lo PLR | 5 | 5 | 3.905 | 5 | 0 | 4.8176 | 4.8783 | 4.8872 | 4.8 | 4.8
CE140 as130 lo ODB | 4 | 4 | 3.262 | 4 | 0 | 3.8079 | 3.8565 | 3.8571 | 3.8 | 3.8
CE150 as110 hiSHR | 66 | 66 | 62.413 | 65 | 0 | 66.1491 | 65.4591 | 66.3121 | 66.3 | 66.2
CE160 as150 hiIDB | 61 | 61 | 55.903 | 60 | 0 | 60.6262 | 60.2388 | 60.7193 | 60.7 | 60.7
CE165 as150 mIDB mODB | 70 | 70 | 66.527 | 69 | 0 | 70.1326 | 69.4843 | 70.0114 | 70.1 | 70.1
CE170 as150 mSHR mPLR | 34 | 34 | 28.795 | 34 | 0 | 34.3527 | 34.2676 | 34.5562 | 34.4 | 34.4
CE180 as150 loSHR | 56 | 56 | 52.034 | 56 | 0 | 55.6374 | 55.4691 | 55.7716 | 55.7 | 55.7
CE185 loSHR hiODB | 65 | 65 | 63.418 | 66 | 0 | 65.3842 | 65.1855 | 65.4519 | 65.4 | 65.4
CE190 as180 loPLR | 8 | 9 | 6.645 | 8 | 0 | 8.4632 | 8.5195 | 8.5321 | 8.5 | 8.5
CE195 as185 loPLR | 11 | 11 | 8.324 | 11 | 0 | 10.6241 | 10.7006 | 10.716 | 10.6 | 10.6
CE200 ARI PLR=1 hiSHR | 73 | 72 | 70.036 | 71 | 0 | 72.576 | 72.576 | 72.5296 | 72.6 | 72.6

## Data-COP
COP: Mean, and (Max-Min)/Mean
Mean COP
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | 0 | Analytical | 0 | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 2.39 | 2.389 | 2.4304 | 2.4064 | 2.404 | 2.4017 | 2.4184 | 2.3889 | 2.39 | 2.39
CE110 as100 lo ODB | 3.38 | 3.342 | 3.4589 | 3.4146 | 3.4007 | 3.4087 | 3.4271 | 3.3795 | 3.38 | 3.38
CE120 as100 hiIDB | 3.59 | 3.59 | 3.6139 | 3.623 | 3.6075 | 3.6054 | 3.6313 | 3.5865 | 3.59 | 3.59
CE130 as100 lo PLR | 1.91 | 1.909 | 1.9752 | 1.953 | 1.9038 | 1.9198 | 1.9163 | 1.8895 | 1.91 | 1.91
CE140 as130 lo ODB | 2.77 | 2.734 | 2.9151 | 2.854 | 2.7714 | 2.7974 | 2.7996 | 2.7502 | 2.77 | 2.77
CE150 as110 hiSHR | 3.62 | 3.63 | 3.6675 | 3.7 | 3.6544 | 3.6496 | 3.6734 | 3.6273 | 3.63 | 3.63
CE160 as150 hiIDB | 3.84 | 3.84 | 3.8658 | 3.95 | 3.8611 | 3.8452 | 3.8599 | 3.8329 | 3.84 | 3.84
CE165 as150 mIDB mODB | 2.92 | 2.92 | 2.9514 | 2.9853 | 2.9415 | 2.9257 | 2.9449 | 2.9295 | 2.93 | 2.93
CE170 as150 mSHR mPLR | 3.38 | 3.39 | 3.4423 | 3.477 | 3.3951 | 3.3944 | 3.4033 | 3.3672 | 3.39 | 3.39
CE180 as150 loSHR | 4.04 | 4.04 | 4.0842 | 4.026 | 4.0432 | 4.0472 | 4.055 | 4.0423 | 4.04 | 4.04
CE185 loSHR hiODB | 2.85 | 2.85 | 2.8744 | 2.823 | 2.8521 | 2.8512 | 2.8574 | 2.8458 | 2.85 | 2.85
CE190 as180 loPLR | 3.41 | 3.41 | 3.4865 | 3.457 | 3.3942 | 3.4096 | 3.4048 | 3.3865 | 3.41 | 3.41
CE195 as185 loPLR | 2.31 | 2.31 | 2.3598 | 2.337 | 2.3033 | 2.3158 | 2.3054 | 2.2944 | 2.31 | 2.31
CE200 ARI PLR=1 hiSHR | 3.62 | 3.61 | 3.6677 | 3.708 | 3.6471 | 3.6102 | 3.6102 | 3.6206 | 3.62 | 3.62
(Max - Min)/Mean COP
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 0 | 0.00083717 | 0.0015062 | 0.0012467 | 0.0026072 | 0 | 0 | 0 |  | 0.00012552
CE110 as100 lo ODB | 0 | 0.010473 | 0.0017378 | 0.0011714 | 0.0027731 | 0 | 0.010592 | 0 |  | 0.00038462
CE120 as100 hiIDB | 0 | 0.0036212 | 0.00079758 | 0.0011041 | 0.0027415 | 0 | 0.012271 | 0 |  | 0.00030641
CE130 as100 lo PLR | 0 | 0.03824 | 0.012602 | 0.0087046 | 0.0037428 | 0 | 0.17198 | 0 |  | -5.2356e-05
CE140 as130 lo ODB | 0 | 0.055962 | 0.010989 | 0.018921 | 0.0038004 | 0 | 0.20433 | 0 |  | 3.6101e-05
CE150 as110 hiSHR | 0.0027624 | 0.0027548 | 0.0014674 | 0.0048649 | 0.010553 | 0 | 0.0092759 | 0 |  | 0.00096419
CE160 as150 hiIDB | 0.0026042 | 0.0052083 | 0.0010614 | 0.0032911 | 0.011024 | 0 | 0.010193 | 0 |  | 0.00026042
CE165 as150 mIDB mODB | 0.010274 | 0.0034247 | 0.0012002 | 0.0026798 | 0.011921 | 0 | 0.0084429 | 0 |  | 0.00030717
CE170 as150 mSHR mPLR | 0 | 0.0058997 | 0.0021466 | 0.0040265 | 0.015183 | 0 | 0.043444 | 0 |  | 0.00026549
CE180 as150 loSHR | 0.0049505 | 0.0024752 | 0.0023307 | 0.009687 | 0.029331 | 0 | 0.011687 | 0 |  | 4.9505e-05
CE185 loSHR hiODB | 0.0070175 | 0.0035088 | 0.0023597 | 0.010273 | 0.034252 | 0 | 0.0091078 | 0 |  | 0.00017544
CE190 as180 loPLR | 0 | 0.02346 | 0.0071705 | 0.018802 | 0.039563 | 0 | 0.10066 | 0 |  | -8.7977e-05
CE195 as185 loPLR | 0 | 0.017316 | 0.0078108 | 0.016688 | 0.043389 | 0 | 0.08606 | 0 |  | 0.00012987
CE200 ARI PLR=1 hiSHR | 0.0055249 | 0 | -1.2839e-05 | 0.0051241 | 0.011968 | 0 | 0 | 0 |  | 8.2873e-05

## Data-Loads
Zone Loads: Total, Sensible, and Latent
Zone Load, Total (kWh,thermal)
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 3656 | 3656 | 3654.42 | 3655.3341 | 3654.1272 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3
CE110 as100 lo ODB | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5345 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1
CE120 as100 hiIDB | 3632 | 3632 | 3630.472 | 3631.5944 | 3630.5353 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9
CE130 as100 lo PLR | 209 | 209 | 207.344 | 207.5029 | 206.7475 | 208.7252 | 209.371 | 208.9462 | 209 | 209
CE140 as130 lo ODB | 190 | 190 | 188.503 | 188.4525 | 188.1832 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7
CE150 as110 hiSHR | 4376 | 4376 | 4374.801 | 4376.0258 | 4374.7468 | 4376.1245 | 4375.5775 | 4376.3129 | 4376.3 | 4376.3
CE160 as150 hiIDB | 4371 | 4371 | 4369.652 | 4371.0434 | 4369.7196 | 4370.9568 | 4370.6181 | 4371.1893 | 4371.1 | 4371.1
CE165 as150 mIDB mODB | 4388 | 4388 | 4386.071 | 4387.456 | 4385.9248 | 4387.7098 | 4387.1605 | 4387.8381 | 4387.9 | 4387.9
CE170 as150 mSHR mPLR | 2159 | 2159 | 2157.351 | 2157.9719 | 2157.1388 | 2158.5245 | 2158.621 | 2158.7129 | 2158.7 | 2158.7
CE180 as150 loSHR | 4376 | 4376 | 4374.852 | 4376.0258 | 4374.7389 | 4376.1245 | 4375.9707 | 4376.3129 | 4376.3 | 4376.3
CE185 loSHR hiODB | 4396 | 4396 | 4393.649 | 4394.7831 | 4393.3107 | 4395.2832 | 4395.0925 | 4395.5062 | 4395.5 | 4395.5
CE190 as180 loPLR | 557 | 559 | 558.09 | 558.0305 | 557.7813 | 559.1652 | 559.4558 | 559.3529 | 559.3 | 559.3
CE195 as185 loPLR | 576 | 579 | 576.926 | 577.0809 | 576.347 | 578.3252 | 578.542 | 578.5462 | 578.6 | 578.6
CE200 ARI PLR=1 hiSHR | 5343 | 5283 | 5341.526 | 5342.9074 | 5341.5034 | 5343.0048 | 5343.0048 | 5343.2549 | 5343.2 | 5343.2
Zone Load, Sensible (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 3656 | 3656 | 3654.42 | 3655.3341 | 3654.1272 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3
CE110 as100 lo ODB | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5345 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1
CE120 as100 hiIDB | 3632 | 3632 | 3630.472 | 3631.5944 | 3630.5353 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9
CE130 as100 lo PLR | 209 | 209 | 207.344 | 207.5029 | 206.7475 | 208.7252 | 209.371 | 208.9462 | 209 | 209
CE140 as130 lo ODB | 190 | 190 | 188.503 | 188.4525 | 188.1832 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7
CE150 as110 hiSHR | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.5501 | 3636.9245 | 3636.3775 | 3637.1129 | 3637.1 | 3637.1
CE160 as150 hiIDB | 3632 | 3632 | 3630.452 | 3631.5944 | 3630.5229 | 3631.7568 | 3631.4181 | 3631.9893 | 3631.9 | 3631.9
CE165 as150 mIDB mODB | 3649 | 3649 | 3646.871 | 3648.007 | 3646.7281 | 3648.5098 | 3647.9605 | 3648.6381 | 3648.7 | 3648.7
CE170 as150 mSHR mPLR | 1420 | 1420 | 1418.151 | 1418.5229 | 1417.9388 | 1419.3245 | 1419.421 | 1419.5129 | 1419.5 | 1419.5
CE180 as150 loSHR | 1420 | 1420 | 1418.052 | 1418.5229 | 1417.9523 | 1419.3245 | 1419.1707 | 1419.5129 | 1419.5 | 1419.5
CE185 loSHR hiODB | 1439 | 1439 | 1436.849 | 1437.2802 | 1436.5241 | 1438.4832 | 1438.2925 | 1438.7062 | 1438.7 | 1438.7
CE190 as180 loPLR | 190 | 190 | 188.49 | 188.4525 | 188.1822 | 189.5652 | 189.8558 | 189.7529 | 189.7 | 189.7
CE195 as185 loPLR | 209 | 209 | 207.326 | 207.5029 | 206.7479 | 208.7252 | 208.942 | 208.9462 | 209 | 209
CE200 ARI PLR=1 hiSHR | 4122 | 4062 | 4120.502 | 4121.6295 | 4120.521 | 4121.9808 | 4121.9808 | 4122.2309 | 4122.2 | 4122.2
Zone Load, Latent (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE150 as110 hiSHR | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2
CE160 as150 hiIDB | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2
CE165 as150 mIDB mODB | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2
CE170 as150 mSHR mPLR | 739 | 739 | 739.2 | 739.449 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2
CE180 as150 loSHR | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8
CE185 loSHR hiODB | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8
CE190 as180 loPLR | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6
CE195 as185 loPLR | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6
CE200 ARI PLR=1 hiSHR | 1221 | 1221 | 1221.024 | 1221.2778 | 1220.9824 | 1221.024 | 1221.024 | 1221.024 | 1221 | 1221
Latent Coil - Zone Load, (Should be 0) (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 0.0049461 | 0 | 3.3138e-14 | 0 | 0 | 0
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 0.00371 | 0 | 2.6912e-15 | 0 | 0 | 0
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 0.0042294 | 0 | 3.8103e-15 | 0 | 0 | 0
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 0.000795 | 0 | 3.1415e-14 | 0 | 0 | 0
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 0.00067806 | 0 | -2.7533e-16 | 0 | 0 | 0
CE150 as110 hiSHR | 0 | 0 | 0 | 2.0516 | -6.5011 | 0 | 0.00687 | -0.0044111 | 0 | 0.2
CE160 as150 hiIDB | 1 | 0 | 0 | 0 | -7.1847 | 0 | -0.00534 | 0.039573 | 0 | -0.1
CE165 as150 mIDB mODB | 1 | 0 | 0 | 0.87925 | -6.03 | 0 | -0.01082 | 0.045435 | 0 | 0.1
CE170 as150 mSHR mPLR | 1 | 0 | 0 | -0.58617 | -5.5533 | 0 | 0.01152 | 0.1157 | 0 | 0.2
CE180 as150 loSHR | 1 | 0 | 0 | -29.6014 | -12.9246 | 0 | -0.00076 | 0.67126 | 0 | -0.7
CE185 loSHR hiODB | 2 | 0 | 0 | -27.5498 | -10.7981 | 0 | 0.01946 | 0.72237 | 0 | -0.6
CE190 as180 loPLR | 3 | 0 | 0 | -3.2239 | -1.6626 | 0 | 0.046846 | 0.11557 | 0 | 0.2
CE195 as185 loPLR | 3 | 0 | 0 | -2.9308 | -1.4535 | 0 | 0.0055 | 0.1294 | 0 | 0
CE200 ARI PLR=1 hiSHR | 1 | 0 | -0.024 | -2.0516 | -10.7612 | 0 | 0 | 0.082262 | 0 | 0
Coil Loads: Total, Sensible, and Latent
Coil Load, Total (kWh,thermal)
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 3800 | 3800 | 3841.47 | 3793.9625 | 3797.6497 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4
CE110 as100 lo ODB | 3765 | 3766 | 3803.58 | 3755.5686 | 3763.0688 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3
CE120 as100 hiIDB | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.9059 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5
CE130 as100 lo PLR | 219 | 219 | 215.778 | 215.1231 | 217.0012 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2
CE140 as130 lo ODB | 198 | 198 | 195.53 | 194.6073 | 196.2821 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3
CE150 as110 hiSHR | 4517 | 4517 | 4542.78 | 4527.5498 | 4508.7225 | 4516.9958 | 4515.0285 | 4517.5274 | 4517.4 | 4518.3
CE160 as150 hiIDB | 4501 | 4500 | 4516.378 | 4508.4994 | 4491.0487 | 4500.0682 | 4498.8816 | 4500.5449 | 4500.3 | 4499.9
CE165 as150 mIDB mODB | 4538 | 4538 | 4567.458 | 4548.9449 | 4528.6592 | 4537.0685 | 4535.1008 | 4536.998 | 4537.3 | 4537.9
CE170 as150 mSHR mPLR | 2233 | 2232 | 2226.057 | 2236.5182 | 2224.8677 | 2231.6851 | 2231.6345 | 2232.3427 | 2231.9 | 2232.5
CE180 as150 loSHR | 4495 | 4495 | 4509.984 | 4534.5838 | 4481.208 | 4494.6115 | 4494.0999 | 4495.2651 | 4494.9 | 4493.8
CE185 loSHR hiODB | 4507 | 4535 | 4564.894 | 4582.6495 | 4522.5899 | 4534.5283 | 4533.9432 | 4535.1231 | 4534.9 | 4533.9
CE190 as180 loPLR | 578 | 577 | 572.607 | 578.5463 | 574.3018 | 577.1889 | 577.6703 | 577.5279 | 577.3 | 577.7
CE195 as185 loPLR | 602 | 601 | 595.24 | 601.6999 | 597.7018 | 600.9508 | 601.339 | 601.3744 | 601.2 | 601.2
CE200 ARI PLR=1 hiSHR | 5498 | 5436 | 5534.2 | 5521.9812 | 5484.4779 | 5497.5648 | 5497.5648 | 5497.8008 | 5497.8 | 5497.8
Coil Load, Sensible (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 3800 | 3800 | 3841.47 | 3793.9625 | 3797.6448 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4
CE110 as100 lo ODB | 3765 | 3766 | 3803.58 | 3755.5686 | 3763.0651 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3
CE120 as100 hiIDB | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.9017 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5
CE130 as100 lo PLR | 219 | 219 | 215.778 | 215.1231 | 217.0004 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2
CE140 as130 lo ODB | 198 | 198 | 195.53 | 194.6073 | 196.2815 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3
CE150 as110 hiSHR | 3778 | 3778 | 3803.58 | 3786.0492 | 3776.027 | 3777.7958 | 3775.8216 | 3778.3318 | 3778.2 | 3779
CE160 as150 hiIDB | 3761 | 3761 | 3777.178 | 3769.0504 | 3759.0367 | 3760.8682 | 3759.6868 | 3761.3053 | 3761.1 | 3760.8
CE165 as150 mIDB mODB | 3798 | 3798 | 3828.258 | 3808.6166 | 3795.4926 | 3797.8685 | 3795.9117 | 3797.7525 | 3798.1 | 3798.6
CE170 as150 mSHR mPLR | 1493 | 1493 | 1486.857 | 1497.6553 | 1491.221 | 1492.4851 | 1492.423 | 1493.027 | 1492.7 | 1493.1
CE180 as150 loSHR | 1537 | 1538 | 1553.184 | 1606.6823 | 1537.3461 | 1537.8115 | 1537.3001 | 1537.7939 | 1538.1 | 1537.7
CE185 loSHR hiODB | 1548 | 1578 | 1608.094 | 1652.6964 | 1576.6014 | 1577.7283 | 1577.1233 | 1577.6007 | 1578.1 | 1577.7
CE190 as180 loPLR | 208 | 208 | 203.007 | 212.1923 | 206.3654 | 207.5889 | 208.0235 | 207.8123 | 207.7 | 207.9
CE195 as185 loPLR | 232 | 232 | 225.64 | 235.0528 | 229.5563 | 231.3508 | 231.7335 | 231.645 | 231.6 | 231.6
CE200 ARI PLR=1 hiSHR | 4276 | 4215 | 4313.176 | 4302.755 | 4274.2567 | 4276.5408 | 4276.5408 | 4276.6945 | 4276.8 | 4276.8
Coil Load, Latent (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 0.0049461 | 0 | 3.3138e-14 | 0 | 0 | 0
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 0.00371 | 0 | 2.6912e-15 | 0 | 0 | 0
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 0.0042294 | 0 | 3.8103e-15 | 0 | 0 | 0
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 0.000795 | 0 | 3.1415e-14 | 0 | 0 | 0
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 0.00067806 | 0 | -2.7533e-16 | 0 | 0 | 0
CE150 as110 hiSHR | 739 | 739 | 739.2 | 741.5006 | 732.6956 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4
CE160 as150 hiIDB | 740 | 739 | 739.2 | 739.449 | 732.0119 | 739.2 | 739.1947 | 739.2396 | 739.2 | 739.1
CE165 as150 mIDB mODB | 740 | 739 | 739.2 | 740.3283 | 733.1667 | 739.2 | 739.1892 | 739.2454 | 739.2 | 739.3
CE170 as150 mSHR mPLR | 740 | 739 | 739.2 | 738.8628 | 733.6467 | 739.2 | 739.2115 | 739.3157 | 739.2 | 739.4
CE180 as150 loSHR | 2958 | 2957 | 2956.8 | 2927.9015 | 2943.8619 | 2956.8 | 2956.7992 | 2957.4713 | 2956.8 | 2956.1
CE185 loSHR hiODB | 2959 | 2957 | 2956.8 | 2929.9531 | 2945.9884 | 2956.8 | 2956.8195 | 2957.5224 | 2956.8 | 2956.2
CE190 as180 loPLR | 370 | 370 | 369.6 | 366.354 | 367.9364 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8
CE195 as185 loPLR | 370 | 370 | 369.6 | 366.6471 | 368.1456 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6
CE200 ARI PLR=1 hiSHR | 1222 | 1221 | 1221 | 1219.2263 | 1210.2212 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221
Sensible Coil - Zone Load, (Fan Heat) (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 144 | 144 | 187.05 | 138.6284 | 143.5176 | 143.6534 | 142.3632 | 144.0536 | 144.1 | 144.1
CE110 as100 lo ODB | 128 | 129 | 167.979 | 118.9918 | 127.5306 | 127.6867 | 126.6828 | 128.1309 | 127.9 | 128.2
CE120 as100 hiIDB | 117 | 117 | 133.008 | 107.5615 | 116.3664 | 116.6726 | 115.4889 | 116.9127 | 116.9 | 116.6
CE130 as100 lo PLR | 10 | 10 | 8.434 | 7.6202 | 10.2529 | 10.2601 | 10.3985 | 10.4079 | 10.3 | 10.2
CE140 as130 lo ODB | 8 | 8 | 7.027 | 6.1547 | 8.0983 | 8.1097 | 8.2063 | 8.2142 | 8.2 | 7.6
CE150 as110 hiSHR | 141 | 141 | 167.979 | 149.4725 | 140.4768 | 140.8714 | 139.4441 | 141.2189 | 141.1 | 141.9
CE160 as150 hiIDB | 129 | 129 | 146.726 | 137.456 | 128.5138 | 129.1114 | 128.2687 | 129.316 | 129.2 | 128.9
CE165 as150 mIDB mODB | 149 | 149 | 181.387 | 160.6096 | 148.7644 | 149.3587 | 147.9512 | 149.1144 | 149.4 | 149.9
CE170 as150 mSHR mPLR | 73 | 73 | 68.706 | 79.1325 | 73.2822 | 73.1606 | 73.002 | 73.5141 | 73.2 | 73.6
CE180 as150 loSHR | 117 | 118 | 135.132 | 188.1594 | 119.3938 | 118.487 | 118.1294 | 118.281 | 118.6 | 118.2
CE185 loSHR hiODB | 109 | 139 | 171.245 | 215.4162 | 140.0773 | 139.2451 | 138.8308 | 138.8945 | 139.4 | 139
CE190 as180 loPLR | 18 | 18 | 14.517 | 23.7397 | 18.1832 | 18.0237 | 18.1676 | 18.0594 | 18 | 18.2
CE195 as185 loPLR | 23 | 23 | 18.314 | 27.5498 | 22.8083 | 22.6256 | 22.7915 | 22.6987 | 22.6 | 22.6
CE200 ARI PLR=1 hiSHR | 154 | 153 | 192.674 | 181.1254 | 153.7356 | 154.56 | 154.56 | 154.4636 | 154.6 | 154.6

## Data-Delta
Sensitivities for Space Cooling Electricity Consumption
Delta Qtot (kWh,e)
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical | 0 | 0 | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | -454 | -441 | -459.621 | -454 | -450.9597 | -455.3055 | -449.9711 | -454.3131 | -453.6 | -453.2
CE120-110 IDB | -65 | -77 | -50.092 | -62 | -62.6782 | -59.6584 | -60.3021 | -63.5575 | -66.2 | -66.4
CE120-100 IDB+ODB | -519 | -518 | -509.713 | -516 | -513.638 | -514.9639 | -510.2732 | -517.8706 | -519.8 | -519.6
CE130-100 PLR | -1421 | -1421 | -1415.398 | -1413 | -1411.4319 | -1413.5415 | -1401.8208 | -1419.9663 | -1421.3 | -1421.1
CE140-130 ODB @loPLR | -42 | -40 | -40.411 | -40 | -40.6934 | -40.9605 | -41.4733 | -41.5864 | -41 | -41.2
CE140-110 PLR @loODB | -1009 | -1020 | -996.188 | -999 | -1001.1655 | -999.1966 | -993.323 | -1007.2396 | -1008.7 | -1009.1
CE150-110 hiSHR v. dry | 131 | 118 | 141.228 | 118 | 128.04 | 132.0944 | 129.6472 | 130.2551 | 129.3 | 129.1
CE160-150 IDB @hiSHR | -68 | -68 | -64.794 | -76 | -65.3743 | -62.3216 | -58.7295 | -66.05 | -67.2 | -67.6
CE165-160 IDB+ODB @hiSH | 362 | 362 | 361.817 | 363 | 359.3413 | 362.977 | 357.0433 | 357.3902 | 360.4 | 360.7
CE170-150 sens x 0.39 | -570 | -569 | -573.348 | -563 | -561.7369 | -563.1461 | -555.7842 | -565.3727 | -568.8 | -568.7
CE180-150 SHR | -125 | -125 | -125.315 | -103 | -115.1083 | -117.7844 | -111.5753 | -123.824 | -124.2 | -124.6
CE180-170 lat x 4 | 445 | 444 | 448.033 | 460 | 446.6285 | 445.3617 | 444.2089 | 441.5487 | 444.6 | 444.1
CE185-180 ODB @loSHR | 461 | 461 | 464.046 | 467 | 458.3877 | 460.255 | 458.3596 | 461.9737 | 461.1 | 461
CE190-180 PLR @loSHR | -919 | -918 | -916.89 | -920 | -917.6654 | -917.2731 | -914.9174 | -917.493 | -918.2 | -917.7
CE190-140 lat @loPLR | 96 | 95 | 95.211 | 94 | 96.4318 | 96.2334 | 96.4774 | 96.1777 | 95.6 | 95.9
CE195-190 ODB @loPLloSH | 86 | 86 | 84.7 | 86 | 85.8951 | 85.7346 | 86.4597 | 86.9875 | 85.9 | 85.8
CE195-185 PLR @loSHR | -1294 | -1293 | -1296.236 | -1301 | -1290.158 | -1291.7935 | -1286.8173 | -1292.4792 | -1293.4 | -1292.9
CE195-130 lat @loPLR | 140 | 141 | 139.5 | 140 | 141.6336 | 141.0075 | 141.4638 | 141.5788 | 140.5 | 140.5
CE200-100 ARI v dry | -54 | -66 | -52.603 | -79 | -55.4338 | -42.2735 | -31.9443 | -54.7376 | -53.4 | -53.5
Del Qcomp (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical |  |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | -430 | -419 | -441.592 | -428 | 0 | -431.8474 | -426.8936 | -430.9138 | -429.8 | -429.5
CE120-110 IDB | -49 | -59 | -15.798 | -45 | 0 | -43.4717 | -43.903 | -47.0715 | -50.1 | -50.2
CE120-100 IDB+ODB | -479 | -478 | -457.39 | -473 | 0 | -475.319 | -470.7965 | -477.9853 | -479.9 | -479.7
CE130-100 PLR | -1224 | -1224 | -1214.26 | -1218 | 0 | -1217.5188 | -1207.8769 | -1223.5648 | -1224.6 | -1224.6
CE140-130 ODB @loPLR | -38 | -37 | -38.399 | -37 | 0 | -37.8005 | -38.2753 | -38.3628 | -37.9 | -37.9
CE140-110 PLR @loODB | -832 | -842 | -811.067 | -827 | 0 | -823.472 | -819.2586 | -831.0138 | -832.7 | -833
CE150-110 hiSHR v. dry | 111 | 100 | 141.228 | 99 | 0 | 112.7146 | 110.9181 | 111.0199 | 110 | 109.8
CE160-150 IDB @hiSHR | -50 | -50 | -44.419 | -56 | 0 | -45.0374 | -42.3919 | -48.5466 | -49.8 | -50.1
CE165-160 IDB+ODB @hiSH | 333 | 332 | 328.567 | 330 | 0 | 333.2246 | 328.108 | 328.3094 | 330.8 | 331.1
CE170-150 sens x 0.39 | -469 | -469 | -468.135 | -459 | 0 | -463.6356 | -458.1666 | -465.9883 | -469.2 | -469.1
CE180-150 SHR | -91 | -91 | -92.832 | -70 | 0 | -84.887 | -80.3105 | -90.836 | -91.2 | -91.5
CE180-170 lat x 4 | 378 | 378 | 375.303 | 389 | 0 | 378.7486 | 377.8561 | 375.1523 | 378 | 377.6
CE185-180 ODB @loSHR | 431 | 431 | 428.419 | 432 | 0 | 429.7507 | 427.9509 | 431.6779 | 430.6 | 430.5
CE190-180 PLR @loSHR | -771 | -770 | -774.839 | -774 | 0 | -769.6356 | -767.9826 | -769.6508 | -770.4 | -770
CE190-140 lat @loPLR | 81 | 81 | 84.624 | 82 | 0 | 81.6639 | 81.8837 | 81.5469 | 81.1 | 81.3
CE195-190 ODB @loPLloSH | 79 | 79 | 79.444 | 79 | 0 | 78.9721 | 79.6337 | 80.1527 | 79.2 | 79.1
CE195-185 PLR @loSHR | -1123 | -1122 | -1123.814 | -1127 | 0 | -1120.4142 | -1116.2999 | -1121.176 | -1121.8 | -1121.4
CE195-130 lat @loPLR | 122 | 123 | 125.669 | 124 | 0 | 122.8356 | 123.242 | 123.3368 | 122.4 | 122.5
CE200-100 ARI v dry | -69 | -79 | -58.431 | -93 | 0 | -58.3094 | -49.8691 | -70.0317 | -68.8 | -68.9
Del Q IDfan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical |  |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | -16 | -15 | -12.268 | -19 | -16.0147 | -15.9627 | -15.7035 | -15.9226 | -16.2 | -16.1
CE120-110 IDB | -11 | -12 | -23.336 | -12 | -11.154 | -11.0148 | -11.1592 | -11.2183 | -11 | -11
CE120-100 IDB+ODB | -27 | -27 | -35.604 | -31 | -27.1687 | -26.9774 | -26.8627 | -27.1409 | -27.2 | -27.1
CE130-100 PLR | -134 | -134 | -136.869 | -133 | -133.2976 | -133.3883 | -131.9736 | -133.646 | -133.8 | -133.7
CE140-130 ODB @loPLR | -2 | -2 | -1.369 | -2 | -2.1553 | -2.1503 | -2.1761 | -2.1936 | -2.2 | -2.2
CE140-110 PLR @loODB | -120 | -121 | -125.97 | -116 | -119.4381 | -119.5759 | -118.4462 | -119.917 | -119.8 | -119.8
CE150-110 hiSHR v. dry | 13 | 12 | 0 | 14 | 12.711 | 13.1873 | 12.7446 | 13.0891 | 13.2 | 13.2
CE160-150 IDB @hiSHR | -12 | -12 | -13.865 | -15 | -11.9732 | -11.7613 | -11.1173 | -11.9106 | -11.9 | -11.9
CE165-160 IDB+ODB @hiSH | 20 | 21 | 22.626 | 24 | 20.2603 | 20.246 | 19.6897 | 19.7887 | 20.1 | 20.1
CE170-150 sens x 0.39 | -68 | -68 | -71.595 | -73 | -67.2399 | -67.7141 | -66.4261 | -67.6284 | -67.9 | -67.9
CE180-150 SHR | -23 | -22 | -22.104 | -24 | -21.8663 | -22.3857 | -21.2749 | -22.4474 | -22.5 | -22.6
CE180-170 lat x 4 | 45 | 46 | 49.491 | 49 | 45.3736 | 45.3284 | 45.1513 | 45.181 | 45.4 | 45.3
CE185-180 ODB @loSHR | 21 | 20 | 24.243 | 25 | 20.7271 | 20.7574 | 20.6923 | 20.6154 | 20.8 | 20.8
CE190-180 PLR @loSHR | -100 | -101 | -96.662 | -98 | -100.3495 | -100.4635 | -99.9852 | -100.6027 | -100.6 | -100.5
CE190-140 lat @loPLR | 10 | 10 | 7.204 | 8 | 9.9333 | 9.9142 | 9.9306 | 9.9559 | 9.9 | 9.9
CE195-190 ODB @loPLloSH | 5 | 5 | 3.577 | 4 | 4.627 | 4.6017 | 4.6449 | 4.6509 | 4.6 | 4.6
CE195-185 PLR @loSHR | -116 | -116 | -117.328 | -119 | -116.4496 | -116.6191 | -116.0326 | -116.5672 | -116.8 | -116.7
CE195-130 lat @loPLR | 13 | 13 | 9.412 | 10 | 12.405 | 12.3655 | 12.3994 | 12.4132 | 12.3 | 12.3
CE200-100 ARI v dry | 10 | 9 | 3.966 | 10 | 9.8015 | 10.9119 | 12.1975 | 10.4073 | 10.5 | 10.6
Del Q ODfan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical |  |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | -8 | -7 | -5.761 | -7 | 0 | -7.4954 | -7.374 | -7.4767 | -7.5 | -7.5
CE120-110 IDB | -5 | -6 | -10.958 | -5 | 0 | -5.172 | -5.24 | -5.2677 | -5.2 | -5.2
CE120-100 IDB+ODB | -13 | -13 | -16.719 | -12 | 0 | -12.6674 | -12.6139 | -12.7444 | -12.7 | -12.7
CE130-100 PLR | -63 | -63 | -64.269 | -62 | 0 | -62.6344 | -61.9703 | -62.7555 | -62.8 | -62.8
CE140-130 ODB @loPLR | -1 | -1 | -0.643 | -1 | 0 | -1.0097 | -1.0218 | -1.03 | -1 | -1
CE140-110 PLR @loODB | -56 | -57 | -59.151 | -56 | 0 | -56.1487 | -55.6182 | -56.3088 | -56.3 | -56.3
CE150-110 hiSHR v. dry | 6 | 5 | 0 | 5 | 0 | 6.1925 | 5.9844 | 6.1462 | 6.2 | 6.1
CE160-150 IDB @hiSHR | -5 | -5 | -6.51 | -5 | 0 | -5.5228 | -5.2203 | -5.5928 | -5.6 | -5.5
CE165-160 IDB+ODB @hiSH | 9 | 9 | 10.624 | 9 | 0 | 9.5064 | 9.2456 | 9.2921 | 9.4 | 9.4
CE170-150 sens x 0.39 | -32 | -32 | -33.618 | -31 | 0 | -31.7964 | -31.1915 | -31.756 | -31.9 | -31.8
CE180-150 SHR | -10 | -10 | -10.379 | -9 | 0 | -10.5117 | -9.99 | -10.5405 | -10.6 | -10.5
CE180-170 lat x 4 | 22 | 22 | 23.239 | 22 | 0 | 21.2847 | 21.2015 | 21.2154 | 21.3 | 21.3
CE185-180 ODB @loSHR | 9 | 9 | 11.384 | 10 | 0 | 9.7468 | 9.7164 | 9.6803 | 9.7 | 9.7
CE190-180 PLR @loSHR | -48 | -47 | -45.389 | -48 | 0 | -47.1741 | -46.9496 | -47.2395 | -47.2 | -47.2
CE190-140 lat @loPLR | 4 | 5 | 3.383 | 4 | 0 | 4.6553 | 4.6631 | 4.6749 | 4.7 | 4.7
CE195-190 ODB @loPLloSH | 3 | 2 | 1.679 | 3 | 0 | 2.1608 | 2.1811 | 2.1839 | 2.1 | 2.1
CE195-185 PLR @loSHR | -54 | -54 | -55.094 | -55 | 0 | -54.7601 | -54.4849 | -54.7359 | -54.8 | -54.8
CE195-130 lat @loPLR | 6 | 6 | 4.419 | 6 | 0 | 5.8064 | 5.8223 | 5.8288 | 5.8 | 5.8
CE200-100 ARI v dry | 5 | 4 | 1.862 | 4 | 0 | 5.124 | 5.7274 | 4.8869 | 5 | 5
Sensitivities for COP and Coil Loads
Delta COP (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical |  |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | 0.99 | 0.953 | 1.0285 | 1.0082 | 0.99667 | 1.0069 | 1.0087 | 0.99059 | 0.99 | 0.99
CE120-110 IDB | 0.21 | 0.248 | 0.155 | 0.20837 | 0.20683 | 0.19677 | 0.20416 | 0.20704 | 0.21 | 0.21
CE120-100 IDB+ODB | 1.2 | 1.201 | 1.1835 | 1.2166 | 1.2035 | 1.2037 | 1.2129 | 1.1976 | 1.2 | 1.2
CE130-100 PLR | -0.48 | -0.48 | -0.4552 | -0.45341 | -0.50017 | -0.48198 | -0.50212 | -0.49937 | -0.48 | -0.48
CE140-130 ODB @loPLR | 0.86 | 0.825 | 0.9399 | 0.901 | 0.86754 | 0.87767 | 0.88334 | 0.86071 | 0.86 | 0.86
CE140-110 PLR @loODB | -0.61 | -0.608 | -0.5438 | -0.56063 | -0.6293 | -0.61124 | -0.6275 | -0.62925 | -0.61 | -0.61
CE150-110 hiSHR v. dry | 0.24 | 0.288 | 0.2086 | 0.28537 | 0.25377 | 0.24097 | 0.24631 | 0.24783 | 0.25 | 0.25
CE160-150 IDB @hiSHR | 0.22 | 0.21 | 0.1983 | 0.25 | 0.20665 | 0.19555 | 0.18654 | 0.20563 | 0.21 | 0.21
CE165-160 IDB+ODB @hiSH | -0.92 | -0.92 | -0.9144 | -0.96474 | -0.91963 | -0.91948 | -0.91505 | -0.90343 | -0.91 | -0.91
CE170-150 sens x 0.39 | -0.24 | -0.24 | -0.2252 | -0.223 | -0.25935 | -0.25525 | -0.27013 | -0.26014 | -0.24 | -0.24
CE180-150 SHR | 0.42 | 0.41 | 0.4167 | 0.326 | 0.38877 | 0.39757 | 0.38162 | 0.41502 | 0.41 | 0.41
CE180-170 lat x 4 | 0.66 | 0.65 | 0.6419 | 0.549 | 0.64811 | 0.65282 | 0.65175 | 0.67516 | 0.65 | 0.65
CE185-180 ODB @loSHR | -1.19 | -1.19 | -1.2098 | -1.203 | -1.1911 | -1.196 | -1.1976 | -1.1965 | -1.19 | -1.19
CE190-180 PLR @loSHR | -0.63 | -0.63 | -0.5977 | -0.569 | -0.64902 | -0.63762 | -0.65027 | -0.65583 | -0.63 | -0.63
CE190-140 lat @loPLR | 0.64 | 0.676 | 0.5714 | 0.603 | 0.62282 | 0.61216 | 0.60515 | 0.63627 | 0.64 | 0.64
CE195-190 ODB @loPLloSH | -1.1 | -1.1 | -1.1267 | -1.12 | -1.0909 | -1.0938 | -1.0994 | -1.0921 | -1.1 | -1.1
CE195-185 PLR @loSHR | -0.54 | -0.54 | -0.5146 | -0.48603 | -0.54881 | -0.53547 | -0.55209 | -0.55141 | -0.54 | -0.54
CE195-130 lat @loPLR | 0.4 | 0.401 | 0.3846 | 0.384 | 0.39945 | 0.39602 | 0.3891 | 0.40487 | 0.4 | 0.4
CE200-100 ARI v dry | 1.23 | 1.221 | 1.2373 | 1.3016 | 1.2431 | 1.2084 | 1.1918 | 1.2317 | 1.23 | 1.23
Del Q coil,t (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical |  |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | -35 | -34 | -37.89 | -38.3939 | -34.5809 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1
CE120-110 IDB | -16 | -17 | -40.1 | -16.4127 | -16.1629 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8
CE120-100 IDB+ODB | -51 | -51 | -77.99 | -54.8066 | -50.7438 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9
CE130-100 PLR | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.6485 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2
CE140-130 ODB @loPLR | -21 | -21 | -20.248 | -20.5158 | -20.7191 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9
CE140-110 PLR @loODB | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.7867 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568
CE150-110 hiSHR v. dry | 752 | 751 | 739.2 | 771.9812 | 745.6537 | 752.3846 | 751.7923 | 752.2836 | 752.4 | 753
CE160-150 IDB @hiSHR | -16 | -17 | -26.402 | -19.0504 | -17.6739 | -16.9277 | -16.1469 | -16.9825 | -17.1 | -18.4
CE165-160 IDB+ODB @hiSH | 37 | 38 | 51.08 | 40.4455 | 37.6106 | 37.0003 | 36.2193 | 36.4531 | 37 | 38
CE170-150 sens x 0.39 | -2284 | -2285 | -2316.723 | -2291.0317 | -2283.8549 | -2285.3107 | -2283.394 | -2285.1847 | -2285.5 | -2285.8
CE180-150 SHR | -22 | -22 | -32.796 | 7.034 | -27.5145 | -22.3843 | -20.9286 | -22.2623 | -22.5 | -24.5
CE180-170 lat x 4 | 2262 | 2263 | 2283.927 | 2298.0657 | 2256.3404 | 2262.9264 | 2262.4654 | 2262.9224 | 2263 | 2261.3
CE185-180 ODB @loSHR | 12 | 40 | 54.91 | 48.0657 | 41.3818 | 39.9168 | 39.8433 | 39.858 | 40 | 40.1
CE190-180 PLR @loSHR | -3917 | -3918 | -3937.377 | -3956.0375 | -3906.9062 | -3917.4227 | -3916.4296 | -3917.7372 | -3917.6 | -3916.1
CE190-140 lat @loPLR | 380 | 379 | 377.077 | 383.939 | 378.0197 | 379.514 | 379.106 | 379.5607 | 379.4 | 380.4
CE195-190 ODB @loPLloSH | 24 | 24 | 22.633 | 23.1536 | 23.4 | 23.7619 | 23.6687 | 23.8465 | 23.9 | 23.5
CE195-185 PLR @loSHR | -3905 | -3934 | -3969.654 | -3980.9496 | -3924.888 | -3933.5775 | -3932.6042 | -3933.7487 | -3933.7 | -3932.7
CE195-130 lat @loPLR | 383 | 382 | 379.462 | 386.5768 | 380.7006 | 381.9655 | 381.5695 | 382.0203 | 381.9 | 382
CE200-100 ARI v dry | 1698 | 1636 | 1692.73 | 1728.0188 | 1686.8281 | 1697.8282 | 1699.6157 | 1697.4409 | 1697.4 | 1697.4
Del Q coil,s (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical |  |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | -35 | -34 | -37.89 | -38.3939 | -34.5797 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1
CE120-110 IDB | -16 | -17 | -40.1 | -16.4127 | -16.1635 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8
CE120-100 IDB+ODB | -51 | -51 | -77.99 | -54.8066 | -50.7431 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9
CE130-100 PLR | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.6444 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2
CE140-130 ODB @loPLR | -21 | -21 | -20.248 | -20.5158 | -20.719 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9
CE140-110 PLR @loODB | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.7837 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568
CE150-110 hiSHR v. dry | 13 | 12 | 0 | 30.4807 | 12.9618 | 13.1846 | 12.5854 | 13.088 | 13.2 | 13.7
CE160-150 IDB @hiSHR | -17 | -17 | -26.402 | -16.9988 | -16.9902 | -16.9277 | -16.1348 | -17.0265 | -17.1 | -18.2
CE165-160 IDB+ODB @hiSH | 37 | 37 | 51.08 | 39.5662 | 36.4558 | 37.0003 | 36.2248 | 36.4472 | 37 | 37.8
CE170-150 sens x 0.39 | -2285 | -2285 | -2316.723 | -2288.3939 | -2284.806 | -2285.3107 | -2283.3986 | -2285.3048 | -2285.5 | -2285.9
CE180-150 SHR | -2241 | -2240 | -2250.396 | -2179.3669 | -2238.6808 | -2239.9843 | -2238.5215 | -2240.5379 | -2240.1 | -2241.3
CE180-170 lat x 4 | 44 | 45 | 66.327 | 109.027 | 46.1251 | 45.3264 | 44.8771 | 44.7669 | 45.4 | 44.6
CE185-180 ODB @loSHR | 11 | 40 | 54.91 | 46.0141 | 39.2553 | 39.9168 | 39.8232 | 39.8069 | 40 | 40
CE190-180 PLR @loSHR | -1329 | -1330 | -1350.177 | -1394.49 | -1330.9807 | -1330.2227 | -1329.2766 | -1329.9815 | -1330.4 | -1329.8
CE190-140 lat @loPLR | 10 | 10 | 7.477 | 17.585 | 10.0839 | 9.914 | 9.4592 | 9.8452 | 9.8 | 10.6
CE195-190 ODB @loPLloSH | 24 | 24 | 22.633 | 22.8605 | 23.1909 | 23.7619 | 23.71 | 23.8326 | 23.9 | 23.7
CE195-185 PLR @loSHR | -1316 | -1346 | -1382.454 | -1417.6436 | -1347.0452 | -1346.3775 | -1345.3897 | -1345.9558 | -1346.5 | -1346.1
CE195-130 lat @loPLR | 13 | 13 | 9.862 | 19.9297 | 12.5558 | 12.3655 | 11.964 | 12.2909 | 12.3 | 12.4
CE200-100 ARI v dry | 476 | 415 | 471.706 | 508.7925 | 476.6119 | 476.8042 | 478.5917 | 476.3346 | 476.4 | 476.4
Del Qcoil,lat (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re | Analytical |  |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE110-100 ODB | 0 | 0 | 0 | 0 | -0.0012361 | 0 | -3.0447e-14 | 0 | 0 | 0
CE120-110 IDB | 0 | 0 | 0 | 0 | 0.00051944 | 0 | 1.1191e-15 | 0 | 0 | 0
CE120-100 IDB+ODB | 0 | 0 | 0 | 0 | -0.00071667 | 0 | -2.9328e-14 | 0 | 0 | 0
CE130-100 PLR | 0 | 0 | 0 | 0 | -0.0041511 | 0 | -1.7231e-15 | 0 | 0 | 0
CE140-130 ODB @loPLR | 0 | 0 | 0 | 0 | -0.00011694 | 0 | -3.169e-14 | 0 | 0 | 0
CE140-110 PLR @loODB | 0 | 0 | 0 | 0 | -0.0030319 | 0 | -2.9665e-15 | 0 | 0 | 0
CE150-110 hiSHR v. dry | 739 | 739 | 739.2 | 741.5006 | 732.6919 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4
CE160-150 IDB @hiSHR | 1 | 0 | 0 | -2.0516 | -0.68366 | 0 | -0.01221 | 0.043984 | 0 | -0.3
CE165-160 IDB+ODB @hiSH | 0 | 0 | 0 | 0.87925 | 1.1548 | 0 | -0.00548 | 0.005862 | 0 | 0.2
CE170-150 sens x 0.39 | 1 | 0 | 0 | -2.6377 | 0.95111 | 0 | 0.00465 | 0.12011 | 0 | 0
CE180-150 SHR | 2219 | 2218 | 2217.6 | 2186.4009 | 2211.1664 | 2217.6 | 2217.5924 | 2218.2757 | 2217.6 | 2216.7
CE180-170 lat x 4 | 2218 | 2218 | 2217.6 | 2189.0387 | 2210.2153 | 2217.6 | 2217.5877 | 2218.1556 | 2217.6 | 2216.7
CE185-180 ODB @loSHR | 1 | 0 | 0 | 2.0516 | 2.1265 | 0 | 0.02022 | 0.051109 | 0 | 0.1
CE190-180 PLR @loSHR | -2588 | -2587 | -2587.2 | -2561.5475 | -2575.9255 | -2587.2 | -2587.1524 | -2587.7557 | -2587.2 | -2586.3
CE190-140 lat @loPLR | 370 | 370 | 369.6 | 366.354 | 367.9358 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8
CE195-190 ODB @loPLloSH | 0 | 0 | 0 | 0.29308 | 0.20914 | 0 | -0.041346 | 0.013833 | 0 | -0.2
CE195-185 PLR @loSHR | -2589 | -2587 | -2587.2 | -2563.306 | -2577.8429 | -2587.2 | -2587.214 | -2587.793 | -2587.2 | -2586.6
CE195-130 lat @loPLR | 370 | 370 | 369.6 | 366.6471 | 368.1448 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6
CE200-100 ARI v dry | 1222 | 1221 | 1221 | 1219.2263 | 1210.2163 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221
results5-3.xls q:db491..dq580; 10/15/02

## Data-TempHum
Indoor Drybulb Temperature: Mean and (Max-Min)/Mean
Mean IDB (°C)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6346 | 22.2 | 22.2 | 22.216
CE110 as100 lo ODB | 22.2 | 22.2 | 22.3 | 22.2778 | 22.1999 | 22.2 | 22.5242 | 22.2 | 22.2 | 22.214
CE120 as100 hiIDB | 26.7 | 26.7 | 26.8 | 26.7222 | 26.7 | 26.7 | 27.0785 | 26.7 | 26.7 | 26.712
CE130 as100 lo PLR | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.6377 | 22.2 | 22.2 | 22.187
CE140 as130 lo ODB | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.5097 | 22.2 | 22.2 | 22.185
CE150 as110 hiSHR | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6771 | 22.2 | 22.2 | 22.216
CE160 as150 hiIDB | 26.7 | 26.7 | 26.8 | 26.7222 | 26.6999 | 26.7 | 26.9948 | 26.7 | 26.7 | 26.714
CE165 as150 mIDB mODB | 23.3 | 23.3 | 23.4 | 23.4444 | 23.2999 | 23.3 | 23.7805 | 23.3 | 23.3 | 23.317
CE170 as150 mSHR mPLR | 22.2 | 22.2 | 22.2 | 22.2222 | 22.1999 | 22.2 | 22.1169 | 22.2 | 22.2 | 22.199
CE180 as150 loSHR | 22.2 | 22.2 | 22.3 | 22.2778 | 22.2 | 22.2 | 22.3344 | 22.2 | 22.2 | 22.205
CE185 loSHR hiODB | 22.2 | 22.2 | 22.3 | 22.3333 | 22.2 | 22.2 | 22.3682 | 22.2 | 22.2 | 22.206
CE190 as180 loPLR | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.9469 | 22.2 | 22.2 | 22.194
CE195 as185 loPLR | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 22.0113 | 22.2 | 22.2 | 22.195
CE200 ARI PLR=1 hiSHR | 26.7 | 26.7 | 26.8 | 26.7778 | 26.6999 | 26.7339 | 26.7339 | 26.7 | 26.7 | 26.713
(Max - Min)/Mean IDB (°C)
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 1.9369e-05 | 0 | 0.049482 | 0 |  | 0.0017105
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 2.4324e-05 | 0 | 0.047948 | 0 |  | 0.0018907
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 1.4232e-05 | 0 | 0.077183 | 0 |  | 0.0017221
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 2.2523e-06 | 0 | 0.056383 | 0 |  | 0.0013521
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 1.3514e-06 | 0 | 0.069271 | 0 |  | 0.0015326
CE150 as110 hiSHR | 0 | 0 | 0 | 0 | 2.7027e-05 | 0 | 0.053799 | 0 |  | 0.0017105
CE160 as150 hiIDB | 0 | 0 | 0 | 0 | 4.2697e-05 | 0 | 0.045194 | 0 |  | 0.0015722
CE165 as150 mIDB mODB | 0 | 0 | 0 | 0 | 4.3777e-05 | 0 | 0.051303 | 0 |  | 0.0015439
CE170 as150 mSHR mPLR | 0 | 0 | 0 | 0 | 2.3423e-05 | 0 | 0.049736 | 0 |  | 0.0013064
CE180 as150 loSHR | 0 | 0 | 0 | 0 | 2.027e-05 | 0 | 0.034924 | 0 |  | 0.00081063
CE185 loSHR hiODB | 0 | 0 | 0 | 0 | 1.4865e-05 | 0 | 0.021459 | 0 |  | 0.00072053
CE190 as180 loPLR | 0 | 0 | 0 | 0 | 4.0541e-06 | 0 | 0.02825 | 0 |  | 0.00072092
CE195 as185 loPLR | 0 | 0 | 0 | 0 | 4.0541e-06 | 0 | 0.022716 | 0 |  | 0.00063077
CE200 ARI PLR=1 hiSHR | 0 | 0 | 0 | 0 | 4.2322e-05 | 0 | 0 | 0 |  | 0
Humidity Ratio: Mean and (Max-Min)/Mean
Mean Humidity Ratio
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 0.0075 | 0.00691 | 0.0076 | 0.0074 | 0.0074745 | 0.0075036 | 0.0075088 | 0.0074274 | 0.00734 | 0.007339
CE110 as100 lo ODB | 0.0066 | 0.00692 | 0.0070296 | 0.0064 | 0.0065835 | 0.0065938 | 0.0066309 | 0.0065187 | 0.0064 | 0.006411
CE120 as100 hiIDB | 0.008 | 0.007 | 0.0078 | 0.0078 | 0.0080402 | 0.0079506 | 0.0079517 | 0.0078783 | 0.00786 | 0.007873
CE130 as100 lo PLR | 0.0075 | 0.00691 | 0.0076 | 0.0073 | 0.0074769 | 0.0075036 | 0.0075194 | 0.0074274 | 0.00734 | 0.007339
CE140 as130 lo ODB | 0.0065 | 0.00692 | 0.0070601 | 0.0064 | 0.0065863 | 0.0065938 | 0.0065941 | 0.0065187 | 0.0064 | 0.006402
CE150 as110 hiSHR | 0.0083 | 0.00853 | 0.0082 | 0.0083 | 0.0084223 | 0.0083236 | 0.0085152 | 0.0082272 | 0.0082 | 0.00821
CE160 as150 hiIDB | 0.0102 | 0.0101 | 0.009701 | 0.0099 | 0.010278 | 0.010069 | 0.010236 | 0.009969 | 0.00994 | 0.009946
CE165 as150 mIDB mODB | 0.0093 | 0.00985 | 0.0090039 | 0.0092 | 0.0093948 | 0.0093021 | 0.0095112 | 0.0092694 | 0.0092 | 0.009208
CE170 as150 mSHR mPLR | 0.0106 | 0.0107 | 0.010494 | 0.0105 | 0.010571 | 0.010471 | 0.010525 | 0.010367 | 0.01045 | 0.010451
CE180 as150 loSHR | 0.0164 | 0.0164 | 0.016614 | 0.0164 | 0.016193 | 0.01631 | 0.016404 | 0.01619 | 0.01623 | 0.01623
CE185 loSHR hiODB | 0.0162 | 0.0171 | 0.016441 | 0.0162 | 0.016067 | 0.016151 | 0.016279 | 0.016056 | 0.01605 | 0.016059
CE190 as180 loPLR | 0.016 | 0.0161 | 0.016254 | 0.0159 | 0.015855 | 0.015921 | 0.015707 | 0.015796 | 0.0159 | 0.015891
CE195 as185 loPLR | 0.0156 | 0.0164 | 0.015764 | 0.0155 | 0.015446 | 0.01547 | 0.015326 | 0.015368 | 0.01544 | 0.015439
CE200 ARI PLR=1 hiSHR | 0.0114 | 0.0115 | 0.010933 | 0.0111 | 0.011461 | 0.011281 | 0.011281 | 0.011129 | 0.01109 | 0.011099
(Max - Min)/Mean Humidity Ratio
| CA-SIS | CLM2000 | DOE21E | DOE21E | E+ | TRN-id | TRN-re |  | Analytical |  | EnergyPlus 8.6.0
| CA-SIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | EnergyPlus/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | E+/NREL
CE100 dry lo IDB hi ODB | 0 | 0.021708 | 0 | 0 | 0.00051398 | 0 | 0 | 0 |  | 0
CE110 as100 lo ODB | 0 | 0.021676 | 0.014226 | 0 | 0.00049972 | 0 | 0 | 0 |  | 0
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 0.00052403 | 0 | 0 | 0 |  | 0
CE130 as100 lo PLR | 0 | 0.01013 | 0 | 0 | 0.00061108 | 0 | 0 | 0 |  | 0
CE140 as130 lo ODB | 0 | 0.011561 | 0.014164 | 0 | 0.00064275 | 0 | 0 | 0 |  | 0
CE150 as110 hiSHR | 0.012048 | 0 | 0 | 0 | 0.013105 | 0 | 0.013153 | 0 |  | 0.00036541
CE160 as150 hiIDB | 0.019608 | 0 | 0.010308 | 0.010101 | 0.013391 | 0 | 0.010747 | 0 |  | 0.00040217
CE165 as150 mIDB mODB | 0.010753 | 0.0010152 | 0.011106 | 0 | 0.013116 | 0 | 0.012512 | 0 |  | 0.0003258
CE170 as150 mSHR mPLR | 0 | 0 | 0.0095289 | 0 | 0.011456 | 0 | 0.023752 | 0 |  | 0.00057411
CE180 as150 loSHR | 0.018293 | 0 | 0.012038 | 0.012195 | 0.010319 | 0 | 0.040234 | 0 |  | 0.00092421
CE185 loSHR hiODB | 0.012346 | 0.005848 | 0.018247 | 0.012346 | 0.010816 | 0 | 0.024571 | 0 |  | 0.00080951
CE190 as180 loPLR | 0 | 0 | 0.018457 | 0.018868 | 0.0145 | 0 | 0.031196 | 0 |  | 0.00075514
CE195 as185 loPLR | 0 | 0.0060976 | 0.01903 | 0.019355 | 0.013755 | 0 | 0.024142 | 0 |  | 0.00064771
CE200 ARI PLR=1 hiSHR | 0.017544 | 0 | 0.0091467 | 0.009009 | 0.012859 | 0 | 0 | 0 |  | 0

## DOE21E-NREL
d:\e\iea22\hvabtest\results\doe2\21EJNA2A.WK3, February 14, 2000 | [5 empty] | Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST | [9 empty] | DOE2.1E Build 133
DOE-2.1E by NREL. | [5 empty] | Program Version Release Date:
[6 empty] | Program Name for Tables and Charts: |  |  |  | DOE2.1E
INSTRUCTIONS | [5 empty] | Results Submission Date: |  |  |  | 2000-02-14
Modeler Organization for Titles (long):
1. Use specified units | [9 empty] | National Renewable Energy Laboratory/J. Neymark & Associates
[6 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | NREL
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity |  | Qfan,heat | (del Qfan) | (del Qfan)
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio | Qfan,heat | - Qfan | /Qfan | /Qcoil
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) | (kWh) | (kWh) | (frac) | (frac)
CE100 | 1519 | 1311 | 141 | 67 | 3793.9625 | 3793.9625 | 0 | 3655.3341 | 3655.3341 | 0 | 2.4064 | 22.3333 | 0.0074 | 2.407 | 22.3333 | 0.0074 | 2.404 | 22.3333 | 0.0074 | 138.6284 | -2.3716 | -0.017108 | -0.00062511
CE110 | 1065 | 883 | 122 | 60 | 3755.5686 | 3755.5686 | 0 | 3636.5768 | 3636.5768 | 0 | 3.4146 | 22.2778 | 0.0064 | 3.417 | 22.2778 | 0.0064 | 3.413 | 22.2778 | 0.0064 | 118.9918 | -3.0082 | -0.025281 | -0.000801
CE120 | 1003 | 838 | 110 | 55 | 3739.1559 | 3739.1559 | 0 | 3631.5944 | 3631.5944 | 0 | 3.623 | 26.7222 | 0.0078 | 3.625 | 26.7222 | 0.0078 | 3.621 | 26.7222 | 0.0078 | 107.5615 | -2.4385 | -0.02267 | -0.00065214
CE130 | 106 | 93 | 8 | 5 | 215.1231 | 215.1231 | 0 | 207.5029 | 207.5029 | 0 | 1.953 | 22.1111 | 0.0073 | 1.961 | 22.1111 | 0.0073 | 1.944 | 22.1111 | 0.0073 | 7.6202 | -0.37984 | -0.049846 | -0.0017657
CE140 | 66 | 56 | 6 | 4 | 194.6073 | 194.6073 | 0 | 188.4525 | 188.4525 | 0 | 2.854 | 22.1111 | 0.0064 | 2.882 | 22.1111 | 0.0064 | 2.828 | 22.1111 | 0.0064 | 6.1547 | 0.15475 | 0.025143 | 0.00079518
CE150 | 1183 | 982 | 136 | 65 | 4527.5498 | 3786.0492 | 741.5006 | 4376.0258 | 3636.5768 | 739.449 | 3.7 | 22.3333 | 0.0083 | 3.709 | 22.3333 | 0.0083 | 3.691 | 22.3333 | 0.0083 | 149.4725 | 13.4725 | 0.090133 | 0.0029757
CE160 | 1107 | 926 | 121 | 60 | 4508.4994 | 3769.0504 | 739.449 | 4371.0434 | 3631.5944 | 739.449 | 3.95 | 26.7222 | 0.0099 | 3.957 | 26.7222 | 0.0099 | 3.944 | 26.7222 | 0.0098 | 137.456 | 16.456 | 0.11972 | 0.00365
CE165 | 1470 | 1256 | 145 | 69 | 4548.9449 | 3808.6166 | 740.3283 | 4387.456 | 3648.007 | 739.449 | 2.9853 | 23.4444 | 0.0092 | 2.989 | 23.4444 | 0.0092 | 2.981 | 23.4444 | 0.0092 | 160.6096 | 15.6096 | 0.09719 | 0.0034315
CE170 | 620 | 523 | 63 | 34 | 2236.5182 | 1497.6553 | 738.8628 | 2157.9719 | 1418.5229 | 739.449 | 3.477 | 22.2222 | 0.0105 | 3.485 | 22.2222 | 0.0105 | 3.471 | 22.2222 | 0.0105 | 79.1325 | 16.1325 | 0.20387 | 0.0072132
CE180 | 1080 | 912 | 112 | 56 | 4534.5838 | 1606.6823 | 2927.9015 | 4376.0258 | 1418.5229 | 2957.5029 | 4.026 | 22.2778 | 0.0164 | 4.053 | 22.2778 | 0.0165 | 4.014 | 22.2778 | 0.0163 | 188.1594 | 76.1594 | 0.40476 | 0.016795
CE185 | 1547 | 1344 | 137 | 66 | 4582.6495 | 1652.6964 | 2929.9531 | 4394.7831 | 1437.2802 | 2957.5029 | 2.823 | 22.3333 | 0.0162 | 2.844 | 22.3333 | 0.0163 | 2.815 | 22.3333 | 0.0161 | 215.4162 | 78.4162 | 0.36402 | 0.017112
CE190 | 160 | 138 | 14 | 8 | 578.5463 | 212.1923 | 366.354 | 558.0305 | 188.4525 | 369.578 | 3.457 | 22.1111 | 0.0159 | 3.489 | 22.1111 | 0.0161 | 3.424 | 22.1111 | 0.0158 | 23.7397 | 9.7397 | 0.41027 | 0.016835
CE195 | 246 | 217 | 18 | 11 | 601.6999 | 235.0528 | 366.6471 | 577.0809 | 207.5029 | 369.578 | 2.337 | 22.1111 | 0.0155 | 2.36 | 22.1111 | 0.0156 | 2.321 | 22.1111 | 0.0153 | 27.5498 | 9.5498 | 0.34664 | 0.015871
CE200 | 1440 | 1218 | 151 | 71 | 5521.9812 | 4302.755 | 1219.2263 | 5342.9074 | 4121.6295 | 1221.2778 | 3.708 | 26.7778 | 0.0111 | 3.717 | 26.7778 | 0.0111 | 3.698 | 26.7778 | 0.011 | 181.1254 | 30.1254 | 0.16632 | 0.0054555
COP=(net refr effect)/(total elec)=((env sens)+(coil lat)); sens coil = (tot coil)-(lat coil); compr elec = (compr+odfan elec)-(odfan elec)
Envelope sensible includes adjustment for simulated zone temp (delta 0-0.1 C), from "QNOW" [sensible zone extraction].
Note: (fan elec) .NE. (total coil)-(sens coil), worsens with increasing humidity, check with jjh.
raw data here |  |  |  |  | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
INSTRUCTIONS |  | Compressor | Supply | Condenser |  | Fan heat | [6 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | + od fan | Fan | (od) Fan | Total | (tot-sns-lat) | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kBtu) | (kWh) | (kBtu) | (kBtu) | (kBtu) | (kBtu) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 |  | 1378 | 141 | 67 | 12945 | 138.6284 | 0 |  | 12472 | 0 |  | 72.2 | 0.0074 |  | 72.2 | 0.0074 |  | 72.2 | 0.0074
CE110 |  | 943 | 122 | 60 | 12814 | 118.9918 | 0 |  | 12408 | 0 |  | 72.1 | 0.0064 |  | 72.1 | 0.0064 |  | 72.1 | 0.0064
CE120 |  | 893 | 110 | 55 | 12758 | 107.5615 | 0 |  | 12391 | 0 |  | 80.1 | 0.0078 |  | 80.1 | 0.0078 |  | 80.1 | 0.0078
CE130 |  | 98 | 8 | 5 | 734 | 7.6202 | 0 |  | 708 | 0 |  | 71.8 | 0.0073 |  | 71.8 | 0.0073 |  | 71.8 | 0.0073
CE140 |  | 60 | 6 | 4 | 664 | 6.1547 | 0 |  | 643 | 0 |  | 71.8 | 0.0064 |  | 71.8 | 0.0064 |  | 71.8 | 0.0064
CE150 |  | 1047 | 136 | 65 | 15448 | 149.4725 | 2530 |  | 12408 | 2523 |  | 72.2 | 0.0083 |  | 72.2 | 0.0083 |  | 72.2 | 0.0083
CE160 |  | 986 | 121 | 60 | 15383 | 137.456 | 2523 |  | 12391 | 2523 |  | 80.1 | 0.0099 |  | 80.1 | 0.0099 |  | 80.1 | 0.0098
CE165 |  | 1325 | 145 | 69 | 15521 | 160.6096 | 2526 |  | 12447 | 2523 |  | 74.2 | 0.0092 |  | 74.2 | 0.0092 |  | 74.2 | 0.0092
CE170 |  | 557 | 63 | 34 | 7631 | 79.1325 | 2521 |  | 4840 | 2523 |  | 72 | 0.0105 |  | 72 | 0.0105 |  | 72 | 0.0105
CE180 |  | 968 | 112 | 56 | 15472 | 188.1594 | 9990 |  | 4840 | 10091 |  | 72.1 | 0.0164 |  | 72.1 | 0.0165 |  | 72.1 | 0.0163
CE185 |  | 1410 | 137 | 66 | 15636 | 215.4162 | 9997 |  | 4904 | 10091 |  | 72.2 | 0.0162 |  | 72.2 | 0.0163 |  | 72.2 | 0.0161
CE190 |  | 146 | 14 | 8 | 1974 | 23.7397 | 1250 |  | 643 | 1261 |  | 71.8 | 0.0159 |  | 71.8 | 0.0161 |  | 71.8 | 0.0158
CE195 |  | 228 | 18 | 11 | 2053 | 27.5498 | 1251 |  | 708 | 1261 |  | 71.8 | 0.0155 |  | 71.8 | 0.0156 |  | 71.8 | 0.0153
CE200 |  | 1289 | 151 | 71 | 18841 | 181.1254 | 4160 |  | 14063 | 4167 |  | 80.2 | 0.0111 |  | 80.2 | 0.0111 |  | 80.2 | 0.011
Table "tkfanheat". Fan Heat Discrepancy
d:\e\iea22\hvabtest\results\doe2\21ejna2a.wk3 a:63; 31 jan 00
F e b r u a r y T o t a l s
| Supply | Evaporator Coil Load |  |  | Envelope Load |  |  | Qfan,heat | (del Qfan) | (del Qfan)
Cases | Fan | Total | Sensible | Latent | Sensible | Latent | Qfan,heat | - Qfan | /Qfan | /Qcoil
CE160 | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (frac) | (frac)
CE100 | 141 | 3793.9625 | 3793.9625 | 0 | 3655.3341 | 0 | 138.6284 | -2.3716 | -0.017108 | -0.00062511
CE110 | 122 | 3755.5686 | 3755.5686 | 0 | 3636.5768 | 0 | 118.9918 | -3.0082 | -0.025281 | -0.000801
CE120 | 110 | 3739.1559 | 3739.1559 | 0 | 3631.5944 | 0 | 107.5615 | -2.4385 | -0.02267 | -0.00065214
CE130 | 8 | 215.1231 | 215.1231 | 0 | 207.5029 | 0 | 7.6202 | -0.37984 | -0.049846 | -0.0017657
CE140 | 6 | 194.6073 | 194.6073 | 0 | 188.4525 | 0 | 6.1547 | 0.15475 | 0.025143 | 0.00079518
CE150 | 136 | 4527.5498 | 3786.0492 | 741.5006 | 3636.5768 | 739.449 | 149.4725 | 13.4725 | 0.090133 | 0.0029757
CE160 | 121 | 4508.4994 | 3769.0504 | 739.449 | 3631.5944 | 739.449 | 137.456 | 16.456 | 0.11972 | 0.00365
CE165 | 145 | 4548.9449 | 3808.6166 | 740.3283 | 3648.007 | 739.449 | 160.6096 | 15.6096 | 0.09719 | 0.0034315
CE170 | 63 | 2236.5182 | 1497.6553 | 738.8628 | 1418.5229 | 739.449 | 79.1325 | 16.1325 | 0.20387 | 0.0072132
CE180 | 112 | 4534.5838 | 1606.6823 | 2927.9015 | 1418.5229 | 2957.5029 | 188.1594 | 76.1594 | 0.40476 | 0.016795
CE185 | 137 | 4582.6495 | 1652.6964 | 2929.9531 | 1437.2802 | 2957.5029 | 215.4162 | 78.4162 | 0.36402 | 0.017112
CE190 | 14 | 578.5463 | 212.1923 | 366.354 | 188.4525 | 369.578 | 23.7397 | 9.7397 | 0.41027 | 0.016835
CE195 | 18 | 601.6999 | 235.0528 | 366.6471 | 207.5029 | 369.578 | 27.5498 | 9.5498 | 0.34664 | 0.015871
CE200 | 151 | 5521.9812 | 4302.755 | 1219.2263 | 4121.6295 | 1221.2778 | 181.1254 | 30.1254 | 0.16632 | 0.0054555
CE100R2EP | 141 | 3794.2556 | 3794.2556 | 0 | 3655.3341 | 0 | 138.9215 | -2.0785 | -0.014962 | -0.00054781
CE180R2EP | 112 | 4534.8769 | 1606.9754 | 2927.9015 | 1418.5229 | 2957.5029 | 188.4525 | 76.4525 | 0.40569 | 0.016859

## DOE21E-CIEMAT
HVBTOUT1.WK3, August 26, 1997 |  |  |  |  | Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST | [8 empty] | DOE2.1E Build 88
CIEMAT: cie0600b.wk3 b:a1..b:v38; 01 jun 00 |  |  |  |  | Program Version Release Date:
[5 empty] | Program Name for Tables and Charts: |  |  |  | DOE2.1E
INSTRUCTIONS |  |  |  |  | Results Submission Date: |  |  |  | 2000-06-01
Modeler Organization for Titles (long):
1. Use specified units | [8 empty] | Centro de Investigaciones Energeticas, Medioambientales y Tecnologicas
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | CIEMAT
2. Data entry is restricted to columns B through Q and rows 13 through 27. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means and maxima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP are defined in Appendix C.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) | fan heat | error %
CE100 | 1520.817 | 1307.458 | 145.185 | 68.174 | 3841.47 | 3841.47 | 0 | 3654.42 | 3654.42 | 0 | 2.4304 | 22.3 | 0.0076 | 2.4324 | 22.3 | 0.0076 | 2.4287 | 22.3 | 0.0076 | 187.05 | 0.011018
CE110 | 1061.196 | 865.866 | 132.917 | 62.413 | 3803.58 | 3803.58 | 0 | 3635.601 | 3635.601 | 0 | 3.4589 | 22.3 | 0.0070296 | 3.4626 | 22.3 | 0.0071 | 3.4566 | 22.3 | 0.007 | 167.979 | 0.0093039
CE120 | 1011.104 | 850.068 | 109.581 | 51.455 | 3763.48 | 3763.48 | 0 | 3630.472 | 3630.472 | 0 | 3.6139 | 26.8 | 0.0078 | 3.6153 | 26.8 | 0.0078 | 3.6124 | 26.8 | 0.0078 | 133.008 | 0.0062638
CE130 | 105.419 | 93.198 | 8.316 | 3.905 | 215.778 | 215.778 | 0 | 207.344 | 207.344 | 0 | 1.9752 | 22.1 | 0.0076 | 1.9809 | 22.1 | 0.0076 | 1.956 | 22.1 | 0.0076 | 8.434 | 0.00054716
CE140 | 65.008 | 54.799 | 6.947 | 3.262 | 195.53 | 195.53 | 0 | 188.503 | 188.503 | 0 | 2.9151 | 22.1 | 0.0070601 | 2.9278 | 22.1 | 0.0071 | 2.8958 | 22.1 | 0.007 | 7.027 | 0.00040931
CE150 | 1202.424 | 1007.094 | 132.917 | 62.413 | 4542.78 | 3803.58 | 739.2 | 4374.801 | 3635.601 | 739.2 | 3.6675 | 22.3 | 0.0082 | 3.6706 | 22.3 | 0.0082 | 3.6652 | 22.3 | 0.0082 | 167.979 | 0.0093039
CE160 | 1137.63 | 962.675 | 119.052 | 55.903 | 4516.378 | 3777.178 | 739.2 | 4369.652 | 3630.452 | 739.2 | 3.8658 | 26.8 | 0.009701 | 3.8682 | 26.8 | 0.0098 | 3.8641 | 26.8 | 0.0097 | 146.726 | 0.0073807
CE165 | 1499.447 | 1291.242 | 141.678 | 66.527 | 4567.458 | 3828.258 | 739.2 | 4386.071 | 3646.871 | 739.2 | 2.9514 | 23.4 | 0.0090039 | 2.9533 | 23.4 | 0.0091 | 2.9498 | 23.4 | 0.009 | 181.387 | 0.010481
CE170 | 629.076 | 538.959 | 61.322 | 28.795 | 2226.057 | 1486.857 | 739.2 | 2157.351 | 1418.151 | 739.2 | 3.4423 | 22.2 | 0.010494 | 3.446 | 22.2 | 0.0105 | 3.4386 | 22.2 | 0.0104 | 68.706 | 0.004991
CE180 | 1077.109 | 914.262 | 110.813 | 52.034 | 4509.984 | 1553.184 | 2956.8 | 4374.852 | 1418.052 | 2956.8 | 4.0842 | 22.3 | 0.016614 | 4.0893 | 22.3 | 0.0167 | 4.0798 | 22.3 | 0.0165 | 135.132 | 0.015907
CE185 | 1541.155 | 1342.681 | 135.056 | 63.418 | 4564.894 | 1608.094 | 2956.8 | 4393.649 | 1436.849 | 2956.8 | 2.8744 | 22.3 | 0.016441 | 2.8778 | 22.3 | 0.0166 | 2.871 | 22.3 | 0.0163 | 171.245 | 0.023022
CE190 | 160.219 | 139.423 | 14.151 | 6.645 | 572.607 | 203.007 | 369.6 | 558.09 | 188.49 | 369.6 | 3.4865 | 22.1 | 0.016254 | 3.5 | 22.1 | 0.0164 | 3.475 | 22.1 | 0.0161 | 14.517 | 0.0018061
CE195 | 244.919 | 218.867 | 17.728 | 8.324 | 595.24 | 225.64 | 369.6 | 576.926 | 207.326 | 369.6 | 2.3598 | 22.1 | 0.015764 | 2.3681 | 22.1 | 0.0159 | 2.3497 | 22.1 | 0.0156 | 18.314 | 0.0026038
CE200 | 1468.214 | 1249.027 | 149.151 | 70.036 | 5534.2 | 4313.176 | 1221 | 5341.526 | 4120.502 | 1221.024 | 3.6677 | 26.8 | 0.010933 | 3.6716 | 26.8 | 0.011 | 3.6716 | 26.8 | 0.0109 | 192.674 | 0.010194

## CLM2000
Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST | [8 empty] | CLIM2000 2.1.6
EDF CLIM2000-12/00 with automated extrap |  |  |  |  | Program Version Release Date:
see EDF modeler report. |  |  |  |  | Program Name for Tables and Charts: |  |  |  | CLM2000
INSTRUCTIONS |  |  |  |  | Results Submission Date: |  |  |  | 2000-12-01
Modeler Organization for Titles (long):
1. Use specified units | [8 empty] | Electricité de France, France
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | EDF
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
BESTEST1
| February totals | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load |  | February mean
|  | Cooling energy consumption | Supply | Condenser | Evaporator coil load |  |  | Enveloppe load |  |  |  |  | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1530 | 1318 | 144 | 68 | 3800 | 3800 | 0 | 3656 | 3656 | 0 | 2.389 | 22.2 | 0.00691 | 2.392 | 22.2 | 0.00699 | 2.39 | 22.2 | 0.00684
CE110 | 1089 | 899 | 129 | 61 | 3766 | 3766 | 0 | 3637 | 3637 | 0 | 3.342 | 22.2 | 0.00692 | 3.357 | 22.2 | 0.00699 | 3.322 | 22.2 | 0.00684
CE120 | 1012 | 840 | 117 | 55 | 3749 | 3749 | 0 | 3632 | 3632 | 0 | 3.59 | 26.7 | 0.007 | 3.596 | 26.7 | 0.007 | 3.583 | 26.7 | 0.007
CE130 | 109 | 94 | 10 | 5 | 219 | 219 | 0 | 209 | 209 | 0 | 1.909 | 22.2 | 0.00691 | 1.923 | 22.2 | 0.00691 | 1.85 | 22.2 | 0.00684
CE140 | 69 | 57 | 8 | 4 | 198 | 198 | 0 | 190 | 190 | 0 | 2.734 | 22.2 | 0.00692 | 2.833 | 22.2 | 0.00692 | 2.68 | 22.2 | 0.00684
CE150 | 1207 | 999 | 141 | 66 | 4517 | 3778 | 739 | 4376 | 3637 | 739 | 3.63 | 22.2 | 0.00853 | 3.63 | 22.2 | 0.00853 | 3.62 | 22.2 | 0.00853
CE160 | 1139 | 949 | 129 | 61 | 4500 | 3761 | 739 | 4371 | 3632 | 739 | 3.84 | 26.7 | 0.0101 | 3.85 | 26.7 | 0.0101 | 3.83 | 26.7 | 0.0101
CE165 | 1501 | 1281 | 150 | 70 | 4538 | 3798 | 739 | 4388 | 3649 | 739 | 2.92 | 23.3 | 0.00985 | 2.93 | 22.2 | 0.00985 | 2.92 | 22.2 | 0.00984
CE170 | 638 | 530 | 73 | 34 | 2232 | 1493 | 739 | 2159 | 1420 | 739 | 3.39 | 22.2 | 0.0107 | 3.4 | 22.2 | 0.0107 | 3.38 | 22.2 | 0.0107
CE180 | 1082 | 908 | 119 | 56 | 4495 | 1538 | 2957 | 4376 | 1420 | 2957 | 4.04 | 22.2 | 0.0164 | 4.05 | 22.2 | 0.0164 | 4.04 | 22.2 | 0.0164
CE185 | 1543 | 1339 | 139 | 65 | 4535 | 1578 | 2957 | 4396 | 1439 | 2957 | 2.85 | 22.2 | 0.0171 | 2.85 | 22.2 | 0.0171 | 2.84 | 22.2 | 0.017
CE190 | 164 | 138 | 18 | 9 | 577 | 208 | 370 | 559 | 190 | 370 | 3.41 | 22.2 | 0.0161 | 3.45 | 22.2 | 0.0161 | 3.37 | 22.2 | 0.0161
CE195 | 250 | 217 | 23 | 11 | 601 | 232 | 370 | 579 | 209 | 370 | 2.31 | 22.2 | 0.0164 | 2.33 | 22.2 | 0.0165 | 2.29 | 22.2 | 0.0164
CE200 | 1464 | 1239 | 153 | 72 | 5436 | 4215 | 1221 | 5283 | 4062 | 1221 | 3.61 | 26.7 | 0.0115 | 3.61 | 26.7 | 0.0115 | 3.61 | 26.7 | 0.0115

## TRN-id
HVBTOUT2.WK3, May 1998 | [5 empty] | Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST | [9 empty] | TRNSYS 14.2-TUD with ideal controller model
Dresden TRNSYS 14.2: Note, combine DRESDEN.WK3 a1..q38 at e:a1 | [5 empty] | Program Version Release Date:
Ideal" results no min/on off requirement | [5 empty] | Program Name for Tables and Charts: |  |  |  | TRN-id
INSTRUCTIONS | [5 empty] | Results Submission Date:
Modeler Organization for Titles (long):
1. Use specified units | [9 empty] | Technische Universität Dresden, Germany
[6 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TUD
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  |  |  | February Totals | [6 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
Cases | Cooling Energie Consumption | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  | Envelope Load | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg]
CE100 | 1522.2661 | 1311.1661 | 143.6481 | 67.452 | 3799.7366 | 3799.7366 | 0 | 3656.0832 | 3656.0832 | 0 | 2.4017 | 22.2 | 0.0075036 | 2.4017 | 22.2 | 0.0075036 | 2.4017 | 22.2 | 0.0075036
CE110 | 1066.9607 | 879.3187 | 127.6854 | 59.9566 | 3764.6112 | 3764.6112 | 0 | 3636.9245 | 3636.9245 | 0 | 3.4087 | 22.2 | 0.0065938 | 3.4087 | 22.2 | 0.0065938 | 3.4087 | 22.2 | 0.0065938
CE120 | 1007.3023 | 835.847 | 116.6706 | 54.7846 | 3748.4294 | 3748.4294 | 0 | 3631.7568 | 3631.7568 | 0 | 3.6054 | 26.7 | 0.0079506 | 3.6054 | 26.7 | 0.0079506 | 3.6054 | 26.7 | 0.0079506
CE130 | 108.7246 | 93.6472 | 10.2598 | 4.8176 | 218.9853 | 218.9853 | 0 | 208.7252 | 208.7252 | 0 | 1.9198 | 22.2 | 0.0075036 | 1.9198 | 22.2 | 0.0075036 | 1.9198 | 22.2 | 0.0075036
CE140 | 67.7641 | 55.8468 | 8.1094 | 3.8079 | 197.6748 | 197.6748 | 0 | 189.5652 | 189.5652 | 0 | 2.7974 | 22.2 | 0.0065938 | 2.7974 | 22.2 | 0.0065938 | 2.7974 | 22.2 | 0.0065938
CE150 | 1199.055 | 992.0333 | 140.8727 | 66.1491 | 4516.9958 | 3777.7958 | 739.2 | 4376.1245 | 3636.9245 | 739.2 | 3.6496 | 22.2 | 0.0083236 | 3.6496 | 22.2 | 0.0083236 | 3.6496 | 22.2 | 0.0083236
CE160 | 1136.7334 | 946.9958 | 129.1114 | 60.6262 | 4500.0682 | 3760.8682 | 739.2 | 4370.9568 | 3631.7568 | 739.2 | 3.8452 | 26.7 | 0.010069 | 3.8452 | 26.7 | 0.010069 | 3.8452 | 26.7 | 0.010069
CE165 | 1499.7105 | 1280.2205 | 149.3574 | 70.1326 | 4537.0685 | 3797.8685 | 739.2 | 4387.7098 | 3648.5098 | 739.2 | 2.9257 | 23.3 | 0.0093021 | 2.9257 | 23.3 | 0.0093021 | 2.9257 | 23.3 | 0.0093021
CE170 | 635.909 | 528.3976 | 73.1586 | 34.3527 | 2231.6851 | 1492.4851 | 739.2 | 2158.5245 | 1419.3245 | 739.2 | 3.3944 | 22.2 | 0.010471 | 3.3944 | 22.2 | 0.010471 | 3.3944 | 22.2 | 0.010471
CE180 | 1081.2706 | 907.1462 | 118.487 | 55.6374 | 4494.6115 | 1537.8115 | 2956.8 | 4376.1245 | 1419.3245 | 2956.8 | 4.0472 | 22.2 | 0.01631 | 4.0472 | 22.2 | 0.01631 | 4.0472 | 22.2 | 0.01631
CE185 | 1541.5256 | 1336.897 | 139.2444 | 65.3842 | 4534.5283 | 1577.7283 | 2956.8 | 4395.2832 | 1438.4832 | 2956.8 | 2.8512 | 22.2 | 0.016151 | 2.8512 | 22.2 | 0.016151 | 2.8512 | 22.2 | 0.016151
CE190 | 163.9975 | 137.5107 | 18.0236 | 8.4632 | 577.1889 | 207.5889 | 369.6 | 559.1652 | 189.5652 | 369.6 | 3.4096 | 22.2 | 0.015921 | 3.4096 | 22.2 | 0.015921 | 3.4096 | 22.2 | 0.015921
CE195 | 249.7321 | 216.4828 | 22.6253 | 10.6241 | 600.9508 | 231.3508 | 369.6 | 578.3252 | 208.7252 | 369.6 | 2.3158 | 22.2 | 0.01547 | 2.3158 | 22.2 | 0.01547 | 2.3158 | 22.2 | 0.01547
CE200 | 1479.9926 | 1252.8566 | 154.56 | 72.576 | 5497.5648 | 4276.5408 | 1221.024 | 5343.0048 | 4121.9808 | 1221.024 | 3.6102 | 26.7339 | 0.011281 | 3.6102 | 26.7339 | 0.011281 | 3.6102 | 26.7339 | 0.011281

## TRN-re
HVBTOUT2.WK3, 23 May 2000 | [5 empty] | Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST | [9 empty] | TRNSYS 14.2-TUD with realistic controller model
"Real control minimum on/off time results | [5 empty] | Program Version Release Date:
[6 empty] | Program Name for Tables and Charts: |  |  |  | TRN-re
INSTRUCTIONS | [5 empty] | Results Submission Date: |  |  |  | 2000-05-23
Modeler Organization for Titles (long):
1. Use specified units | [9 empty] | Technische Universität Dresden, Germany
[6 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TUD
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
TRNSYS, realistic controller, 23 May 00
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  |  |  | February Totals | [6 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
Cases | Cooling Energie Consumption | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  | Envelope Load | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg]
CE100 | 1511.9369 | 1302.7258 | 142.3625 | 66.8486 | 3797.9491 | 3797.9491 | 3.3138e-14 | 3655.5859 | 3655.5859 | 0 | 2.4184 | 22.6346 | 0.0075088 | 2.4184 | 23.21 | 0.007509 | 2.4184 | 22.09 | 0.007509
CE110 | 1061.9658 | 875.8322 | 126.659 | 59.4747 | 3763.2362 | 3763.2362 | 2.6912e-15 | 3636.5534 | 3636.5534 | 0 | 3.4271 | 22.5242 | 0.0066309 | 3.4553 | 23.06 | 0.006631 | 3.419 | 21.98 | 0.006631
CE120 | 1001.6637 | 831.9292 | 115.4998 | 54.2347 | 3746.8105 | 3746.8105 | 3.8103e-15 | 3631.3216 | 3631.3216 | 0 | 3.6313 | 27.0785 | 0.0079517 | 3.6541 | 28.26 | 0.007952 | 3.6095 | 26.17 | 0.007952
CE130 | 110.1161 | 94.8489 | 10.3889 | 4.8783 | 219.7695 | 219.7695 | 3.1415e-14 | 209.371 | 209.371 | 0 | 1.9163 | 21.6377 | 0.0075194 | 2.0033 | 22.25 | 0.007519 | 1.6737 | 21.03 | 0.007519
CE140 | 68.6428 | 56.5735 | 8.2128 | 3.8565 | 198.5643 | 198.5643 | -2.7533e-16 | 190.358 | 190.358 | 0 | 2.7996 | 21.5097 | 0.0065941 | 2.8848 | 22.25 | 0.006594 | 2.3127 | 20.76 | 0.006594
CE150 | 1191.613 | 986.7503 | 139.4036 | 65.4591 | 4515.0285 | 3775.8216 | 739.2069 | 4375.5775 | 3636.3775 | 739.2 | 3.6734 | 22.6771 | 0.0085152 | 3.6952 | 23.28 | 0.008566 | 3.6611 | 22.06 | 0.008454
CE160 | 1132.8835 | 944.3585 | 128.2863 | 60.2388 | 4498.8816 | 3759.6868 | 739.1947 | 4370.6181 | 3631.4181 | 739.2 | 3.8599 | 26.9948 | 0.010236 | 3.8606 | 27.61 | 0.01029 | 3.8212 | 26.39 | 0.01018
CE165 | 1489.9268 | 1272.4664 | 147.976 | 69.4843 | 4535.1008 | 3795.9117 | 739.1892 | 4387.1605 | 3647.9605 | 739.2 | 2.9449 | 23.7805 | 0.0095112 | 2.9584 | 24.48 | 0.009553 | 2.9336 | 23.26 | 0.009434
CE170 | 635.8287 | 528.5837 | 72.9774 | 34.2676 | 2231.6345 | 1492.423 | 739.2115 | 2158.621 | 1419.421 | 739.2 | 3.4033 | 22.1169 | 0.010525 | 3.4645 | 22.67 | 0.01065 | 3.3167 | 21.57 | 0.0104
CE180 | 1080.0377 | 906.4398 | 118.1287 | 55.4691 | 4494.0999 | 1537.3001 | 2956.7992 | 4375.9707 | 1419.1707 | 2956.8 | 4.055 | 22.3344 | 0.016404 | 4.0754 | 22.79 | 0.01679 | 4.028 | 22.01 | 0.01613
CE185 | 1538.3972 | 1334.3908 | 138.821 | 65.1855 | 4533.9432 | 1577.1233 | 2956.8195 | 4395.0925 | 1438.2925 | 2956.8 | 2.8574 | 22.3682 | 0.016279 | 2.8622 | 22.61 | 0.01648 | 2.8362 | 22.13 | 0.01608
CE190 | 165.1202 | 138.4572 | 18.1435 | 8.5195 | 577.6703 | 208.0235 | 369.6468 | 559.4558 | 189.8558 | 369.6 | 3.4048 | 21.9469 | 0.015707 | 3.508 | 22.25 | 0.01595 | 3.1652 | 21.63 | 0.01546
CE195 | 251.5799 | 218.0909 | 22.7884 | 10.7006 | 601.339 | 231.7335 | 369.6055 | 578.542 | 208.942 | 369.6 | 2.3054 | 22.0113 | 0.015326 | 2.4571 | 22.26 | 0.01551 | 2.2587 | 21.76 | 0.01514
CE200 | 1479.9926 | 1252.8566 | 154.56 | 72.576 | 5497.5648 | 4276.5408 | 1221.024 | 5343.0048 | 4121.9808 | 1221.024 | 3.6102 | 26.7339 | 0.011281 | 3.6102 | 26.73 | 0.01128 | 3.6102 | 26.73 | 0.01128

## CA-SIS
Program Name and Version (with full build detail):
CA-SIS V1
Program Version Release Date:
[5 empty] | Program Name for Tables and Charts: |  |  |  | CA-SIS
[5 empty] | Results Submission Date: |  |  |  | 2000-05-01
Modeler Organization for Titles (long):
Electricité de France, France
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | EDF
C
CA-SIS 05/00
Entered at A25 from CASI0500.WK3 a:a7..a:t20
| February Totals | [9 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
| cooloing energy Consumption |  |  |  | Evaporator coil Load |  |  | envelope load
cases | Total | compres-sor | supply fan | conden-ser fan | total | sensible | latent | total | sensible | latent | COP | IDB | humidity ratio | COP | IDB | humidity ratio | COP | IDB | humidity ratio
| kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh |  | °C | kg/kg |  | °C | kg/kg |  | °C | kg/kg
CE100 | 1531 | 1319 | 144 | 68 | 3800 | 3800 | 0 | 3656 | 3656 | 0 | 2.39 | 22.2 | 0.0075 | 2.39 | 22.2 | 0.0075 | 2.39 | 22.2 | 0.0075
CE110 | 1077 | 889 | 128 | 60 | 3765 | 3765 | 0 | 3637 | 3637 | 0 | 3.38 | 22.2 | 0.0066 | 3.38 | 22.2 | 0.0066 | 3.38 | 22.2 | 0.0066
CE120 | 1012 | 840 | 117 | 55 | 3749 | 3749 | 0 | 3632 | 3632 | 0 | 3.59 | 26.7 | 0.008 | 3.59 | 26.7 | 0.008 | 3.59 | 26.7 | 0.008
CE130 | 110 | 95 | 10 | 5 | 219 | 219 | 0 | 209 | 209 | 0 | 1.91 | 22.2 | 0.0075 | 1.91 | 22.2 | 0.0075 | 1.91 | 22.2 | 0.0075
CE140 | 68 | 57 | 8 | 4 | 198 | 198 | 0 | 190 | 190 | 0 | 2.77 | 22.2 | 0.0065 | 2.77 | 22.2 | 0.0065 | 2.77 | 22.2 | 0.0065
CE150 | 1208 | 1000 | 141 | 66 | 4517 | 3778 | 739 | 4376 | 3637 | 739 | 3.62 | 22.2 | 0.0083 | 3.63 | 22.2 | 0.0084 | 3.62 | 22.2 | 0.0083
CE160 | 1140 | 950 | 129 | 61 | 4501 | 3761 | 740 | 4371 | 3632 | 739 | 3.84 | 26.7 | 0.0102 | 3.84 | 26.7 | 0.0103 | 3.83 | 26.7 | 0.0101
CE165 | 1502 | 1283 | 149 | 70 | 4538 | 3798 | 740 | 4388 | 3649 | 739 | 2.92 | 23.3 | 0.0093 | 2.94 | 23.3 | 0.0094 | 2.91 | 23.3 | 0.0093
CE170 | 638 | 531 | 73 | 34 | 2233 | 1493 | 740 | 2159 | 1420 | 739 | 3.38 | 22.2 | 0.0106 | 3.38 | 22.2 | 0.106 | 3.38 | 22.2 | 0.106
CE180 | 1083 | 909 | 118 | 56 | 4495 | 1537 | 2958 | 4376 | 1420 | 2957 | 4.04 | 22.2 | 0.0164 | 4.05 | 22.2 | 0.0165 | 4.03 | 22.2 | 0.0162
CE185 | 1544 | 1340 | 139 | 65 | 4507 | 1548 | 2959 | 4396 | 1439 | 2957 | 2.85 | 22.2 | 0.0162 | 2.86 | 22.2 | 0.0163 | 2.84 | 22.2 | 0.0161
CE190 | 164 | 138 | 18 | 8 | 578 | 208 | 370 | 557 | 190 | 367 | 3.41 | 22.2 | 0.016 | 3.41 | 22.2 | 0.016 | 3.41 | 22.2 | 0.016
CE195 | 250 | 217 | 23 | 11 | 602 | 232 | 370 | 576 | 209 | 367 | 2.31 | 22.2 | 0.0156 | 2.31 | 22.2 | 0.0156 | 2.31 | 22.2 | 0.0156
CE200 | 1477 | 1250 | 154 | 73 | 5498 | 4276 | 1222 | 5343 | 4122 | 1221 | 3.62 | 26.7 | 0.0114 | 3.63 | 26.7 | 0.0115 | 3.61 | 26.7 | 0.0113

## E+V1
HVBOUT2A.WK3, August 08, 2000 |  |  |  |  | Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST | [8 empty] | EnergyPlus Version 1.0.0.023
EnergyPlus Version 1.0.0.023 14Jun01 |  |  |  |  | Program Version Release Date:
[5 empty] | Program Name for Tables and Charts: |  |  |  | EnergyPlus
INSTRUCTIONS |  |  |  |  | Results Submission Date: |  |  |  | 2001-06-14
Modeler Organization for Titles (long):
1. Use specified units | [8 empty] | GARD Analytics, USA
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | GARD
2. Data entry is restricted to columns B through T and rows 25 through 38. ; The protection
;; option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. ; Similarly,
;; February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
;; of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y ;; T o t a l s | [6 empty] | February Mean |  | ;;;;;;; February Maximum |  |  | ;;;;;;; February Minimum
|  | Cooling Energy Consumption |  |  | ;;;;;;;;;;; Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1520.0282 |  | 143.5533 |  | 3797.6497 | 3797.6448 | 0.0049461 | 3654.1272 | 3654.1272 | 0 | 2.404 | 22.1999 | 0.0074745 | 2.4067 | 22.2001 | 0.0074747 | 2.4005 | 22.1997 | 0.0074708
CE110 | 1069.0685 |  | 127.5385 |  | 3763.0688 | 3763.0651 | 0.00371 | 3635.5345 | 3635.5345 | 0 | 3.4007 | 22.1999 | 0.0065835 | 3.4049 | 22.2002 | 0.0065837 | 3.3954 | 22.1997 | 0.0065804
CE120 | 1006.3903 |  | 116.3845 |  | 3746.9059 | 3746.9017 | 0.0042294 | 3630.5353 | 3630.5353 | 0 | 3.6075 | 26.7 | 0.0080402 | 3.6118 | 26.7001 | 0.0080404 | 3.6019 | 26.6997 | 0.0080362
CE130 | 108.5963 |  | 10.2557 |  | 217.0012 | 217.0004 | 0.000795 | 206.7475 | 206.7475 | 0 | 1.9038 | 22.2 | 0.0074769 | 1.907 | 22.2 | 0.0074771 | 1.8999 | 22.2 | 0.0074725
CE140 | 67.903 |  | 8.1004 |  | 196.2821 | 196.2815 | 0.00067806 | 188.1832 | 188.1832 | 0 | 2.7714 | 22.2 | 0.0065863 | 2.7761 | 22.2 | 0.0065865 | 2.7656 | 22.2 | 0.0065822
CE150 | 1197.1085 |  | 140.2495 |  | 4508.7225 | 3776.027 | 732.6956 | 4374.7468 | 3635.5501 | 739.1966 | 3.6544 | 22.1999 | 0.0084223 | 3.6756 | 22.2002 | 0.0084444 | 3.637 | 22.1996 | 0.0083341
CE160 | 1131.7342 |  | 128.2763 |  | 4491.0487 | 3759.0367 | 732.0119 | 4369.7196 | 3630.5229 | 739.1966 | 3.8611 | 26.6999 | 0.010278 | 3.8843 | 26.7005 | 0.010307 | 3.8417 | 26.6993 | 0.010169
CE165 | 1491.0755 |  | 148.5366 |  | 4528.6592 | 3795.4926 | 733.1667 | 4385.9248 | 3646.7281 | 739.1966 | 2.9415 | 23.2999 | 0.0093948 | 2.9606 | 23.3004 | 0.0094184 | 2.9255 | 23.2994 | 0.0092952
CE170 | 635.3716 |  | 73.0096 |  | 2224.8677 | 1491.221 | 733.6467 | 2157.1388 | 1417.9388 | 739.2 | 3.3951 | 22.1999 | 0.010571 | 3.4229 | 22.2002 | 0.010593 | 3.3713 | 22.1997 | 0.010472
CE180 | 1082.0002 |  | 118.3832 |  | 4481.208 | 1537.3461 | 2943.8619 | 4374.7389 | 1417.9523 | 2956.7866 | 4.0432 | 22.2 | 0.016193 | 4.1051 | 22.2002 | 0.016224 | 3.9865 | 22.1997 | 0.016057
CE185 | 1540.3879 |  | 139.1103 |  | 4522.5899 | 1576.6014 | 2945.9884 | 4393.3107 | 1436.5241 | 2956.7866 | 2.8521 | 22.2 | 0.016067 | 2.9025 | 22.2001 | 0.016096 | 2.8049 | 22.1998 | 0.015922
CE190 | 164.3348 |  | 18.0337 |  | 574.3018 | 206.3654 | 367.9364 | 557.7813 | 188.1822 | 369.5991 | 3.3942 | 22.2 | 0.015855 | 3.4525 | 22.2 | 0.015913 | 3.3182 | 22.2 | 0.015683
CE195 | 250.2299 |  | 22.6607 |  | 597.7018 | 229.5563 | 368.1456 | 576.347 | 206.7479 | 369.5991 | 2.3033 | 22.2 | 0.015446 | 2.3495 | 22.2 | 0.015494 | 2.2496 | 22.2 | 0.015281
CE200 | 1464.5945 |  | 153.3548 |  | 5484.4779 | 4274.2567 | 1210.2212 | 5341.5034 | 4120.521 | 1220.9824 | 3.6471 | 26.6999 | 0.011461 | 3.6707 | 26.7005 | 0.01149 | 3.6271 | 26.6993 | 0.011342

## Analytical-TUD
HVBTOUT2.WK3, September 02, 1998 |  |  |  |  | Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST | [8 empty] | Quasi-Analytical Solution with ideal controller model
TUD Analytical Verification |  |  |  |  | Program Version Release Date:
[5 empty] | Program Name for Tables and Charts: |  |  |  | Analytical
INSTRUCTIONS |  |  |  |  | Results Submission Date: |  |  |  | 2000-08-10
Modeler Organization for Titles (long):
1. Use specified units | [8 empty] | Technische Universität Dresden, Germany
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TUD
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
TUD Analytical Verication, 10 Aug 00 |  |  |  | Patm = 101325 Pa; difference between saturation enthalpy and zone air enthalpy considered
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1530.548 | 1318.8515 | 144.0538 | 67.6427 | 3800.3599 | 3800.3599 | 0 | 3656.3062 | 3656.3062 | 0 | 2.3889 | 22.2 | 0.0074274 | 2.3889 | 22.2 | 0.0074274 | 2.3889 | 22.2 | 0.0074274
CE110 | 1076.2349 | 887.9378 | 128.1312 | 60.166 | 3765.2438 | 3765.2438 | 0 | 3637.1129 | 3637.1129 | 0 | 3.3795 | 22.2 | 0.0065187 | 3.3795 | 22.2 | 0.0065187 | 3.3795 | 22.2 | 0.0065187
CE120 | 1012.6774 | 840.8662 | 116.9129 | 54.8982 | 3748.902 | 3748.902 | 0 | 3631.9893 | 3631.9893 | 0 | 3.5865 | 26.7 | 0.0078783 | 3.5865 | 26.7 | 0.0078783 | 3.5865 | 26.7 | 0.0078783
CE130 | 110.5818 | 95.2867 | 10.4079 | 4.8872 | 219.3541 | 219.3541 | 0 | 208.9462 | 208.9462 | 0 | 1.8895 | 22.2 | 0.0074274 | 1.8895 | 22.2 | 0.0074274 | 1.8895 | 22.2 | 0.0074274
CE140 | 68.9953 | 56.924 | 8.2142 | 3.8571 | 197.9671 | 197.9671 | 0 | 189.7529 | 189.7529 | 0 | 2.7502 | 22.2 | 0.0065187 | 2.7502 | 22.2 | 0.0065187 | 2.7502 | 22.2 | 0.0065187
CE150 | 1206.49 | 998.9576 | 141.2203 | 66.3121 | 4517.5274 | 3778.3318 | 739.1956 | 4376.3129 | 3637.1129 | 739.2 | 3.6273 | 22.2 | 0.0082272 | 3.6273 | 22.2 | 0.0082272 | 3.6273 | 22.2 | 0.0082272
CE160 | 1140.44 | 950.4111 | 129.3096 | 60.7193 | 4500.5449 | 3761.3053 | 739.2396 | 4371.1893 | 3631.9893 | 739.2 | 3.8329 | 26.7 | 0.009969 | 3.8329 | 26.7 | 0.009969 | 3.8329 | 26.7 | 0.009969
CE165 | 1497.8302 | 1278.7205 | 149.0983 | 70.0114 | 4536.998 | 3797.7525 | 739.2454 | 4387.8381 | 3648.6381 | 739.2 | 2.9295 | 23.3 | 0.0092694 | 2.9295 | 23.3 | 0.0092694 | 2.9295 | 23.3 | 0.0092694
CE170 | 641.1173 | 532.9693 | 73.5918 | 34.5562 | 2232.3427 | 1493.027 | 739.3157 | 2158.7129 | 1419.5129 | 739.2 | 3.3672 | 22.2 | 0.010367 | 3.3672 | 22.2 | 0.010367 | 3.3672 | 22.2 | 0.010367
CE180 | 1082.666 | 908.1216 | 118.7728 | 55.7716 | 4495.2651 | 1537.7939 | 2957.4713 | 4376.3129 | 1419.5129 | 2956.8 | 4.0423 | 22.2 | 0.01619 | 4.0423 | 22.2 | 0.01619 | 4.0423 | 22.2 | 0.01619
CE185 | 1544.6397 | 1339.7996 | 139.3882 | 65.4519 | 4535.1231 | 1577.6007 | 2957.5224 | 4395.5062 | 1438.7062 | 2956.8 | 2.8458 | 22.2 | 0.016056 | 2.8458 | 22.2 | 0.016056 | 2.8458 | 22.2 | 0.016056
CE190 | 165.173 | 138.4708 | 18.1701 | 8.5321 | 577.5279 | 207.8123 | 369.7156 | 559.3529 | 189.7529 | 369.6 | 3.3865 | 22.2 | 0.015796 | 3.3865 | 22.2 | 0.015796 | 3.3865 | 22.2 | 0.015796
CE195 | 252.1605 | 218.6235 | 22.821 | 10.716 | 601.3744 | 231.645 | 369.7294 | 578.5462 | 208.9462 | 369.6 | 2.2944 | 22.2 | 0.015368 | 2.2944 | 22.2 | 0.015368 | 2.2944 | 22.2 | 0.015368
CE200 | 1475.8104 | 1248.8198 | 154.4611 | 72.5296 | 5497.8008 | 4276.6945 | 1221.1063 | 5343.2549 | 4122.2309 | 1221.024 | 3.6206 | 26.7 | 0.011129 | 3.6206 | 26.7 | 0.011129 | 3.6206 | 26.7 | 0.011129

## Analytical-HTAL1
Program Name and Version (with full build detail):
Quasi-Analytical Solution with ideal controller model
Program Version Release Date:
[5 empty] | Program Name for Tables and Charts: |  |  |  | Analytical
[5 empty] | Results Submission Date: |  |  |  | 2000-08-15
Modeler Organization for Titles (long):
Hochschule Technik & Architektur Luzern, Switzerland
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | HTAL1
27 | 1999
HTAL1 (analytical verification) updated by jn 15 Aug 00 (Markus' results sent 25 Jul 00)
100 | 1530.8 | 1319 | 144.1 | 67.6 | 3800.4 | 3800.4 | 0 | 3656.3 | 3656.3 | 0 | 2.39 | 22.2 | 0.00734
110 | 1077.2 | 889.2 | 127.9 | 60.1 | 3765 | 3765 | 0 | 3637.1 | 3637.1 | 0 | 3.38 | 22.2 | 0.0064
120 | 1011 | 839.1 | 116.9 | 54.9 | 3748.8 | 3748.8 | 0 | 3631.9 | 3631.9 | 0 | 3.59 | 26.7 | 0.00786
130 | 109.5 | 94.4 | 10.3 | 4.8 | 219.3 | 219.3 | 0 | 209 | 209 | 0 | 1.91 | 22.2 | 0.00734
140 | 68.5 | 56.5 | 8.1 | 3.8 | 197.9 | 197.9 | 0 | 189.7 | 189.7 | 0 | 2.77 | 22.2 | 0.0064
150 | 1206.5 | 999.2 | 141.1 | 66.3 | 4517.4 | 3778.2 | 739.2 | 4376.3 | 3637.1 | 739.2 | 3.63 | 22.2 | 0.0082
160 | 1139.3 | 949.4 | 129.2 | 60.7 | 4500.3 | 3761.1 | 739.2 | 4371.1 | 3631.9 | 739.2 | 3.84 | 26.7 | 0.00994
165 | 1499.7 | 1280.2 | 149.3 | 70.1 | 4537.3 | 3798.1 | 739.2 | 4387.9 | 3648.7 | 739.2 | 2.93 | 23.3 | 0.0092
170 | 637.7 | 530 | 73.2 | 34.4 | 2231.9 | 1492.7 | 739.2 | 2158.7 | 1419.5 | 739.2 | 3.39 | 22.2 | 0.01045
180 | 1082.3 | 908 | 118.6 | 55.7 | 4494.9 | 1538.1 | 2956.8 | 4376.3 | 1419.5 | 2956.8 | 4.04 | 22.2 | 0.01623
185 | 1543.4 | 1338.6 | 139.4 | 65.4 | 4534.9 | 1578.1 | 2956.8 | 4395.5 | 1438.7 | 2956.8 | 2.85 | 22.2 | 0.01605
190 | 164.1 | 137.6 | 18 | 8.5 | 577.3 | 207.7 | 369.6 | 559.3 | 189.7 | 369.6 | 3.41 | 22.2 | 0.0159
195 | 250 | 216.8 | 22.6 | 10.6 | 601.2 | 231.6 | 369.6 | 578.6 | 209 | 369.6 | 2.31 | 22.2 | 0.01544
200 | 1477.4 | 1250.2 | 154.6 | 72.6 | 5497.8 | 4276.8 | 1221 | 5343.2 | 4122.2 | 1221 | 3.62 | 26.7 | 0.01109

## Analytical-HTAL2
Program Name and Version (with full build detail):
Quasi-Analytical Solution with realistic controller model
Program Version Release Date:
[5 empty] | Program Name for Tables and Charts: |  |  |  | Analytical
[5 empty] | Results Submission Date: |  |  |  | 2000-09-05
Modeler Organization for Titles (long):
Hochschule Technik & Architektur Luzern, Switzerland
[5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | HTAL2
HTAL numerical solution ("HTAL2"), 05 sep 00
100 | 1530.6 | 1318.9 | 144 | 67.6 | 3800.4 | 3800.4 | 0 | 3656.3 | 3656.3 | 0 | 2.39 | 22.216 | 0.007339 | 2.3893 | 22.235 | 0.007339 | 2.389 | 22.197 | 0.007339
110 | 1077.4 | 889.4 | 127.9 | 60.1 | 3765.3 | 3765.3 | 0 | 3637.1 | 3637.1 | 0 | 3.38 | 22.214 | 0.006411 | 3.3783 | 22.235 | 0.006411 | 3.377 | 22.193 | 0.006411
120 | 1011 | 839.2 | 116.9 | 54.9 | 3748.5 | 3748.5 | 0 | 3631.9 | 3631.9 | 0 | 3.59 | 26.712 | 0.007873 | 3.5941 | 26.735 | 0.007873 | 3.593 | 26.689 | 0.007873
130 | 109.5 | 94.3 | 10.3 | 4.8 | 219.2 | 219.2 | 0 | 209 | 209 | 0 | 1.91 | 22.187 | 0.007339 | 1.9079 | 22.202 | 0.007339 | 1.908 | 22.172 | 0.007339
140 | 68.3 | 56.4 | 8.1 | 3.8 | 197.3 | 197.3 | 0 | 189.7 | 189.7 | 0 | 2.77 | 22.185 | 0.006402 | 2.7701 | 22.202 | 0.006402 | 2.77 | 22.168 | 0.006402
150 | 1206.5 | 999.2 | 141.1 | 66.2 | 4518.3 | 3779 | 739.4 | 4376.3 | 3637.1 | 739.2 | 3.63 | 22.216 | 0.00821 | 3.6295 | 22.235 | 0.008212 | 3.626 | 22.197 | 0.008209
160 | 1138.9 | 949.1 | 129.2 | 60.7 | 4499.9 | 3760.8 | 739.1 | 4371.1 | 3631.9 | 739.2 | 3.84 | 26.714 | 0.009946 | 3.838 | 26.735 | 0.009948 | 3.837 | 26.693 | 0.009944
165 | 1499.6 | 1280.2 | 149.3 | 70.1 | 4537.9 | 3798.6 | 739.3 | 4387.9 | 3648.7 | 739.2 | 2.93 | 23.317 | 0.009208 | 2.9269 | 23.335 | 0.00921 | 2.926 | 23.299 | 0.009207
170 | 637.8 | 530.1 | 73.2 | 34.4 | 2232.5 | 1493.1 | 739.4 | 2158.7 | 1419.5 | 739.2 | 3.39 | 22.199 | 0.010451 | 3.3859 | 22.214 | 0.010454 | 3.385 | 22.185 | 0.010448
180 | 1081.9 | 907.7 | 118.5 | 55.7 | 4493.8 | 1537.7 | 2956.1 | 4376.3 | 1419.5 | 2956.8 | 4.04 | 22.205 | 0.01623 | 4.0442 | 22.214 | 0.016237 | 4.044 | 22.196 | 0.016222
185 | 1542.9 | 1338.2 | 139.3 | 65.4 | 4533.9 | 1577.7 | 2956.2 | 4395.5 | 1438.7 | 2956.8 | 2.85 | 22.206 | 0.016059 | 2.8485 | 22.214 | 0.016065 | 2.848 | 22.198 | 0.016052
190 | 164.2 | 137.7 | 18 | 8.5 | 577.7 | 207.9 | 369.8 | 559.3 | 189.7 | 369.6 | 3.41 | 22.194 | 0.015891 | 3.4087 | 22.202 | 0.015897 | 3.409 | 22.186 | 0.015885
195 | 250 | 216.8 | 22.6 | 10.6 | 601.2 | 231.6 | 369.6 | 578.6 | 209 | 369.6 | 2.31 | 22.195 | 0.015439 | 2.3143 | 22.202 | 0.015444 | 2.314 | 22.188 | 0.015434
200 | 1477.1 | 1250 | 154.6 | 72.6 | 5497.8 | 4276.8 | 1221 | 5343.2 | 4122.2 | 1221 | 3.62 | 26.713 | 0.011099 | 3.6173 | 26.713 | 0.011099 | 3.617 | 26.713 | 0.011099