## Read Me
ASHRAE Standard 140-2020
Informative Annex B16, Section B16.5.2 Example Results
for
Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
This spreadsheet contains the Standard 140, Informative Annex B16, Section B16.5.2 example results.
Users interested in looking at the example result tables and figures should go to the "Table List"
and "Figure List" sheets for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE: (see RESULTS5-3B.DOCX for spreadsheet navigation)
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results. See instructions on page.
"Program List" : Documentation of simulation programs used to produce informative Annex B16, Section B16.5.2 example results
"Table List" : Listing of informative Annex B16, Section B16.5.2 Tables with locations
"Figure List" : Listing of informative Annex B16, Section B16.5.2 Figures with locations
"Table-Q" through "Table-T" : Formatted result tables
"Fig B16.5.2-1 Qtot" through "Fig B16.5.2-52 HrOHR": Result figures
"A" : Unformatted raw data compilation, all programs used by tables.
"Qdata" through "Tdata" : Unformatted results for use in charts.
Individual Example Result Worksheets as follows:
TRNSYS-TUD: Example Results for TRANSYS 14.2 submitted by Technische Universität Dresden, Germany
DOE22: Example Results for DOE 2.2 nt42, submitted by National Renewable Energy Laboratory, USA
DOE21E: Example Results for DOE 2.1E build 120, submitted by National Renewable Energy Laboratory, USA
EnergyPlus1.0: Example Results for EnergyPlus Version 1.0 submitted by GARD Analytics
CodyRun: Example Results for CodyRun/LGIMAT submitted by Universite de la Reunion Island, France
HOT3000: Example Results for HOT3000/ESP-r submitted by CANMET Energy Technology Centre, Natural Resources Canada, Canada

## Adding Results
RESULTS5-3B.XLSX
Output spreadsheet for Section 5.3 - Cooling Equipment Tests CE300 through CE545
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
New result data can be entered on sheet "YourData". The format for the results data is identical to the Standard Output Report (Sec5-3Bout.XLS).
Import data so that Cell B62 of Sec5-3Bout.XLS is in B62 of Sheet "YourData". Data should land in "YourData" cells as tabulated below.
The new data will then appear in rightmost column of each table on sheets "Table-Q" to "Table-T". Chart update of "YourData" is also automated.
Complete the program information block on "Yourdata" which is used for legend titles for the tables and graphs.
Sample Program Information Block (Complete for For New Results On Your Data)
Program Name and Version (with full build detail):
Tested Program V1.2.3
| Program Version Release Date: |  |  |  | 2009-01-01
| Program Name for Tables and Charts (short): |  |  |  | Tested Prg
| Results Submission Date: |  |  |  | 2010-01-01
Modeler Organization for Titles (long):
Testing Organization
| Modeler Organization for Tables and Charts (short): |  |  |  | Org
CELL ADDRESS GUIDE FOR EXAMPLE RESULT SHEETS AND NEW RESULTS DATA
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
CE300 | B62 | C62 | D62 | E62 | F62 | G62 | H62 | I62 | J62 | K62 | L62 | M62 | N62 | CE300 | Q62 | R62 | S62 | T62 | U62 | V62 | W62 | X62 | Y62 | Z62 | AA62 | AB62 | AC62 | AD62 | AE62 | AF62 | AG62 | AH62
CE310 | B63 | C63 | D63 | E63 | F63 | G63 | H63 | I63 | J63 | K63 | L63 |  |  | CE310 | Q63 | R63 | S63 | T63 | U63 | V63 | W63 | X63 | Y63 | Z63 | AA63 | AB63
CE320 | B64 | C64 | D64 | E64 | F64 | G64 | H64 | I64 | J64 | K64 | L64 |  |  | CE320 | Q64 | R64 | S64 | T64 | U64 | V64 | W64 | X64 | Y64 | Z64 | AA64 | AB64
CE330 | B65 | C65 | D65 | E65 | F65 | G65 | H65 | I65 | J65 | K65 | L65 |  |  | CE330 | Q65 | R65 | S65 | T65 | U65 | V65 | W65 | X65 | Y65 | Z65 | AA65 | AB65
CE340 | B66 | C66 | D66 | E66 | F66 | G66 | H66 | I66 | J66 | K66 | L66 |  |  | CE340 | Q66 | R66 | S66 | T66 | U66 | V66 | W66 | X66 | Y66 | Z66 | AA66 | AB66
CE350 | B67 | C67 | D67 | E67 | F67 | G67 | H67 | I67 | J67 | K67 | L67 |  |  | CE350 | Q67 | R67 | S67 | T67 | U67 | V67 | W67 | X67 | Y67 | Z67 | AA67 | AB67
CE360 | B68 | C68 | D68 | E68 | F68 | G68 | H68 | I68 | J68 | K68 | L68 |  |  | CE360 | Q68 | R68 | S68 | T68 | U68 | V68 | W68 | X68 | Y68 | Z68 | AA68 | AB68
CE400 | B69 | C69 | D69 | E69 | F69 | G69 | H69 | I69 | J69 | K69 | L69 |  |  | CE400 | Q69 | R69 | S69 | T69 | U69 | V69 | W69 | X69 | Y69 | Z69 | AA69 | AB69
CE410 | B70 | C70 | D70 | E70 | F70 | G70 | H70 | I70 | J70 | K70 | L70 |  |  | CE410 | Q70 | R70 | S70 | T70 | U70 | V70 | W70 | X70 | Y70 | Z70 | AA70 | AB70
CE420 | B71 | C71 | D71 | E71 | F71 | G71 | H71 | I71 | J71 | K71 | L71 |  |  | CE420 | Q71 | R71 | S71 | T71 | U71 | V71 | W71 | X71 | Y71 | Z71 | AA71 | AB71
CE430 | B72 | C72 | D72 | E72 | F72 | G72 | H72 | I72 | J72 | K72 | L72 |  |  | CE430 | Q72 | R72 | S72 | T72 | U72 | V72 | W72 | X72 | Y72 | Z72 | AA72 | AB72
CE440 | B73 | C73 | D73 | E73 | F73 | G73 | H73 | I73 | J73 | K73 | L73 |  |  | CE440 | Q73 | R73 | S73 | T73 | U73 | V73 | W73 | X73 | Y73 | Z73 | AA73 | AB73
CE500 | B74 | C74 | D74 | E74 | F74 | G74 | H74 | I74 | J74 | K74 | L74 |  |  | CE500 | Q74 | R74 | S74 | T74 | U74 | V74 | W74 | X74 | Y74 | Z74 | AA74 | AB74
CE500 May-Sep | B75 | C75 | D75 | E75 | F75 | G75 | H75 | I75 | J75 | K75 | L75 |  |  | CE510 | Q75 | R75 | S75 | T75 | U75 | V75 | W75 | X75 | Y75 | Z75 | AA75 | AB75
CE510 May-Sep | B76 | C76 | D76 | E76 | F76 | G76 | H76 | I76 | J76 | K76 | L76 |  |  | CE520 | Q76 | R76 | S76 | T76 | U76 | V76 | W76 | X76 | Y76 | Z76 | AA76 | AB76
CE520 | B77 | C77 | D77 | E77 | F77 | G77 | H77 | I77 | J77 | K77 | L77 |  |  | CE522 | Q77 | R77 | S77 | T77 | U77 | V77 | W77 | X77 | Y77 | Z77 | AA77 | AB77
CE522 | B78 | C78 | D78 | E78 | F78 | G78 | H78 | I78 | J78 | K78 | L78 |  |  | CE525 | Q78 | R78 | S78 | T78 | U78 | V78 | W78 | X78 | Y78 | Z78 | AA78 | AB78
CE525 | B79 | C79 | D79 | E79 | F79 | G79 | H79 | I79 | J79 | K79 | L79 |  |  | CE530 | Q79 | R79 | S79 | T79 | U79 | V79 | W79 | X79 | Y79 | Z79 | AA79 | AB79
CE530 | B80 | C80 | D80 | E80 | F80 | G80 | H80 | I80 | J80 | K80 | L80 |  |  | CE540 | Q80 | R80 | S80 | T80 | U80 | V80 | W80 | X80 | Y80 | Z80 | AA80 | AB80
CE540 | B81 | C81 | D81 | E81 | F81 | G81 | H81 | I81 | J81 | K81 | L81 |  |  | CE545 | Q81 | R81 | S81 | T81 | U81 | V81 | W81 | X81 | Y81 | Z81 | AA81 | AB81
CE545 | B82 | C82 | D82 | E82 | F82 | G82 | H82 | I82 | J82 | K82 | L82
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e CE 3 0 0 | [10 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum* |  | Cases
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | B89 | C89 | D89 | E89 | F89 | G89 | H89 | I89 | J89 | K89 | L89 |  |  | CE300 | Q89 | R89 | S89 | T89 | U89 | V89 | W89 | X89 | Y89 | Z89 | AA89 | AB89 | AC89 | AD89 | AE89 | AF89 | AG89 | AH89 | AI89 | AJ89 | AK89 | AL89 | AM89 | AN89 | CE300
2 | B90 | C90 | D90 | E90 | F90 | G90 | H90 | I90 | J90 | K90 | L90 |  |  | CE310 | Q90 | R90 | S90 | T90 | U90 | V90 | W90 | X90 | Y90 | Z90 | AA90 | AB90 | AC90 | AD90 | AE90 | AF90 | AG90 | AH90 | AI90 | AJ90 | AK90 | AL90 | AM90 | AN90 | CE310
3 | B91 | C91 | D91 | E91 | F91 | G91 | H91 | I91 | J91 | K91 | L91 |  |  | CE320 | Q91 | R91 | S91 | T91 | U91 | V91 | W91 | X91 | Y91 | Z91 | AA91 | AB91 | AC91 | AD91 | AE91 | AF91 | AG91 | AH91 | AI91 | AJ91 | AK91 | AL91 | AM91 | AN91 | CE320
4 | B92 | C92 | D92 | E92 | F92 | G92 | H92 | I92 | J92 | K92 | L92 |  |  | CE330 | Q92 | R92 | S92 | T92 | U92 | V92 | W92 | X92 | Y92 | Z92 | AA92 | AB92 | AC92 | AD92 | AE92 | AF92 | AG92 | AH92 | AI92 | AJ92 | AK92 | AL92 | AM92 | AN92 | CE330
5 | B93 | C93 | D93 | E93 | F93 | G93 | H93 | I93 | J93 | K93 | L93 |  |  | CE340 | Q93 | R93 | S93 | T93 | U93 | V93 | W93 | X93 | Y93 | Z93 | AA93 | AB93 | AC93 | AD93 | AE93 | AF93 | AG93 | AH93 | AI93 | AJ93 | AK93 | AL93 | AM93 | AN93 | CE340
6 | B94 | C94 | D94 | E94 | F94 | G94 | H94 | I94 | J94 | K94 | L94 |  |  | CE350 | Q94 | R94 | S94 | T94 | U94 | V94 | W94 | X94 | Y94 | Z94 | AA94 | AB94 | AC94 | AD94 | AE94 | AF94 | AG94 | AH94 | AI94 | AJ94 | AK94 | AL94 | AM94 | AN94 | CE350
7 | B95 | C95 | D95 | E95 | F95 | G95 | H95 | I95 | J95 | K95 | L95 |  |  | CE360 | Q95 | R95 | S95 | T95 | U95 | V95 | W95 | X95 | Y95 | Z95 | AA95 | AB95 | AC95 | AD95 | AE95 | AF95 | AG95 | AH95 | AI95 | AJ95 | AK95 | AL95 | AM95 | AN95 | CE360
8 | B96 | C96 | D96 | E96 | F96 | G96 | H96 | I96 | J96 | K96 | L96 |  |  | CE400 | Q96 | R96 | S96 | T96 | U96 | V96 | W96 | X96 | Y96 | Z96 | AA96 | AB96 | AC96 | AD96 | AE96 | AF96 | AG96 | AH96 | AI96 | AJ96 | AK96 | AL96 | AM96 | AN96 | CE400
9 | B97 | C97 | D97 | E97 | F97 | G97 | H97 | I97 | J97 | K97 | L97 |  |  | CE410 | Q97 | R97 | S97 | T97 | U97 | V97 | W97 | X97 | Y97 | Z97 | AA97 | AB97 | AC97 | AD97 | AE97 | AF97 | AG97 | AH97 | AI97 | AJ97 | AK97 | AL97 | AM97 | AN97 | CE410
10 | B98 | C98 | D98 | E98 | F98 | G98 | H98 | I98 | J98 | K98 | L98 |  |  | CE420 | Q98 | R98 | S98 | T98 | U98 | V98 | W98 | X98 | Y98 | Z98 | AA98 | AB98 | AC98 | AD98 | AE98 | AF98 | AG98 | AH98 | AI98 | AJ98 | AK98 | AL98 | AM98 | AN98 | CE420
11 | B99 | C99 | D99 | E99 | F99 | G99 | H99 | I99 | J99 | K99 | L99 |  |  | CE430 | Q99 | R99 | S99 | T99 | U99 | V99 | W99 | X99 | Y99 | Z99 | AA99 | AB99 | AC99 | AD99 | AE99 | AF99 | AG99 | AH99 | AI99 | AJ99 | AK99 | AL99 | AM99 | AN99 | CE430
12 | B100 | C100 | D100 | E100 | F100 | G100 | H100 | I100 | J100 | K100 | L100 |  |  | CE440 | Q100 | R100 | S100 | T100 | U100 | V100 | W100 | X100 | Y100 | Z100 | AA100 | AB100 | AC100 | AD100 | AE100 | AF100 | AG100 | AH100 | AI100 | AJ100 | AK100 | AL100 | AM100 | AN100 | CE440
13 | B101 | C101 | D101 | E101 | F101 | G101 | H101 | I101 | J101 | K101 | L101 |  |  | CE500 | Q101 | R101 | S101 | T101 | U101 | V101 | W101 | X101 | Y101 | Z101 | AA101 | AB101 | AC101 | AD101 | AE101 | AF101 | AG101 | AH101 | AI101 | AJ101 | AK101 | AL101 | AM101 | AN101 | CE500
14 | B102 | C102 | D102 | E102 | F102 | G102 | H102 | I102 | J102 | K102 | L102 |  |  | CE510 | Q102 | R102 | S102 | T102 | U102 | V102 | W102 | X102 | Y102 | Z102 | AA102 | AB102 | AC102 | AD102 | AE102 | AF102 | AG102 | AH102 | AI102 | AJ102 | AK102 | AL102 | AM102 | AN102 | CE510
15 | B103 | C103 | D103 | E103 | F103 | G103 | H103 | I103 | J103 | K103 | L103 |  |  | CE520 | Q103 | R103 | S103 | T103 | U103 | V103 | W103 | X103 | Y103 | Z103 | AA103 | AB103 | AC103 | AD103 | AE103 | AF103 | AG103 | AH103 | AI103 | AJ103 | AK103 | AL103 | AM103 | AN103 | CE520
16 | B104 | C104 | D104 | E104 | F104 | G104 | H104 | I104 | J104 | K104 | L104 |  |  | CE522 | Q104 | R104 | S104 | T104 | U104 | V104 | W104 | X104 | Y104 | Z104 | AA104 | AB104 | AC104 | AD104 | AE104 | AF104 | AG104 | AH104 | AI104 | AJ104 | AK104 | AL104 | AM104 | AN104 | CE522
17 | B105 | C105 | D105 | E105 | F105 | G105 | H105 | I105 | J105 | K105 | L105 |  |  | CE525 | Q105 | R105 | S105 | T105 | U105 | V105 | W105 | X105 | Y105 | Z105 | AA105 | AB105 | AC105 | AD105 | AE105 | AF105 | AG105 | AH105 | AI105 | AJ105 | AK105 | AL105 | AM105 | AN105 | CE525
18 | B106 | C106 | D106 | E106 | F106 | G106 | H106 | I106 | J106 | K106 | L106 |  |  | CE530 | Q106 | R106 | S106 | T106 | U106 | V106 | W106 | X106 | Y106 | Z106 | AA106 | AB106 | AC106 | AD106 | AE106 | AF106 | AG106 | AH106 | AI106 | AJ106 | AK106 | AL106 | AM106 | AN106 | CE530
19 | B107 | C107 | D107 | E107 | F107 | G107 | H107 | I107 | J107 | K107 | L107 |  |  | CE540 | Q107 | R107 | S107 | T107 | U107 | V107 | W107 | X107 | Y107 | Z107 | AA107 | AB107 | AC107 | AD107 | AE107 | AF107 | AG107 | AH107 | AI107 | AJ107 | AK107 | AL107 | AM107 | AN107 | CE540
20 | B108 | C108 | D108 | E108 | F108 | G108 | H108 | I108 | J108 | K108 | L108 |  |  | CE545 | Q108 | R108 | S108 | T108 | U108 | V108 | W108 | X108 | Y108 | Z108 | AA108 | AB108 | AC108 | AD108 | AE108 | AF108 | AG108 | AH108 | AI108 | AJ108 | AK108 | AL108 | AM108 | AN108 | CE545
21 | B109 | C109 | D109 | E109 | F109 | G109 | H109 | I109 | J109 | K109 | L109 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | B110 | C110 | D110 | E110 | F110 | G110 | H110 | I110 | J110 | K110 | L110
23 | B111 | C111 | D111 | E111 | F111 | G111 | H111 | I111 | J111 | K111 | L111
24 | B112 | C112 | D112 | E112 | F112 | G112 | H112 | I112 | J112 | K112 | L112
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | B120 | C120 | D120 | E120 | F120 | G120 | H120 | I120 | J120 | K120 | L120
June 25 | B121 | C121 | D121 | E121 | F121 | G121 | H121 | I121 | J121 | K121 | L121
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | B129 | C129 | D129 | E129 | F129 | G129 | H129 | I129 | J129 | K129 | L129
June 25 | B130 | C130 | D130 | E130 | F130 | G130 | H130 | I130 | J130 | K130 | L130

## YourData
Sec5-3Bout.XLS |  |  |  |  | Program Name and Version (with full build detail):
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545 |  |  |  |  | EnergyPlus 22.2
[5 empty] | Program Version Release Date: |  |  |  | 09/27/22
Content Instructions (same as for Sec5-3Bout.XLS) |  |  |  |  | Program Name for Tables and Charts (short): |  |  |  | E+
[5 empty] | Results Submission Date: |  |  |  | 11/03/2022
1. Use specified units |  |  |  |  | Modeler Organization for Titles (long):
National Renewable Energy Laboratory
2. Data entry is restricted to the following ranges: |  |  |  |  | Modeler Organization for Tables and Charts (short): |  |  |  | NREL
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
CE300 | 35068.4 |  |  | 10862.1 | 78483.2 | 55162.5 | 23320.7 | 3.2423 | 24.09 | 0.0091452 | 47.8416 | 19.9141 | 0.011608 | CE300 | 12008.3 | 20-Jul | 15 | 23460.4 | 20-Jul | 15 | 10627.1 | 10-Jul | 13 | 33102.8 | 20-Jul | 15 | 34.775 | 20-Jul | 15 | 0.021868 | 02-Oct | 9
CE310 | 39454.7 |  |  | 10862.1 | 97424.1 | 55040.5 | 42383.5 | 3.4073 | 24.0992 | 0.01114 | 57.8642 |  |  | CE310 | 12572.9 | 20-Jul | 15 | 23130.2 | 11-Jul | 16 | 16663.8 | 04-Aug | 15 | 37377.4 | 17-Sep | 15
CE320 | 39401.2 |  |  | 10862.1 | 97530.6 | 61680.8 | 35849.8 | 3.4174 | 24.2374 | 0.010025 | 51.3749 |  |  | CE320 | 12990.4 | 20-Jul | 15 | 31510.9 | 24-Apr | 16 | 22783.2 | 02-Oct | 10 | 40101.2 | 02-Oct | 10
CE330 | 40517.6 |  |  | 10862.1 | 104008 | 62978 | 41030.1 | 3.5072 | 24.3005 | 0.0098657 | 50.5144 |  |  | CE330 | 13358.2 | 20-Jul | 15 | 34588.6 | 14-Jun | 14 | 27609.7 | 18-Sep | 16 | 43602.8 | 02-Oct | 9
CE340 | 40108.1 |  |  | 10862.1 | 101274 | 62312.3 | 38961.4 | 3.4628 | 24.3151 | 0.0098887 | 50.5645 |  |  | CE340 | 13176.7 | 20-Jul | 15 | 32733 | 24-Apr | 15 | 24471.4 | 02-Oct | 10 | 41613.2 | 02-Oct | 10
CE350 | 31418.4 |  |  | 10862.1 | 66739.7 | 48329.2 | 18410.5 | 3.2467 | 26.238 | 0.0097768 | 44.5051 |  |  | CE350 | 12008.3 | 20-Jul | 15 | 23460.4 | 20-Jul | 15 | 10627.7 | 10-Jul | 13 | 33102.8 | 20-Jul | 15
CE360 | 54965.7 |  |  | 10862.1 | 162309 | 134626 | 27683.1 | 3.6802 | 25.4584 | 0.0085826 | 41.1929 |  |  | CE360 | 12778.1 | 20-Jul | 15 | 32382.2 | 24-Apr | 16 | 8943.89 | 02-Oct | 10 | 38701.5 | 02-Oct | 11
CE400 | 30806.6 |  |  | 10862.1 | 64232 | 41879.7 | 22352.3 | 3.2205 | 23.1744 | 0.0097582 | 53.6426 |  |  | CE400 | 12008.3 | 20-Jul | 15 | 23460.4 | 20-Jul | 15 | 22710.3 | 17-Jun | 16 | 39126.4 | 25-Oct | 15
CE410 | 30806.6 |  |  | 10862.1 | 64232 | 41879.7 | 22352.3 | 3.2205 | 23.1744 | 0.0097582 | 53.6426 |  |  | CE410 | 12008.3 | 20-Jul | 15 | 23460.4 | 20-Jul | 15 | 22710.3 | 17-Jun | 16 | 39126.4 | 25-Oct | 15
CE420 | 32979.1 |  |  | 10862.1 | 71255.7 | 49340.7 | 21915 | 3.2218 | 23.2471 | 0.0093283 | 51.2369 |  |  | CE420 | 12008.3 | 20-Jul | 15 | 23460.4 | 20-Jul | 15 | 10627.1 | 10-Jul | 13 | 33102.8 | 20-Jul | 15
CE430 | 32145.9 |  |  | 10862.1 | 68494.9 | 46967.3 | 21527.6 | 3.2182 | 23.2048 | 0.0093596 | 51.5407 |  |  | CE430 | 12008.3 | 20-Jul | 15 | 23460.4 | 20-Jul | 15 | 11370 | 24-Oct | 13 | 33102.8 | 20-Jul | 15
CE440 | 33306.7 |  |  | 10862.1 | 72440.2 | 49950.6 | 22489.6 | 3.2275 | 23.3644 | 0.0092081 | 50.1304 |  |  | CE440 | 12008.3 | 20-Jul | 15 | 23460.4 | 20-Jul | 15 | 10627.1 | 10-Jul | 13 | 33102.8 | 20-Jul | 15
CE500 | 23081.6 |  |  | 2631.63 | 65590.5 | 47359.2 | 18231.3 | 3.2074 | 20.4527 | 0.0091211 | 57.6611 |  |  | CE500 | 10435.6 | 20-Jul | 15 | 19788.3 | 20-Jul | 15 | 7905.77 | 29-Jun | 16 | 27650.3 | 29-Jun | 16
CE500 May-Sep | 18035.1 |  |  | 2031.6 | 50356.3 | 36366.4 | 13989.9 | 3.1466 | 25.0003 | 0.010955 | 55.3803 |  |  | CE510 | 11451.2 | 20-Jul | 15 | 22227.9 | 20-Jul | 15 | 9037.8 | 17-Jun | 14 | 31189.2 | 17-Jun | 14
CE510 May-Sep | 35791.5 |  |  | 4065.93 | 112796 | 81316.5 | 31479.4 | 3.5554 | 25.0001 | 0.010975 | 55.4805 |  |  | CE520 | 11261.9 | 20-Jul | 15 | 20009.7 | 20-Jul | 16 | 7783.51 | 29-Jun | 16 | 27726.7 | 29-Jun | 16
CE520 | 25814.2 |  |  | 3140.93 | 66213.2 | 47984.5 | 18228.8 | 2.9203 | 13.6682 | 0.0059977 | 60.6002 |  |  | CE522 | 10899.4 | 20-Jul | 15 | 19894.5 | 20-Jul | 15 | 7847.84 | 29-Jun | 16 | 27693.3 | 29-Jun | 16
CE522 | 24389.1 |  |  | 2879.52 | 65894.6 | 47664.6 | 18230 | 3.0635 | 17.0792 | 0.0074596 | 59.392 |  |  | CE525 | 9585.57 | 20-Jul | 15 | 19590.8 | 20-Jul | 15 | 8001.29 | 29-Jun | 16 | 27558.2 | 29-Jun | 16
CE525 | 20791.2 |  |  | 2194.14 | 65029.4 | 46798.5 | 18230.8 | 3.4968 | 27.1806 | 0.013329 | 53.4435 |  |  | CE530 | 8296.96 | 20-Jul | 15 | 19656.9 | 20-Jul | 15 | 118.546 | 16-Mar | 10 | 19656.9 | 20-Jul | 15
CE530 | 18005.8 |  |  | 2123.87 | 46991.8 | 46991.5 | 0.29966 | 2.9588 | 20.5927 | 0.0064288 | 47.2083 |  |  | CE540 | 9079.35 | 20-Jul | 15 | 19813 | 20-Jul | 15 | 1652.71 | 11-Mar | 10 | 19813 | 20-Jul | 15
CE540 | 20131 |  |  | 2495.13 | 47484.3 | 47475.3 | 8.9734 | 2.6925 | 13.7992 | 0.0043084 | 45.874 |  |  | CE545 | 7768.34 | 20-Jul | 15 | 19538.9 | 20-Jul | 15 | 7.276e-12 | 26-Apr | 16 | 19538.9 | 20-Jul | 15
CE545 | 16610.1 |  |  | 1865.43 | 46636.8 | 46636.8 | 7.0947e-14 | 3.1629 | 27.3198 | 0.0067476 | 38.6413
| * | **
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e CE 3 0 0 | [10 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum* |  | Cases
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2158.8116 |  | 7622.8659 | 5807.1758 | 1815.6901 | 0.0092316 | 3.531 | 17.9875 | 23.9449 | 17.2608 | 0.011202 |  |  | CE300 | 3.9235 | 31-DEC | 23 | 2.7748 | 13-JUN | 16 | 25.0098 | 11-Oct | 16 | 8.7245 | 06-Jan | 6 | 0.013503 | 16-Nov | 17 | 0.0019292 | 11-Jan | 3 | 67.6923 | 16-Nov | 17 | 14.3847 | 06-Nov | 6 | CE300
2 | 2172.7778 |  | 7649.3005 | 5849.9146 | 1799.3859 | 0.0091954 | 3.5205 | 18.1125 | 23.9635 | 17.238 | 0.011296 |  |  | CE310 | 4.1956 | 31-DEC | 23 | 2.8678 | 01-DEC | 14 | 26.5994 | 20-Jul | 16 | 8.7244 | 06-Jan | 6 | 0.015486 | 01-Oct | 8 | 0.0019435 | 05-Jan | 7 | 77.8153 | 02-Oct | 8 | 15.4675 | 06-Nov | 8 | CE310
3 | 2153.5299 |  | 7600.2302 | 5805.9069 | 1794.3233 | 0.0092021 | 3.5292 | 17.9875 | 23.9448 | 17.2372 | 0.011199 |  |  | CE320 | 3.9652 | 31-DEC | 23 | 2.8234 | 31-MAR | 14 | 31.8734 | 20-Jul | 15 | 7.7583 | 06-Jan | 6 | 0.017695 | 01-Oct | 11 | 0.0019351 | 11-Jan | 3 | 82.653 | 18-Sep | 10 | 14.793 | 06-Nov | 6 | CE320
4 | 2115.3848 |  | 7484.5372 | 5740.2671 | 1744.2701 | 0.0091456 | 3.5381 | 17.8 | 23.9168 | 17.1776 | 0.011061 |  |  | CE330 | 4.0954 | 31-DEC | 23 | 2.829 | 31-MAR | 14 | 31.55 | 20-Jul | 15 | 8.7254 | 06-Jan | 6 | 0.017804 | 10-Jul | 12 | 0.0019292 | 11-Jan | 3 | 76.6464 | 22-Sep | 20 | 14.3846 | 06-Nov | 6 | CE330
5 | 2036.9032 |  | 7238.5532 | 5610.6038 | 1627.9494 | 0.0090239 | 3.5537 | 17.425 | 23.8612 | 17.0259 | 0.010484 |  |  | CE340 | 4.015 | 31-DEC | 23 | 2.829 | 31-MAR | 14 | 31.7866 | 20-Jul | 15 | 8.7254 | 06-Jan | 6 | 0.017695 | 10-Jul | 12 | 0.0019292 | 11-Jan | 3 | 80.4986 | 18-Sep | 10 | 14.3846 | 06-Nov | 6 | CE340
6 | 2187.9729 |  | 7586.232 | 6012.3778 | 1573.8542 | 0.0088774 | 3.4672 | 18.575 | 24.0336 | 16.9792 | 0.010648 |  |  | CE350 | 4.3445 | 31-DEC | 23 | 2.7748 | 13-JUN | 16 | 35.004 | 30-May | 5 | 8.7245 | 06-Jan | 6 | 0.01691 | 02-Oct | 1 | 0.0019292 | 11-Jan | 3 | 67.6923 | 16-Nov | 17 | 14.3847 | 06-Nov | 6 | CE350
7 | 2936.1359 |  | 9424.7066 | 7529.5778 | 1895.1288 | 0.0091438 | 3.2099 | 22.9 | 24.6836 | 17.5106 | 0.012288 |  |  | CE360 | 4.431 | 31-DEC | 23 | 2.829 | 31-MAR | 14 | 32.8991 | 10-Jul | 13 | 8.7247 | 06-Jan | 6 | 0.013503 | 16-Nov | 17 | 0.0019292 | 11-Jan | 3 | 67.6921 | 16-Nov | 17 | 14.3846 | 06-Nov | 6 | CE360
8 | 3581.7706 |  | 10852.9883 | 8750.6043 | 2102.3839 | 0.0094511 | 3.0301 | 26.375 | 25.2069 | 17.9249 | 0.011849 |  |  | CE400 | 4.0877 | 31-DEC | 23 | 2.7748 | 13-JUN | 16 | 25.2805 | 16-Jun | 15 | 8.7245 | 06-Jan | 6 | 0.016065 | 02-Apr | 5 | 0.0019292 | 11-Jan | 3 | 89.7515 | 02-Apr | 2 | 16.3281 | 06-Nov | 6 | CE400
9 | 4783.9708 |  | 14320.6146 | 11757.532 | 2563.0826 | 0.0095853 | 2.9935 | 28.2625 | 25.491 | 18.0324 | 0.01158 |  |  | CE410 | 4.0877 | 31-DEC | 23 | 2.7748 | 13-JUN | 16 | 25.2805 | 16-Jun | 15 | 8.7245 | 06-Jan | 6 | 0.016065 | 02-Apr | 5 | 0.0019292 | 11-Jan | 3 | 89.7515 | 02-Apr | 2 | 16.3281 | 06-Nov | 6 | CE410
10 | 5040.7118 |  | 15041.3724 | 11985.1166 | 3056.2558 | 0.0099388 | 2.984 | 28.9 | 25.5874 | 18.4056 | 0.012406 |  |  | CE420 | 3.8494 | 31-DEC | 23 | 2.7748 | 13-JUN | 16 | 25.0098 | 11-Oct | 16 | 8.7245 | 06-Jan | 6 | 0.014713 | 02-Apr | 1 | 0.0019292 | 11-Jan | 3 | 89.6904 | 02-Apr | 1 | 16.3281 | 06-Nov | 6 | CE420
11 | 5497.6583 |  | 16166.4586 | 12475.0244 | 3691.4342 | 0.010352 | 2.9406 | 30.275 | 25.7959 | 18.8977 | 0.013949 |  |  | CE430 | 3.8047 | 31-DEC | 23 | 2.7748 | 13-JUN | 16 | 25.0098 | 11-Oct | 16 | 8.7245 | 06-Jan | 6 | 0.016065 | 02-Apr | 5 | 0.0019292 | 11-Jan | 3 | 89.7516 | 02-Apr | 2 | 16.3281 | 06-Nov | 6 | CE430
12 | 5719.4412 |  | 16775.956 | 12653.6049 | 4122.351 | 0.01066 | 2.9331 | 30.7875 | 25.8724 | 19.1799 | 0.013761 |  |  | CE440 | 3.8047 | 31-DEC | 23 | 2.7748 | 13-JUN | 16 | 25.0098 | 11-Oct | 16 | 8.7245 | 06-Jan | 6 | 0.013503 | 16-Nov | 17 | 0.0019292 | 11-Jan | 3 | 71.2182 | 22-Oct | 2 | 16.3281 | 06-Nov | 6 | CE440
13 | 7242.7351 |  | 21905.3987 | 17367.1031 | 4538.2956 | 0.010086 | 3.0245 | 30.9125 | 25.89 | 18.7418 | 0.011999 |  |  | CE500 | 4.1745 | 02-OCT | 23 | 2.6942 | 01-MAY | 11 | 25.0065 | 01-Apr | 18 | 8.9365 | 21-Dec | 0 | 0.011341 | 20-Jul | 15 | 0.0070081 | 20-Dec | 12 | 100 | 22-Nov | 3 | 53.15 | 30-Apr | 4 | CE500
14 | 7097.0494 |  | 20969.1965 | 17569.37 | 3399.8265 | 0.0096498 | 2.9546 | 31.475 | 25.9791 | 18.3119 | 0.011528 |  |  | CE510 | 4.7069 | 02-OCT | 23 | 2.7894 | 05-JAN | 16 | 25.0119 | 29-Jul | 16 | 8.9365 | 21-Dec | 0 | 0.011356 | 20-Jul | 15 | 0.0070081 | 20-Dec | 12 | 100 | 22-Nov | 3 | 53.2331 | 04-May | 4 | CE510
15 | 8703.2518 |  | 26478.5567 | 22450.3965 | 4028.1603 | 0.0094732 | 3.0424 | 32.0125 | 26.0608 | 18.2778 | 0.012086 |  |  | CE520 | 3.8381 | 02-OCT | 23 | 2.4617 | 01-MAY | 11 | 15.286 | 20-Jul | 16 | 8.8335 | 21-Dec | 0 | 0.0070875 | 20-Jul | 16 | 0.0064297 | 10-Nov | 5 | 92.4609 | 20-Dec | 11 | 60.8073 | 28-Nov | 0 | CE520
16 | 8855.9558 |  | 26987.6781 | 22526.3936 | 4461.2845 | 0.0095739 | 3.0474 | 32.2 | 26.0905 | 18.4491 | 0.013492 |  |  | CE522 | 4.0071 | 02-OCT | 23 | 2.5774 | 01-MAY | 11 | 20.0055 | 06-Apr | 19 | 8.8955 | 21-Dec | 0 | 0.0089495 | 20-Jul | 15 | 0.006988 | 20-Dec | 12 | 100 | 16-Dec | 5 | 57.5773 | 30-Apr | 4 | CE522
17 | 5804.0265 |  | 16564.4348 | 13054.3458 | 3510.0889 | 0.010315 | 2.854 | 31.8875 | 26.0423 | 18.9278 | 0.014504 |  |  | CE525 | 4.548 | 02-OCT | 23 | 2.9321 | 01-MAY | 11 | 35.0003 | 14-Jul | 18 | 9.0129 | 21-Dec | 0 | 0.017771 | 20-Jul | 15 | 0.0070456 | 20-Dec | 12 | 100 | 13-Nov | 2 | 45.8033 | 05-Oct | 2 | CE525
18 | 5964.1384 |  | 17440.5686 | 12853.2483 | 4587.3203 | 0.010882 | 2.9242 | 31.325 | 25.9556 | 19.4457 | 0.015288 |  |  | CE530 | 3.8229 | 02-OCT | 23 | 2.4932 | 01-MAY | 11 | 25.0075 | 05-Apr | 19 | 8.9353 | 21-Dec | 0 | 0.0063992 | 12-Apr | 19 | 0.0063743 | 17-Oct | 10 | 91.0266 | 20-Dec | 11 | 32.2082 | 18-Apr | 19 | CE530
19 | 5626.7777 |  | 17110.3595 | 12150.2245 | 4960.135 | 0.011035 | 3.0409 | 29.35 | 25.6565 | 19.4839 | 0.01493 |  |  | CE540 | 3.4684 | 02-OCT | 23 | 2.2786 | 01-MAY | 11 | 15.0072 | 19-Apr | 23 | 8.8312 | 21-Dec | 0 | 0.0037752 | 13-Oct | 3 | 0.0037714 | 17-Oct | 10 | 54.4724 | 20-Dec | 11 | 35.4808 | 28-Sep | 18 | CE540
20 | 5325.0779 |  | 16772.6619 | 11538.0162 | 5234.6457 | 0.011089 | 3.1497 | 27.6125 | 25.3949 | 19.5144 | 0.01597 |  |  | CE545 | 4.1194 | 02-OCT | 23 | 2.6584 | 01-MAY | 11 | 35.0003 | 14-Jul | 18 | 9.0112 | 21-Dec | 0 | 0.00679 | 31-Dec | 9 | 0.00679 | 01-Apr | 1 | 96.3941 | 20-Dec | 11 | 19.2458 | 18-Apr | 17 | CE545
21 | 4378.162 |  | 13638.9608 | 9051.7607 | 4587.2001 | 0.01132 | 3.1152 | 27.2 | 25.3328 | 19.7633 | 0.01681 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 4332.3646 |  | 13589.0288 | 8940.5195 | 4648.5093 | 0.011371 | 3.1366 | 26.8875 | 25.2855 | 19.7984 | 0.016771
23 | 4224.3277 |  | 13392.3113 | 8741.5976 | 4650.7137 | 0.011389 | 3.1703 | 26.325 | 25.2004 | 19.7897 | 0.016784
24 | 4202.6476 |  | 13398.2802 | 8662.1586 | 4736.1216 | 0.011445 | 3.1881 | 26.1 | 25.1665 | 19.8376 | 0.017077
| * | **
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 4020.64 |  |  | 518.124 | 13654.8 | 9850.99 | 3803.78 | 0.010601 | 3.8986 | 16.8146 | 25.0003
June 25 | 5245.59 |  |  | 566.826 | 13734 | 9923.88 | 3810.08 | 0.011099 | 2.9169 | 29.5167 | 18.8666
|  | * | **
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3134.34 |  |  | 416.337 | 9780.15 | 9780.15 | -1.2316e-13 | 0.0063966 | 3.5983 | 16.8146 | 25.0003
June 25 | 4093.44 |  |  | 458.652 | 9843.74 | 9843.74 | 5.0212e-13 | 0.0063966 | 2.6963 | 29.5167 | 14.8958
|  | * | **
* | EnergyPlus compressor values includes the condenser fan
** | EnergyPlus can't calculate isolated condenser fan values

## Title Page
ASHRAE Standard 140-2020 | To print example results:
Informative Annex B16, Section B16.5.2 | 1. Select results type in cell B21:
"Example" for Standard 140 Annex B16.5.2 Example Results;
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545 | "Title Page" thru "Figure List"
"Table-Q" thru "Table-T"
"Fig B16.5.2-1 Qtot" thru "Fig B16.5.2-52 HrOHR"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Scratch area for Table subtitle 1
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
Scratch area for Table subtitle 2
Scratch area for chart subtitles
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2 Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545

## Program List
ASHRAE Standard 140-2020
Participating Organizations and Computer Programs for
Quasi-analytical Solutions and Example Simulation Results
Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
The quasi-analytical solutions and programs used to generate the example simulation results are described in
Table B17-2. The first column of Table B17-2 ("Model"), indicates the proper program name and version
number, or indicates a quasi-analytical solution.
The second column ("Authoring Organization") indicates the national research facility, university, or industry
organization with expertise in building science that wrote the simulation software or did the quasi-analytical solutions.
The third column ("Implemented By") indicates the national research facility, university, or industry
organization with expertise in building science that performed the simulations or did the quasi-analytical solutions.
The entries in the fourth column are the abbreviations for the simulations and quasi-analytical solutions
generally used in the tables and charts which follow.
See Standard 140, Annex B17 for further details.
TABLE B17-2
Participating Organizations and Computer Programs
Model | Authoring Organization | Implemented By | Abbreviation
CODYRUN/LGIMAT | Université de la Reunion Island, France | Université de la Reunion Island, France | CODYRUN/UR
DOE-2.1E version 120 (ESTSC release) | LANL/LBNL/ESTSC/JJH,a,b,c,d United States | NREL/JNA,e United States | DOE-2.1E-E/NREL DOE21E-E
DOE-2.2 NT42j | LBNL/JJH,b,d United States | NREL/JNA,e United States | DOE-2.2/NREL
EnergyPlus 1.1.0.020 | LBNL/UIUC/CERL/OSU/GARD Analytics/FSEC/DOE-BT,b,f,g,h,i,j United States | GARD Analytics, United States | EnergyPlus/GARD
HOT3000/ESP-r | CETC/ESRU,k,l Canada/United Kingdom | CETC,k Canada | HOT3000/NRCan
TRNSYS 14.2-TUD with real controller model | University of Wisconsin, USA; Technische Universität Dresden, Germany | Technische Universität Dresden, Germany | TRNSYS/TUD
aLANL: Los Alamos National Laboratory, United States
bLBNL: Lawrence Berkeley National Laboratory, United States
cESTSC: Energy Science and Technology Software Center (at Oak Ridge National Laboratory), United States
dJJH: James J. Hirsch & Associates, United States
eNREL/JNA: National Renewable Energy Laboratory/J. Neymark & Associates, United States
fUIUC: University of Illinois Urbana/Champaign, United States
gCERL: U.S. Army Corps of Engineers, Construction Engineering Research Laboratories, United States
hOSU: Oklahoma State University, United States
iFSEC: University of Central Florida, Florida Solar Energy Center, United States
jDOE-BT: U.S. Department of Energy, Office of Building Technologies, Energy Efficiency and Renewable Energy,
United States
kCETC:CANMET Energy Technology Centre, Natural Resources Canada, Canada
lESRU: Energy Systems Research Unit, University of Strathclyde, Scotland, United Kingdom

## Tables List
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B16.5.2-1 | Annual Space Cooling Electricity Consumption (Total, Compressor) | Table-Q | A7 – O56
| B16.5.2-2 | Annual Space Cooling Electricity Consumption (Supply Fan, Condenser Fan) |  | A57 – O106
| B16.5.2-3 | Weather Data Checks, CE300 Only |  | A109 – O119
| B16.5.2-4 | Annual Space Cooling Coil Loads (Total, Sensible) |  | A120 – O169
| B16.5.2-5 | Annual Space Cooling Coil Loads (Latent) |  | A170 – O195
| B16.5.2-6 | Various Annual Means (COP2, IDB) |  | A196 – O245
| B16.5.2-7 | Various Annual Means (Humidity Ratio, Relative Humidity) |  | A246 – O295
| B16.5.2-8 | f(ODB) Sensitivities, CE500 and CE530, April 30 and June 25 (Energy, Coil Loads) |  | A296 – O349
| B16.5.2-9 | f(ODB) Sensitivities, CE500 and CE530, April 30 and June 25 (COP2, Zone Conditions) |  | A350 – O382
| B16.5.2-10 | Hourly Integrated Maxima (Total Cooling System Energy Consumption and Total Coil Load) | Table R | A7 – AB54
| B16.5.2-11 | Hourly Integrated Maxima (Sensible Coil Load and Latent Coil Load) |  | A55 – AB102
| B16.5.2-12 | Hourly Integrated Maxima and Minima (COP2) |  | A103 – AB150
| B16.5.2-13 | Hourly Integrated Maxima and Minima (IDB) |  | A151 – AB198
| B16.5.2-14 | Hourly Integrated Maxima and Minima (Zone Humidity Ratio) |  | A199 – AB246
| B16.5.2-15 | Hourly Integrated Maxima and Minima (Relative Humidity) |  | A247 – AB295
| B16.5.2-16 | June 28 Hourly Output—Case CE300 | Table-S | A7 – M215
|  | TRNSYS-TUD |  | A7 – M35
|  | DOE-2.2 |  | A39 – M65
|  | DOE-2.1E-E |  | A69 – M95
|  | ENERGYPLUS |  | A99 – M125
|  | CODYRUN |  | A129 – M155
|  | HOT3000 |  | A159 – M185
|  | Tested Program |  | A189 – M215
| B16.5.2-17 | Delta Annual Space Cooling Electricity Consumptions (Total, Compressor) | Table-T | A7 – O50
| B16.5.2-18 | Delta Annual Space Cooling Electricity Consumptions (Fans) |  | A52 – O95
| B16.5.2-19 | Delta Annual Cooling Coil Loads |  | A100 – O143
| B16.5.2-20 | Delta Various Annual Means (COP2, IDB) |  | A146 – O189
| B16.5.2-21 | Delta Various Annual Means (Zone Humidity, Relative Humidity) |  | A192 – O235
| B16.5.2-22 | Delta Hourly Integrated Maximum Total Consumptions |  | A243 – O265
| B16.5.2-23 | Delta Hourly Integrated Maximum Coil Loads (Total, Sensible) |  | A267 – O310
| B16.5.2-24 | Delta Hourly Integrated Maximum Coil Loads (Latent) |  | A311 – O333
| B16.5.2-25 | Delta Hourly Integrated Maximum and Minimum COP2 |  | A336 – O379
| B16.5.2-26 | Delta Hourly Integrated Maximum and Minimum IDB |  | A381 – O424
| B16.5.2-27 | Delta Hourly Integrated Maximum and Minimum Zone Humidity Ratio |  | A426 – O469
| B16.5.2-28 | Delta Hourly Integrated Maximum and Minimum Zone Relative Humidity |  | A471 – O514

## Figures List
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
List of Figures
| Figure | Title | Sheet Tab
| B16.5.2-1 | HVAC BESTEST: CE300 - CE545 Annual Total Electricity Consumption | Fig B16.5.2-1 Qtot
| B16.5.2-2 | HVAC BESTEST: CE300 - CE545 Annual Total Space Cooling Electricity Consumption Sensitivities | Fig B16.5.2-2 dQtot
| B16.5.2-3 | HVAC BESTEST: CE300 - CE545 Peak Hour Total Electricity Consumption | Fig B16.5.2-3 Ptot
| B16.5.2-4 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Total Space Cooling Consumption Sensitivities | Fig B16.5.2-4 dPtot
| B16.5.2-5 | HVAC BESTEST: CE300 - CE545 Annual Compressor Electricity Consumption | Fig B16.5.2-5 Qcomp
| B16.5.2-6 | HVAC BESTEST: CE300 - CE545 Annual Compressor Electricity Consumption Sensitivities | Fig B16.5.2-6 dQcomp
| B16.5.2-7 | HVAC BESTEST: CE300 - CE545 Annual Indoor (Supply) Fan Electricity Consumption | Fig B16.5.2-7 Qidfan
| B16.5.2-8 | HVAC BESTEST: CE300 - CE545 Annual Indoor (Supply) Fan Electricity Consumption Sensitivities | Fig B16.5.2-8 dQidfan
| B16.5.2-9 | HVAC BESTEST: CE300 - CE545 Annual Outdoor (Condenser) Fan Electricity Consumption | Fig B16.5.2-9 Qodfan
| B16.5.2-10 | HVAC BESTEST: CE300 - CE545 Annual Outdoor (Condenser) Fan Electricity Consumption Sensitivities | Fig B16.5.2-10 dQodfan
| B16.5.2-11 | HVAC BESTEST: CE300 - CE545 Annual Total Coil Load | Fig B16.5.2-11 QCtot
| B16.5.2-12 | HVAC BESTEST: CE300 - CE545 Peak Hour Total Coil Load | Fig B16.5.2-12 PCtot
| B16.5.2-13 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Total Coil Load Sensitivities | Fig B16.5.2-13 dPCtot
| B16.5.2-14 | HVAC BESTEST: CE300 - CE545 Annual Sensible Coil Load | Fig B16.5.2-14 QCSens
| B16.5.2-15 | HVAC BESTEST: CE300 - CE545 Annual Sensible Cooling Load Sensitivities | Fig B16.5.2-15 dQCsens
| B16.5.2-16 | HVAC BESTEST: CE300 - CE545 Peak Hour Sensible Coil Load | Fig B16.5.2-16 PCSens
| B16.5.2-17 | HVAC BESTEST: CE300 - CE545 Annual Latent Coil Load | Fig B16.5.2-17 QClat
| B16.5.2-18 | HVAC BESTEST: CE300 - CE545 Annual Latent Cooling Load Sensitivities | Fig B16.5.2-18 dQClat
| B16.5.2-19 | HVAC BESTEST: CE300 - CE545 Peak Hour Latent Coil Load | Fig B16.5.2-19 PClat
| B16.5.2-20 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Latent Coil Load Sensitivities | Fig B16.5.2-20 dPClat
| B16.5.2-21 | HVAC BESTEST: CE300 - CE545 Annual Mean COP2 | Fig B16.5.2-21 COP2
| B16.5.2-22 | HVAC BESTEST: CE300 - CE545 Annual Mean COP2 Sensitivities | Fig B16.5.2-22 dCOP2
| B16.5.2-23 | HVAC BESTEST: CE300 - CE545 Hourly Maximum COP2 | Fig B16.5.2-23 MxCOP2
| B16.5.2-24 | HVAC BESTEST: CE300 - CE545 Hourly Maximum COP2 Sensitivities | Fig B16.5.2-24 dMxCOP2
| B16.5.2-25 | HVAC BESTEST: CE300 - CE545 Hourly Minimum COP2 | Fig B16.5.2-25 MnCOP2
| B16.5.2-26 | HVAC BESTEST: CE300 - CE545 Hourly Minimum COP2 Sensitivities | Fig B16.5.2-26 dMnCOP2
| B16.5.2-27 | HVAC BESTEST: CE300 - CE545 Annual Mean Indoor Dry-Bulb Temperature | Fig B16.5.2-27 IDB
| B16.5.2-28 | HVAC BESTEST: CE300 - CE545 Annual Mean IDB Sensitivities | Fig B16.5.2-28 dIDB
| B16.5.2-29 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Indoor Dry-Bulb Temperature | Fig B16.5.2-29 MxIDB
| B16.5.2-30 | HVAC BESTEST: CE300 - CE545 Hourly Maximum IDB Sensitivities | Fig B16.5.2-30 dMxIDB
| B16.5.2-31 | HVAC BESTEST: CE300 - CE545 Hourly Minimum Indoor Dry-Bulb Temperature | Fig B16.5.2-31 MnIDB
| B16.5.2-32 | HVAC BESTEST: CE300 - CE545 Annual Mean Zone Humidity Ratio | Fig B16.5.2-32 Humrat
| B16.5.2-33 | HVAC BESTEST: CE300 - CE545 Annual Mean Humidity Ratio Sensitivities | Fig B16.5.2-33 dHumrat
| B16.5.2-34 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Zone Humidity Ratio | Fig B16.5.2-34 MxHum
| B16.5.2-35 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Humidity Ratio Sensitivities | Fig B16.5.2-35 dMxHumrat
| B16.5.2-36 | HVAC BESTEST: CE300 - CE545 Hourly Minimum Zone Humidity Ratio | Fig B16.5.2-36 MnHum
| B16.5.2-37 | HVAC BESTEST: CE300 - CE545 Annual Mean Relative Humidity | Fig B16.5.2-37 RelHum
| B16.5.2-38 | HVAC BESTEST: CE300 - CE545 Annual Mean Relative Humidity Sensitivities | Fig B16.5.2-38 dRelHum
| B16.5.2-39 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Zone Relative Humidity | Fig B16.5.2-39 MxRelHum
| B16.5.2-40 | HVAC BESTEST: CE300 - CE545 Hourly Maximum Relative Humidity Sensitivities | Fig B16.5.2-40 dMxRelHum
| B16.5.2-41 | HVAC BESTEST: CE300 - CE545 Hourly Minimum Zone Relative Humidity | Fig B16.5.2-41 MnRelHum
| B16.5.2-42 | HVAC BESTEST: f(ODB) for CE500, CE530 Specific Day Electricity Consumptions | Fig B16.5.2-42 Qf(ODB)
| B16.5.2-43 | HVAC BESTEST: f(ODB) for CE500, CE530 Specific Day Coil Loads | Fig B16.5.2-43 QCf(ODB)
| B16.5.2-44 | HVAC BESTEST: f(ODB) for CE500, CE530 Specific Day COP2 | Fig B16.5.2-44 COP2f(ODB)
| B16.5.2-45 | HVAC BESTEST: f(ODB) for CE500, CE530 Specific Day Humidity Ratio | Fig B16.5.2-45 Humratf(ODB)
| B16.5.2-46 | HVAC BESTEST: CE300 June 28 Hourly Electricity Consumption | Fig B16.5.2-46 HrQ
| B16.5.2-47 | HVAC BESTEST: CE300 June 28 Hourly Coil Loads | Fig B16.5.2-47 HrQC
| B16.5.2-48 | HVAC BESTEST: CE300 June 28 Hourly COP2 | Fig B16.5.2-48 HrCOP2
| B16.5.2-49 | HVAC BESTEST: CE300 June 28 Hourly Zone Humidity Ratio | Fig B16.5.2-49 HrHum
| B16.5.2-50 | HVAC BESTEST: CE300 June 28 Hourly EDB & EWB | Fig B16.5.2-50 HrEDB,EWB
| B16.5.2-51 | HVAC BESTEST: CE300 June 28 Hourly ODB | Fig B16.5.2-51 HrODB
| B16.5.2-52 | HVAC BESTEST: CE300 June 28 Hourly OHR | Fig B16.5.2-52 HrOHR

## Table-Q
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.2-1. Annual Space Cooling Electricity Consumption (Total, Compressor)
Energy Consumption, Total (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 35633.7773 | 34750 | 34755 | 34745.6375 | 34976.411 | 35070 | 34745.6375 | 35633.7773 | 34988.471 | 2.538%
CE310 | 39973.3798 | 39379 | 39384 | 39290.3641 | 39519.569 | 39608 | 39290.3641 | 39973.3798 | 39525.7188 | 1.728%
CE320 | 40059.657 | 38745 | 38792 | 39079.1002 | 39400.815 | 39457 | 38745 | 40059.657 | 39255.5954 | 3.349%
CE330 | 40963.3004 | 39708 | 39438 | 40143.3736 | 40535.137 | 40330 | 39438 | 40963.3004 | 40186.3018 | 3.796%
CE340 | 40619.2951 | 39358 | 39265 | 39783.0185 | 40065.261 | 39947 | 39265 | 40619.2951 | 39839.5958 | 3.399%
CE350 | 32236.9795 | 30547 | 30548 | 31145.1136 | 31586.592 | 31742 | 30547 | 32236.9795 | 31300.9475 | 5.399%
CE360 | 55298.7917 | 54064 | 54016 | 54704.711 | 54843.258 | 55068 | 54016 | 55298.7917 | 54665.7934 | 2.347%
CE400 | 32045.1536 | 30846 | 30876 | 31012.681 |  | 31413 | 30846 | 32045.1536 | 31238.5669 | 3.839%
CE410 | 32078.4319 | 31668 | 31699 |  |  | 31503 | 31503 | 32078.4319 | 31737.108 | 1.813%
CE420 | 33387.0076 | 32530 | 32910 | 32735.5046 |  | 33208 | 32530 | 33387.0076 | 32954.1024 | 2.601%
CE430 | 32538.0313 | 31932 | 31811 | 31772.397 |  | 31818 | 31772.397 | 32538.0313 | 31974.2857 | 2.395%
CE440 | 33691.321 | 33032 | 32973 | 33031.6453 |  | 33248 | 32973 | 33691.321 | 33195.1933 | 2.164%
CE500 | 22337.887 | 22817 | 22822 | 23034.6081 | 22322.953 | 23138 | 22322.953 | 23138 | 22745.408 | 3.583%
CE500 May-Sep | 17390.8511 | 17872 | 17870 | 17996.1112 | 17434.537 | 18051 | 17390.8511 | 18051 | 17769.0832 | 3.715%
CE510 May-Sep | 34608.7754 | 35971 | 35970 | 35732.4838 | 34848.637 | 35845 | 34608.7754 | 35971 | 35495.9827 | 3.838%
CE520 | 24986.582 | 25389 | 25390 | 25017.1776 | 25131.07 | 25781 | 24986.582 | 25781 | 25282.4716 | 3.142%
CE522 | 23544.1607 | 24293 | 24307 | 24077.7247 | 23619.744 | 24360 | 23544.1607 | 24360 | 24033.6049 | 3.395%
CE525 | 20320.874 | 20408 | 20421 | 20701.5603 | 20241.713 | 21323 | 20241.713 | 21323 | 20569.3579 | 5.257%
CE530 | 17281.271 | 17540 | 17537 | 17741.9432 | 17442.468 | 17875 | 17281.271 | 17875 | 17569.6137 | 3.379%
CE540 | 19430.3785 | 19878 | 19874 | 19061.1125 | 19536.572 | 20164 | 19061.1125 | 20164 | 19657.3438 | 5.611%
CE545 | 15687.0796 | 15802 | 15791 | 16635.7259 | 15791.081 | 16339 | 15687.0796 | 16635.7259 | 16007.6477 | 5.926%
Energy Consumption, Compressor (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 22353.5343 | 21569 | 21573 |  | 21770.001 | 21876 | 21569 | 22353.5343 | 21828.3071 | 3.594%
CE310 | 26339.6254 | 25813 | 25817 |  | 25936.821 | 26053 | 25813 | 26339.6254 | 25991.8893 | 2.026%
CE320 | 26433.1374 | 25250 | 25294 |  | 25846.026 | 25912 | 25250 | 26433.1374 | 25747.0327 | 4.595%
CE330 | 27299.7321 | 26172 | 25925 |  | 26927.733 | 26775 | 25925 | 27299.7321 | 26619.893 | 5.164%
CE340 | 26962.9373 | 25829 | 25745 |  | 26472.79 | 26400 | 25745 | 26962.9373 | 26281.9455 | 4.634%
CE350 | 19316.8404 | 17802 | 17801 |  | 18738.055 | 18891 | 17801 | 19316.8404 | 18509.7791 | 8.189%
CE360 | 40105.8399 | 38999 | 38955 |  | 39697.162 | 39941 | 38955 | 40105.8399 | 39539.6004 | 2.911%
CE400 | 19178.9487 | 18106 | 18131 |  |  | 18629 | 18106 | 19178.9487 | 18511.2372 | 5.796%
CE410 | 19204.4944 | 18823 | 18850 |  |  | 18685 | 18685 | 19204.4944 | 18890.6236 | 2.75%
CE420 | 20358.5854 | 19596 | 19934 |  |  | 20214 | 19596 | 20358.5854 | 20025.6463 | 3.808%
CE430 | 19598.6211 | 19059 | 18951 |  |  | 18966 | 18951 | 19598.6211 | 19143.6553 | 3.383%
CE440 | 20629.1333 | 20042 | 19989 |  |  | 20249 | 19989 | 20629.1333 | 20227.2833 | 3.165%
CE500 | 17854.2956 | 18473 | 18478 |  | 17857.852 | 18522 | 17854.2956 | 18522 | 18237.0295 | 3.661%
CE500 May-Sep | 13942.1479 | 14508 | 14506 |  | 13988.512 | 14491 | 13942.1479 | 14508 | 14287.132 | 3.961%
CE510 May-Sep | 27747.879 | 28811 | 28810 |  | 27901.957 | 28721 | 27747.879 | 28811 | 28398.3672 | 3.744%
CE520 | 19521.2767 | 20121 | 20126 |  | 19654.972 | 20185 | 19521.2767 | 20185 | 19921.6497 | 3.332%
CE522 | 18620.3108 | 19407 | 19418 |  | 18689.799 | 19281 | 18620.3108 | 19418 | 19083.222 | 4.18%
CE525 | 16557.8748 | 16880 | 16893 |  | 16506.802 | 17443 | 16506.802 | 17443 | 16856.1354 | 5.554%
CE530 | 13656.9951 | 14127 | 14124 |  | 13855.928 | 14172 | 13656.9951 | 14172 | 13987.1846 | 3.682%
CE540 | 15020.7433 | 15680 | 15677 |  | 15163.82 | 15664 | 15020.7433 | 15680 | 15441.1127 | 4.269%
CE545 | 12621.8685 | 12967 | 12957 |  | 12750.623 | 13215 | 12621.8685 | 13215 | 12902.2983 | 4.597%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-2. Annual Space Cooling Electricity Consumption (Supply Fan, Condenser Fan)
Energy Consumption, Supply Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 10876.9887 | 0.1646%
CE310 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 10876.9887 | 0.1646%
CE320 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 10876.9887 | 0.1646%
CE330 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 10876.9887 | 0.1646%
CE340 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 10876.9887 | 0.1646%
CE350 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 10876.9887 | 0.1646%
CE360 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 10876.9887 | 0.1646%
CE400 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 10876.4024 | 0.1647%
CE410 | 10879.92 | 10880 | 10880 |  |  | 10880 | 10879.92 | 10880 | 10879.98 | 0.0007353%
CE420 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 10876.4024 | 0.1647%
CE430 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 10876.4024 | 0.1647%
CE440 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 10876.4024 | 0.1647%
CE500 | 2563.8216 | 2369 | 2369 | 2628.3265 | 2553.232 | 2639 | 2369 | 2639 | 2520.3967 | 10.71%
CE500 May-Sep | 1972.0485 | 1837 | 1837 | 2028.9634 | 1970.497 | 2035 | 1837 | 2035 | 1946.7515 | 10.17%
CE510 May-Sep | 3923.2198 | 4099 | 4099 | 4063.3025 | 3972.28 | 4073 | 3923.2198 | 4099 | 4038.3004 | 4.353%
CE520 | 3125.1884 | 2874 | 2871 | 3018.6693 | 3131.271 | 3200 | 2871 | 3200 | 3036.6881 | 10.83%
CE522 | 2815.5716 | 2704 | 2707 | 2842.5564 | 2819.112 | 2904 | 2704 | 2904 | 2798.7067 | 7.146%
CE525 | 2151.7702 | 1886 | 1885 | 2179.8959 | 2135.708 | 2221 | 1885 | 2221 | 2076.5624 | 16.18%
CE530 | 2072.4451 | 1833 | 1833 | 2090.2174 | 2050.856 | 2117 | 1833 | 2117 | 1999.4197 | 14.2%
CE540 | 2521.5317 | 2258 | 2258 | 2309.2457 | 2500.416 | 2573 | 2258 | 2573 | 2403.3656 | 13.11%
CE545 | 1752.7588 | 1501 | 1501 | 1870.9023 | 1738.667 | 1786 | 1501 | 1870.9023 | 1691.7214 | 21.87%
Energy Consumption, Condenser Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 2400.3229 | 2301 | 2302 |  | 2326.49 | 2323 | 2301 | 2400.3229 | 2330.5626 | 4.262%
CE310 | 2753.8345 | 2686 | 2687 |  | 2702.828 | 2691 | 2686 | 2753.8345 | 2704.1325 | 2.509%
CE320 | 2746.5996 | 2615 | 2618 |  | 2674.869 | 2681 | 2615 | 2746.5996 | 2667.0937 | 4.934%
CE330 | 2783.6483 | 2656 | 2633 |  | 2727.484 | 2693 | 2633 | 2783.6483 | 2698.6265 | 5.582%
CE340 | 2776.4378 | 2649 | 2640 |  | 2712.551 | 2684 | 2640 | 2776.4378 | 2692.3978 | 5.068%
CE350 | 2040.2191 | 1865 | 1867 |  | 1968.617 | 1970 | 1865 | 2040.2191 | 1942.1672 | 9.022%
CE360 | 4313.0318 | 4185 | 4181 |  | 4266.176 | 4272 | 4181 | 4313.0318 | 4243.4416 | 3.111%
CE400 | 1986.2848 | 1860 | 1865 |  |  | 1902 | 1860 | 1986.2848 | 1903.3212 | 6.635%
CE410 | 1994.0175 | 1965 | 1969 |  |  | 1936 | 1936 | 1994.0175 | 1966.0044 | 2.951%
CE420 | 2148.5022 | 2054 | 2096 |  |  | 2115 | 2054 | 2148.5022 | 2103.3756 | 4.493%
CE430 | 2059.4903 | 1993 | 1980 |  |  | 1970 | 1970 | 2059.4903 | 2000.6226 | 4.473%
CE440 | 2182.2678 | 2110 | 2104 |  |  | 2120 | 2104 | 2182.2678 | 2129.0669 | 3.676%
CE500 | 1919.7698 | 1975 | 1975 |  | 1911.869 | 1976 | 1911.869 | 1976 | 1951.5278 | 3.286%
CE500 May-Sep | 1476.6547 | 1527 | 1527 |  | 1475.528 | 1524 | 1475.528 | 1527 | 1506.0365 | 3.418%
CE510 May-Sep | 2937.6766 | 3061 | 3061 |  | 2974.4 | 3050 | 2937.6766 | 3061 | 3016.8153 | 4.088%
CE520 | 2340.1169 | 2394 | 2393 |  | 2344.827 | 2396 | 2340.1169 | 2396 | 2373.5888 | 2.354%
CE522 | 2108.2783 | 2182 | 2182 |  | 2110.833 | 2174 | 2108.2783 | 2182 | 2151.4223 | 3.427%
CE525 | 1611.2289 | 1642 | 1643 |  | 1599.203 | 1663 | 1599.203 | 1663 | 1631.6864 | 3.91%
CE530 | 1551.8309 | 1580 | 1580 |  | 1535.684 | 1585 | 1535.684 | 1585 | 1566.503 | 3.148%
CE540 | 1888.1035 | 1940 | 1939 |  | 1872.336 | 1926 | 1872.336 | 1940 | 1913.0879 | 3.537%
CE545 | 1312.4522 | 1334 | 1333 |  | 1301.791 | 1337 | 1301.791 | 1337 | 1323.6486 | 2.66%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-3. Weather Data Checks, CE300 Only
Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Variable | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
Annual Mean Output
ODB (°C) | 19.9145 | 19.8889 | 19.8889 | 19.9141 | 19.9145 | 19.91 | 19.8889 | 19.9145 | 19.9051 | 0.1284%
OHR (kg/kg) | 0.011643 | 0.0116 | 0.0116 | 0.011593 | 0.011649 | 0.0116 | 0.011593 | 0.011649 | 0.011614 | 0.4762%
Annual Hourly Integrated Maxima
ODB (°C) | 34.7 | 35 | 35 | 34.775 | 35 | 35 | 34.7 | 35 | 34.9125 | 0.8593%
OHR (kg/kg) | 0.021878 | 0.0225 | 0.0225 | 0.021842 | 0.022406 | 0.0223 | 0.021842 | 0.0225 | 0.022238 | 2.96%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-4. Annual Space Cooling Coil Loads ( Total, Sensible )
Total Sensible + Latent (kWh,thermal) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 80426.8675 | 77283.4356 | 77291.9355 | 77317.9497 | 77744.589 | 78257 | 77283.4356 | 80426.8675 | 78053.6295 | 4.027%
CE310 | 99342.1316 | 97394.7852 | 97412.0781 | 96447.5904 | 97295.866 | 97261 | 96447.5904 | 99342.1316 | 97525.5752 | 2.968%
CE320 | 99791.678 | 96356.3319 | 96493.2096 | 96083.5597 | 97141.307 | 96957 | 96083.5597 | 99791.678 | 97137.181 | 3.817%
CE330 | 105012.8715 | 100729.9701 | 100993.467 | 102211.3604 | 103712.915 | 102008 | 100729.9701 | 105012.8715 | 102444.764 | 4.181%
CE340 | 102727.9789 | 99027.6453 | 99223.143 | 99708.5156 | 100676.21 | 99753 | 99027.6453 | 102727.9789 | 100186.0821 | 3.693%
CE350 | 69387.9976 | 63736.3536 | 63634.6479 | 65790.3681 | 66860.163 | 67389 | 63634.6479 | 69387.9976 | 66133.0884 | 8.7%
CE360 | 162974.0626 | 159807.2061 | 159853.809 | 161248.445 | 161200.179 | 162168 | 159807.2061 | 162974.0626 | 161208.6169 | 1.964%
CE400 | 68792.8221 | 64917.5466 | 65025.1143 | 65413.8414 |  | 66898 | 64917.5466 | 68792.8221 | 66209.4649 | 5.853%
CE410 | 68672.8538 | 66779.6109 | 66843.5067 |  |  | 66175 | 66175 | 68672.8538 | 67117.7429 | 3.722%
CE420 | 72609.3074 | 69610.9569 | 70882.1316 | 70349.4668 |  | 71803 | 69610.9569 | 72609.3074 | 71050.9725 | 4.22%
CE430 | 69756.312 | 67640.7387 | 67219.2609 | 67141.3524 |  | 67200 | 67141.3524 | 69756.312 | 67791.5328 | 3.857%
CE440 | 73711.3635 | 71380.1085 | 71181.0936 | 71417.307 |  | 72029 | 71181.0936 | 73711.3635 | 71943.7745 | 3.517%
CE500 | 63357.1063 | 65995.8615 | 65992.3443 | 65571.1832 | 63105.366 | 65614 | 63105.366 | 65995.8615 | 64939.3102 | 4.451%
CE500 May-Sep | 48443.4308 | 50692.8174 | 50690.4726 | 50354.2901 | 48439.57 | 50357 | 48439.57 | 50692.8174 | 49829.5968 | 4.522%
CE510 May-Sep | 108974.3099 | 114017.9517 | 114015.3138 | 112792.6463 | 108979.013 | 112781 | 108974.3099 | 114017.9517 | 111926.7058 | 4.506%
CE520 | 63421.5444 | 66571.2168 | 66565.3548 | 66087.7865 | 63212.102 | 66146 | 63212.102 | 66571.2168 | 65334.0008 | 5.141%
CE522 | 63389.2228 | 66373.0812 | 66371.9088 | 65850.6755 | 63157.03 | 65900 | 63157.03 | 66373.0812 | 65173.653 | 4.935%
CE525 | 63292.9454 | 65399.1099 | 65395.0065 | 64973.3114 | 63001.558 | 65155 | 63001.558 | 65399.1099 | 64536.1552 | 3.715%
CE530 | 45045.848 | 46634.2617 | 46630.7445 | 46944.3571 | 44875.414 | 47002 | 44875.414 | 47002 | 46188.7709 | 4.604%
CE540 | 45112.827 | 47129.8938 | 47126.0835 | 47296.6053 | 44979.842 | 47462 | 44979.842 | 47462 | 46517.8753 | 5.336%
CE545 | 44981.3517 | 46239.7491 | 46235.9388 | 46611.8912 | 44775.11 | 46668 | 44775.11 | 46668 | 45918.6735 | 4.122%
Sensible Coil Load (kWh,thermal) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 56661.7484 | 55796.8608 | 55804.7745 | 55251.9574 | 55209.465 | 55191 | 55191 | 56661.7484 | 55652.6344 | 2.643%
CE310 | 56256.3775 | 56300.9928 | 56312.7168 | 55225.158 | 55185.072 | 55083 | 55083 | 56312.7168 | 55727.2195 | 2.207%
CE320 | 62859.2053 | 62697.021 | 62746.848 | 62043.4531 | 62008.804 | 62734 | 62008.804 | 62859.2053 | 62514.8886 | 1.36%
CE330 | 63083.3765 | 63311.0655 | 63327.7722 | 63778.6556 | 62649.459 | 61822 | 61822 | 63778.6556 | 62995.3881 | 3.106%
CE340 | 63032.6061 | 63053.4306 | 63110.5851 | 62885.8356 | 62380.56 | 61406 | 61406 | 63110.5851 | 62644.8362 | 2.721%
CE350 | 50370.8304 | 47684.439 | 47676.5253 | 48545.0123 | 48588.802 | 48768 | 47676.5253 | 50370.8304 | 48605.6015 | 5.543%
CE360 | 134976.8351 | 134919.792 | 134939.7228 | 135287.1959 | 134205.707 | 134697 | 134205.707 | 135287.1959 | 134837.7088 | 0.8021%
CE400 | 41952.3595 | 41419.1334 | 41437.0125 | 40687.7468 |  | 41181 | 40687.7468 | 41952.3595 | 41335.4504 | 3.059%
CE410 | 45676.6456 | 47658.6462 | 47659.8186 |  |  | 45585 | 45585 | 47659.8186 | 46645.0276 | 4.448%
CE420 | 50389.8247 | 49666.0881 | 50612.2149 | 49523.9279 |  | 49984 | 49523.9279 | 50612.2149 | 50035.2111 | 2.175%
CE430 | 47863.3462 | 47731.335 | 47454.0624 | 46738.5816 |  | 46143 | 46143 | 47863.3462 | 47186.0651 | 3.646%
CE440 | 50876.0725 | 50592.5772 | 50492.0439 | 50060.1752 |  | 49785 | 49785 | 50876.0725 | 50361.1738 | 2.166%
CE500 | 45043.8 | 47649.8532 | 47646.0429 | 47491.2402 | 44874.225 | 47530 | 44874.225 | 47649.8532 | 46705.8602 | 5.943%
CE500 May-Sep | 34443.2344 | 36595.5867 | 36593.2419 | 36475.5877 | 34448.151 | 36480 | 34443.2344 | 36595.5867 | 35839.3003 | 6.006%
CE510 May-Sep | 77489.4321 | 82305.7041 | 82303.0662 | 81566.3401 | 77498.985 | 81563 | 77489.4321 | 82305.7041 | 80454.4213 | 5.986%
CE520 | 45109.6141 | 48101.5203 | 48095.6583 | 47986.359 | 44976.724 | 48059 | 44976.724 | 48101.5203 | 47054.8126 | 6.641%
CE522 | 45076.0312 | 47962.2978 | 47961.4185 | 47757.6997 | 44924.113 | 47795 | 44924.113 | 47962.2978 | 46912.76 | 6.476%
CE525 | 44979.0103 | 47217.5307 | 47213.4273 | 46929.7377 | 44775.105 | 47110 | 44775.105 | 47217.5307 | 46370.8018 | 5.267%
CE530 | 45045.848 | 46573.59 | 46570.0728 | 46944.356 | 44874.225 | 47002 | 44874.225 | 47002 | 46168.3486 | 4.609%
CE540 | 45111.8473 | 47022.9123 | 47019.102 | 47288.0472 | 44976.747 | 47460 | 44976.747 | 47460 | 46479.776 | 5.343%
CE545 | 44981.3517 | 46214.2494 | 46210.4391 | 46611.8912 | 44775.105 | 46668 | 44775.105 | 46668 | 45910.1727 | 4.123%
* ABS[(Max-Min)/(Mean of Example Simulation Results)]
Table B16.5.2-5. Annual Space Cooling Coil Loads ( Latent )
Latent Coil Load(kWh,thermal) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 23765.119 | 21486.5748 | 21487.161 | 22065.9923 | 22535.143 | 23067 | 21486.5748 | 23765.119 | 22401.165 | 10.17%
CE310 | 43085.7541 | 41093.7924 | 41099.3613 | 41222.4325 | 42110.836 | 42178 | 41093.7924 | 43085.7541 | 41798.3627 | 4.766%
CE320 | 36932.4726 | 33659.3109 | 33746.3616 | 34040.1066 | 35132.592 | 34224 | 33659.3109 | 36932.4726 | 34622.474 | 9.454%
CE330 | 41929.495 | 37418.9046 | 37665.6948 | 38432.7048 | 41063.373 | 40186 | 37418.9046 | 41929.495 | 39449.362 | 11.43%
CE340 | 39695.3729 | 35974.2147 | 36112.5579 | 36822.6801 | 38295.624 | 38346 | 35974.2147 | 39695.3729 | 37541.0749 | 9.912%
CE350 | 19017.1672 | 16051.9146 | 15958.1226 | 17245.3558 | 18271.394 | 18621 | 15958.1226 | 19017.1672 | 17527.4924 | 17.45%
CE360 | 27997.2274 | 24887.4141 | 24914.0862 | 25961.249 | 26994.482 | 27470 | 24887.4141 | 27997.2274 | 26370.7431 | 11.79%
CE400 | 26840.4626 | 23498.4132 | 23588.1018 | 24726.0946 |  | 25717 | 23498.4132 | 26840.4626 | 24874.0144 | 13.44%
CE410 | 22996.2083 | 19120.9647 | 19183.6881 |  |  | 20590 | 19120.9647 | 22996.2083 | 20472.7153 | 18.93%
CE420 | 22219.4827 | 19944.8688 | 20269.9167 | 20825.5388 |  | 21855 | 19944.8688 | 22219.4827 | 21022.9614 | 10.82%
CE430 | 21892.9657 | 19909.4037 | 19765.1985 | 20402.7708 |  | 21057 | 19765.1985 | 21892.9657 | 20605.4677 | 10.33%
CE440 | 22835.291 | 20787.5313 | 20689.0497 | 21357.1318 |  | 22244 | 20689.0497 | 22835.291 | 21582.6008 | 9.944%
CE500 | 18313.3062 | 18346.0083 | 18346.3014 | 18079.943 | 18231.141 | 18084 | 18079.943 | 18346.3014 | 18233.45 | 1.461%
CE500 May-Sep | 14000.1964 | 14097.2307 | 14097.2307 | 13878.7023 | 13991.418 | 13877 | 13877 | 14097.2307 | 13990.2964 | 1.574%
CE510 May-Sep | 31484.8778 | 31712.2476 | 31712.2476 | 31226.3062 | 31479.856 | 31217 | 31217 | 31712.2476 | 31472.0892 | 1.574%
CE520 | 18311.9303 | 18469.6965 | 18469.6965 | 18101.4275 | 18235.133 | 18087 | 18087 | 18469.6965 | 18279.1473 | 2.094%
CE522 | 18313.1916 | 18410.7834 | 18410.4903 | 18092.9758 | 18233.151 | 18104 | 18092.9758 | 18410.7834 | 18260.7653 | 1.74%
CE525 | 18313.9351 | 18181.5792 | 18181.5792 | 18043.5737 | 18226.509 | 18045 | 18043.5737 | 18313.9351 | 18165.3627 | 1.488%
CE530 | 0 | 60.6717 | 60.6717 | 0.0011462 | 1.186 | 0 | 0 | 60.6717 | 20.4218 | 297.1%
CE540 | 0.97976 | 106.9815 | 106.9815 | 8.5582 | 3.09 | 2 | 0.97976 | 106.9815 | 38.0985 | 278.2%
CE545 | 0 | 25.4997 | 25.4997 | 3.4549e-12 | 0.004 | 0 | 0 | 25.4997 | 8.5006 | 300%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-6. Various Annual Means (COP2, IDB)
COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 3.2491 | 3.2377 | 3.2374 | 3.2373 | 3.2264 | 3.23 | 3.2264 | 3.2491 | 3.2363 | 0.7007%
CE310 | 3.4146 | 3.4175 | 3.4175 | 3.3927 | 3.3972 | 3.38 | 3.38 | 3.4175 | 3.4032 | 1.102%
CE320 | 3.4199 | 3.458 | 3.4571 | 3.4052 | 3.406 | 3.39 | 3.39 | 3.458 | 3.4227 | 1.986%
CE330 | 3.4907 | 3.4942 | 3.5364 | 3.4907 | 3.4973 | 3.46 | 3.46 | 3.5364 | 3.4949 | 2.187%
CE340 | 3.4543 | 3.4773 | 3.4956 | 3.4476 | 3.4495 | 3.42 | 3.42 | 3.4956 | 3.4574 | 2.187%
CE350 | 3.2489 | 3.2408 | 3.2354 | 3.2436 | 3.2289 | 3.23 | 3.2289 | 3.2489 | 3.238 | 0.6186%
CE360 | 3.669 | 3.7006 | 3.7058 | 3.6779 | 3.6667 | 3.66 | 3.66 | 3.7058 | 3.68 | 1.245%
CE400 | 3.2503 | 3.2514 | 3.2519 | 3.2462 |  | 3.26 | 3.2462 | 3.26 | 3.252 | 0.4228%
CE410 | 3.2395 | 3.2124 | 3.2107 |  |  | 3.21 | 3.21 | 3.2395 | 3.2182 | 0.9171%
CE420 | 3.2261 | 3.2153 | 3.2175 | 3.2162 |  | 3.21 | 3.21 | 3.2261 | 3.217 | 0.4993%
CE430 | 3.2208 | 3.213 | 3.2115 | 3.2109 |  | 3.21 | 3.21 | 3.2208 | 3.2132 | 0.3359%
CE440 | 3.2313 | 3.2223 | 3.2219 | 3.2214 |  | 3.22 | 3.22 | 3.2313 | 3.2234 | 0.3518%
CE500 | 3.2041 | 3.2275 | 3.2265 | 3.2133 | 3.192 | 3.2 | 3.192 | 3.2275 | 3.2106 | 1.105%
CE500 May-Sep | 3.1418 | 3.1614 | 3.1616 | 3.1536 | 3.1324 | 3.14 | 3.1324 | 3.1616 | 3.1485 | 0.9285%
CE510 May-Sep | 3.5513 | 3.5774 | 3.5774 | 3.5616 | 3.5295 | 3.55 | 3.5295 | 3.5774 | 3.5579 | 1.345%
CE520 | 2.9011 | 2.9567 | 2.956 | 3.0042 | 2.8733 | 2.92 | 2.8733 | 3.0042 | 2.9352 | 4.459%
CE522 | 3.0581 | 3.0744 | 3.0728 | 3.101 | 3.0363 | 3.07 | 3.0363 | 3.101 | 3.0688 | 2.109%
CE525 | 3.4835 | 3.5309 | 3.528 | 3.508 | 3.4796 | 3.41 | 3.41 | 3.5309 | 3.49 | 3.464%
CE530 | 2.9618 | 2.969 | 2.9694 | 2.9993 | 2.9156 | 2.98 | 2.9156 | 2.9993 | 2.9658 | 2.823%
CE540 | 2.668 | 2.6748 | 2.6752 | 2.8234 | 2.6403 | 2.69 | 2.6403 | 2.8234 | 2.6953 | 6.794%
CE545 | 3.2281 | 3.2333 | 3.2355 | 3.157 | 3.1863 | 3.2 | 3.157 | 3.2355 | 3.2067 | 2.451%
IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 23.6243 | 24.0556 | 24.0556 | 24.0907 | 24.0816 | 23.99 | 23.6243 | 24.0907 | 23.983 | 1.945%
CE310 | 23.7556 | 24.1111 | 24.0556 | 24.0921 | 24.0897 | 24.01 | 23.7556 | 24.1111 | 24.019 | 1.48%
CE320 | 23.9005 | 24.3889 | 24.3889 | 24.2544 | 24.3274 | 24.53 | 23.9005 | 24.53 | 24.2983 | 2.591%
CE330 | 23.8797 | 24.2778 | 24.2778 | 24.2734 | 24.2955 | 24.18 | 23.8797 | 24.2955 | 24.1974 | 1.718%
CE340 | 23.8756 | 24.2778 | 24.2778 | 24.2983 | 24.3089 | 24.21 | 23.8756 | 24.3089 | 24.208 | 1.79%
CE350 | 25.6595 | 26.1667 | 26.1667 | 26.2416 | 26.2686 | 26.15 | 25.6595 | 26.2686 | 26.1088 | 2.333%
CE360 | 25.3649 | 25.6111 | 25.5556 | 25.3232 | 25.4809 | 25.37 | 25.3232 | 25.6111 | 25.4509 | 1.131%
CE400 | 24.1263 | 24.0556 | 24.0556 | 24.092 |  | 23.99 | 23.99 | 24.1263 | 24.0639 | 0.5664%
CE410 | 24.1221 | 24.0556 | 24.0556 |  |  | 23.99 | 23.99 | 24.1221 | 24.0558 | 0.5493%
CE420 | 23.9262 | 24.0556 | 24.0556 | 24.0906 |  | 23.99 | 23.9262 | 24.0906 | 24.0236 | 0.6846%
CE430 | 23.9916 | 24.0556 | 24.0556 | 24.0906 |  | 23.99 | 23.99 | 24.0906 | 24.0367 | 0.4186%
CE440 | 23.9118 | 24.0556 | 24.0556 | 24.0907 |  | 23.99 | 23.9118 | 24.0907 | 24.0207 | 0.7448%
CE500 | 20.2342 | 20.6667 | 20.5556 | 20.3795 | 21.0978 | 22.86 | 20.2342 | 22.86 | 20.9656 | 12.52%
CE500 May-Sep | 24.5723 | 25 | 25 | 24.9823 | 25 | 25 | 24.5723 | 25 | 24.9258 | 1.716%
CE510 May-Sep | 25.8168 | 25.1111 | 25.1111 | 24.9596 | 25 | 25 | 24.9596 | 25.8168 | 25.1664 | 3.406%
CE520 | 13.5171 | 13.7778 | 13.7222 | 13.5769 | 14.1421 | 14.89 | 13.5171 | 14.89 | 13.9377 | 9.85%
CE522 | 16.9456 | 17.2778 | 17.2222 | 16.9966 | 17.729 | 18.7 | 16.9456 | 18.7 | 17.4785 | 10.04%
CE525 | 26.8443 | 27.3889 | 27.2778 | 27.1041 | 27.7709 | 30.69 | 26.8443 | 30.69 | 27.846 | 13.81%
CE530 | 20.0253 | 20.6111 | 20.5556 | 20.586 | 21.0978 | 22.86 | 20.0253 | 22.86 | 20.956 | 13.53%
CE540 | 13.2893 | 13.7778 | 13.7222 | 13.7934 | 14.1406 | 14.98 | 13.2893 | 14.98 | 13.9506 | 12.12%
CE545 | 26.6052 | 27.3333 | 27.2778 | 27.3123 | 27.7166 | 30.69 | 26.6052 | 30.69 | 27.8225 | 14.68%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-7. Various Annual Means (Humidity Ratio, Zone Relative Humidity)
Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 0.0090691 | 0.0092 | 0.0092 | 0.0092861 | 0.0091748 | 0.0092 | 0.0090691 | 0.0092861 | 0.0091883 | 2.362%
CE310 | 0.011071 | 0.0113 | 0.0113 | 0.011261 | 0.011175 | 0.0111 | 0.011071 | 0.0113 | 0.011201 | 2.045%
CE320 | 0.009988 | 0.0101 | 0.0101 | 0.010114 | 0.010049 | 0.0099 | 0.0099 | 0.010114 | 0.010042 | 2.132%
CE330 | 0.0097409 | 0.0099 | 0.0099 | 0.0099684 | 0.0098116 | 0.0099 | 0.0097409 | 0.0099684 | 0.0098702 | 2.305%
CE340 | 0.0097914 | 0.0099 | 0.0099 | 0.0099837 | 0.0098683 | 0.0099 | 0.0097914 | 0.0099837 | 0.0098906 | 1.944%
CE350 | 0.0097059 | 0.01 | 0.01 | 0.0099257 | 0.0097585 | 0.00977 | 0.0097059 | 0.01 | 0.00986 | 2.982%
CE360 | 0.0084995 | 0.0087 | 0.0087 | 0.0087659 | 0.0085524 | 0.00858 | 0.0084995 | 0.0087659 | 0.008633 | 3.086%
CE400 | 0.0098011 | 0.01 | 0.01 | 0.010087 |  | 0.01 | 0.0098011 | 0.010087 | 0.0099776 | 2.864%
CE410 | 0.0097405 | 0.0095 | 0.0095 |  |  | 0.0095 | 0.0095 | 0.0097405 | 0.0095601 | 2.515%
CE420 | 0.0092639 | 0.0094 | 0.0094 | 0.0094486 |  | 0.0093 | 0.0092639 | 0.0094486 | 0.0093625 | 1.972%
CE430 | 0.0093103 | 0.0094 | 0.0094 | 0.0094895 |  | 0.0094 | 0.0093103 | 0.0094895 | 0.0094 | 1.907%
CE440 | 0.0091578 | 0.0093 | 0.0093 | 0.0093341 |  | 0.0092 | 0.0091578 | 0.0093341 | 0.0092584 | 1.904%
CE500 | 0.0097753 |  |  | 0.0093728 | 0.010218 | 0.0107 | 0.0093728 | 0.0107 | 0.010017 | 13.25%
CE500 May-Sep | 0.011021 | 0.0114 | 0.0114 | 0.011322 | 0.011329 | 0.0109 | 0.0109 | 0.0114 | 0.011229 | 4.453%
CE510 May-Sep | 0.011395 | 0.0114 | 0.0114 | 0.011329 | 0.011328 | 0.0109 | 0.0109 | 0.0114 | 0.011292 | 4.428%
CE520 | 0.0066924 |  |  | 0.0060452 | 0.0070234 | 0.00763 | 0.0060452 | 0.00763 | 0.0068477 | 23.14%
CE522 | 0.0081904 |  |  | 0.0076074 | 0.0085797 | 0.00901 | 0.0076074 | 0.00901 | 0.0083469 | 16.8%
CE525 | 0.013713 |  |  | 0.013802 | 0.01398 | 0.0151 | 0.013713 | 0.0151 | 0.014149 | 9.805%
CE530 | 0.0062265 |  |  | 0.0067122 | 0.0057975 | 0.00667 | 0.0057975 | 0.0067122 | 0.0063516 | 14.4%
CE540 | 0.0044601 |  |  | 0.0043466 | 0.0038546 | 0.00463 | 0.0038546 | 0.00463 | 0.0043228 | 17.94%
CE545 | 0.0062265 |  |  | 0.0067334 | 0.006749 | 0.00722 | 0.0062265 | 0.00722 | 0.0067322 | 14.76%
Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE300 | 48.6149 | 48.26 | 48.28 | 48.5913 | 47.8261 | 47.93 | 47.8261 | 48.6149 | 48.2504 | 1.635%
CE310 | 58.3307 | 58.51 | 58.53 | 58.5512 | 57.841 | 57.8 | 57.8 | 58.5512 | 58.2605 | 1.289%
CE320 | 52.0053 | 51.21 | 51.25 | 51.8407 | 51.1034 | 49.94 | 49.94 | 52.0053 | 51.2249 | 4.032%
CE330 | 50.8445 | 50.58 | 50.65 | 51.1765 | 50.0848 | 50.7 | 50.0848 | 51.1765 | 50.6726 | 2.154%
CE340 | 51.085 | 50.69 | 50.73 | 51.1479 | 50.2967 | 50.78 | 50.2967 | 51.1479 | 50.7883 | 1.676%
CE350 | 45.484 | 45.45 | 45.55 | 45.1731 | 44.3162 | 44.56 | 44.3162 | 45.55 | 45.0889 | 2.736%
CE360 | 41.0335 | 41.49 | 41.49 | 42.3695 | 40.871 | 41.21 | 40.871 | 42.3695 | 41.4107 | 3.619%
CE400 | 50.7709 | 52.21 | 52.25 | 52.5485 |  | 52.01 | 50.7709 | 52.5485 | 51.9579 | 3.421%
CE410 | 50.4971 | 49.65 | 49.63 |  |  | 49.75 | 49.63 | 50.4971 | 49.8818 | 1.738%
CE420 | 48.7794 | 49.14 | 48.97 | 49.3981 |  | 48.76 | 48.76 | 49.3981 | 49.0095 | 1.302%
CE430 | 48.8219 | 49.17 | 49.3 | 49.6002 |  | 49.17 | 48.8219 | 49.6002 | 49.2124 | 1.581%
CE440 | 48.3298 | 48.46 | 48.57 | 48.8288 |  | 48.23 | 48.23 | 48.8288 | 48.4837 | 1.235%
CE500 | 66.5261 |  |  | 59.1976 | 65.9419 | 63.73 | 59.1976 | 66.5261 | 63.8489 | 11.48%
CE500 May-Sep | 57.0476 | 57.47 | 57.47 | 57.3219 | 57.0722 | 55.13 | 55.13 | 57.47 | 56.9186 | 4.111%
CE510 May-Sep | 54.7001 | 57.36 | 57.36 | 57.4361 | 57.0615 | 55.24 | 54.7001 | 57.4361 | 56.5263 | 4.84%
CE520 | 69.8745 |  |  | 61.4049 | 70.2268 | 72.17 | 61.4049 | 72.17 | 68.419 | 15.73%
CE522 | 68.6774 |  |  | 60.7524 | 68.2314 | 68.11 | 60.7524 | 68.6774 | 66.4428 | 11.93%
CE525 | 61.4674 |  |  | 54.9944 | 60.1387 | 57.37 | 54.9944 | 61.4674 | 58.4926 | 11.07%
CE530 | 46.7299 |  |  | 48.9733 | 41.4516 | 39.6 | 39.6 | 48.9733 | 44.1887 | 21.21%
CE540 | 48.521 |  |  | 46.3072 | 40.0509 | 43.82 | 40.0509 | 48.521 | 44.6748 | 18.96%
CE545 | 36.6249 |  |  | 38.6306 | 36.8747 | 29.2 | 29.2 | 38.6306 | 35.3325 | 26.69%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-8. f(ODB) Sensitivity CE500 and CE530, April 30 and June 25 (Energy, Coil Loads)
Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
Energy Consumption, Compr. + Both Fans (Wh,e)
CE500Apr30 | 3892.9389 | 3975.4583 | 3975.1667 | 4028.8242 | 3901.0417 | 4073 | 3892.9389 | 4073 | 3974.4049 | 4.531%
CE500Jun25 | 5044.9219 | 5204.3333 | 5204.0833 | 5228.78 | 5066.5 | 5230 | 5044.9219 | 5230 | 5163.1031 | 3.585%
Del CE500 | 1151.9831 | 1228.875 | 1228.9167 | 1199.9558 | 1165.4583 | 1157 | 1151.9831 | 1228.9167 | 1188.6981 | 6.472%
CE530Apr30 | 3022.7732 | 3062 | 3061.7917 | 3101.4372 | 3091.5417 | 3144 | 3022.7732 | 3144 | 3080.5906 | 3.935%
CE530Jun25 | 3894.1233 | 3978.2083 | 3978.0833 | 4028.6999 | 3934.625 | 4043 | 3894.1233 | 4043 | 3976.1233 | 3.744%
Del CE530 | 871.3501 | 916.2083 | 916.2917 | 927.2627 | 843.0833 | 899 | 843.0833 | 927.2627 | 895.5327 | 9.4%
Energy Consumption, Compressor (Wh,e)
CE500Apr30 | 3014.619 | 3119.8333 | 3119.6667 |  | 3020.0417 | 3159 | 3014.619 | 3159 | 3086.6321 | 4.678%
CE500Jun25 | 4083.8829 | 4263.5417 | 4263.4167 |  | 4105.9583 | 4239 | 4083.8829 | 4263.5417 | 4191.1599 | 4.287%
Del CE500 | 1069.2639 | 1143.7083 | 1143.75 |  | 1085.9167 | 1080 | 1069.2639 | 1143.75 | 1104.5278 | 6.744%
CE530Apr30 | 2311.4724 | 2390.0417 | 2389.9167 |  | 2378.4583 | 2411 | 2311.4724 | 2411 | 2376.1778 | 4.189%
CE530Jun25 | 3118.0954 | 3243 | 3242.9583 |  | 3165.5833 | 3248 | 3118.0954 | 3248 | 3203.5274 | 4.055%
Del CE530 | 806.623 | 852.9583 | 853.0417 |  | 787.125 | 837 | 787.125 | 853.0417 | 827.3496 | 7.967%
Energy Consumption, Condenser Fan (Wh,e)
CE500Apr30 | 376.0762 | 389.125 | 389.0833 |  | 377.25 | 391 | 376.0762 | 391 | 384.5069 | 3.881%
CE500Jun25 | 411.4946 | 426.3333 | 426.3333 |  | 411.3333 | 424 | 411.3333 | 426.3333 | 419.8989 | 3.572%
Del CE500 | 35.4184 | 37.2083 | 37.25 |  | 34.0833 | 33 | 33 | 37.25 | 35.392 | 12.01%
CE530Apr30 | 304.5625 | 311.1667 | 311.125 |  | 305.3333 | 314 | 304.5625 | 314 | 309.2375 | 3.052%
CE530Jun25 | 332.2771 | 339.625 | 339.625 |  | 329.25 | 340 | 329.25 | 340 | 336.1554 | 3.198%
Del CE530 | 27.7146 | 28.4583 | 28.5 |  | 23.9167 | 26 | 23.9167 | 28.5 | 26.9179 | 17.03%
Energy Consumption, Supply Fan (Wh,e)
CE500Apr30 | 502.2437 | 466.5 | 466.4167 | 518.9273 | 503.75 | 522 | 466.4167 | 522 | 496.6396 | 11.19%
CE500Jun25 | 549.5444 | 514.4583 | 514.3333 | 565.5397 | 549.2083 | 566 | 514.3333 | 566 | 543.1807 | 9.512%
Del CE500 | 47.3007 | 47.9583 | 47.9167 | 46.6123 | 45.4583 | 44 | 44 | 47.9583 | 46.5411 | 8.505%
CE530Apr30 | 406.7383 | 360.7917 | 360.75 | 412.3973 | 407.75 | 419 | 360.75 | 419 | 394.5712 | 14.76%
CE530Jun25 | 443.7507 | 395.5833 | 395.5 | 450.0798 | 439.7917 | 454 | 395.5 | 454 | 429.7842 | 13.61%
Del CE530 | 37.0125 | 34.7917 | 34.75 | 37.6824 | 32.0417 | 35 | 32.0417 | 37.6824 | 35.213 | 16.02%
Sensible + Latent Coil Load (Wh,th)
CE500Apr30 | 13185.6871 | 13732.6998 | 13732.9074 | 13655.2659 | 13169.5417 | 13673 | 13169.5417 | 13732.9074 | 13524.8503 | 4.165%
CE500Jun25 | 13188.0504 | 13837.5319 | 13837.3853 | 13733.0749 | 13198.0833 | 13727 | 13188.0504 | 13837.5319 | 13586.8543 | 4.78%
Del CE500 | 2.3633 | 104.8321 | 104.4779 | 77.809 | 28.5417 | 54 | 2.3633 | 104.8321 | 62.004 | 165.3%
CE530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9775.2401 | 9365.4583 | 9798 | 9353.1633 | 9798 | 9622.401 | 4.623%
CE530Jun25 | 9376.2963 | 9760.7918 | 9760.6941 | 9835.1361 | 9387.625 | 9834 | 9376.2963 | 9835.1361 | 9659.0905 | 4.75%
Del CE530 | 23.1329 | 39.6418 | 39.2998 | 59.896 | 22.1667 | 36 | 22.1667 | 59.896 | 36.6895 | 102.8%
Sensible Coil Load (Wh,th)
CE500Apr30 | 9374.7971 | 9924.8179 | 9925.0255 | 9883.6259 | 9365.4583 | 9902 | 9365.4583 | 9925.0255 | 9729.2874 | 5.751%
CE500Jun25 | 9377.6867 | 9981.2396 | 9981.0931 | 9952.5713 | 9387.625 | 9946 | 9377.6867 | 9981.2396 | 9771.0359 | 6.177%
Del CE500 | 2.8896 | 56.4217 | 56.0676 | 68.9454 | 22.1667 | 44 | 2.8896 | 68.9454 | 41.7485 | 158.2%
CE530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9775.2401 | 9365.4583 | 9798 | 9353.1633 | 9798 | 9622.401 | 4.623%
CE530Jun25 | 9376.2963 | 9760.7674 | 9760.6697 | 9835.1361 | 9387.625 | 9834 | 9376.2963 | 9835.1361 | 9659.0824 | 4.75%
Del CE530 | 23.1329 | 39.6174 | 39.2754 | 59.896 | 22.1667 | 36 | 22.1667 | 59.896 | 36.6814 | 102.9%
Latent Coil Load (Wh,th)
CE500Apr30 | 3810.89 | 3807.8819 | 3807.8819 | 3771.64 | 3804.375 | 3770 | 3770 | 3810.89 | 3795.4448 | 1.077%
CE500Jun25 | 3810.3637 | 3856.2923 | 3856.2923 | 3780.5037 | 3810.4167 | 3780 | 3780 | 3856.2923 | 3815.6448 | 1.999%
Del CE500 | -0.52625 | 48.4104 | 48.4104 | 8.8636 | 6.0417 | 10 | -0.52625 | 48.4104 | 20.2 | 242.3%
CE530Apr30 | -5.4771e-13 | 0 | 0 | 5.713e-13 | 0 | 0 | -5.4771e-13 | 5.713e-13 | 3.9312e-15 | ----
CE530Jun25 | 7.2905e-13 | 0.024425 | 0.024425 | 6.6831e-13 | 0 | 0 | 0 | 0.024425 | 0.0081417 | ----
Del CE530 | 1.2768e-12 | 0.024425 | 0.024425 | 9.7013e-14 | 0 | 0 | 0 | 0.024425 | 0.0081417 | ----
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-9. f(ODB) Sensitivity CE500 and CE530, April 30 and June 25 (COP2, Zone Conditions)
Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
Humidity Ratio (kg/kg)
CE500Apr30 | 0.010675 | 0.011 | 0.011 | 0.010984 | 0.010938 | 0.016 | 0.010675 | 0.016 | 0.011766 | 45.25%
CE500Jun25 | 0.011168 | 0.0115 | 0.0115 | 0.011459 | 0.011479 | 0.011 | 0.011 | 0.0115 | 0.011351 | 4.405%
Del CE500 | 0.00049288 | 0.0005 | 0.0005 | 0.00047513 | 0.00054117 | -0.005 | -0.005 | 0.00054117 | -0.00041514 | 1335%
CE530Apr30 | 0.006208 | 0.0071 | 0.0071 | 0.0067531 | 0.005485 | 0.00674 | 0.005485 | 0.0071 | 0.0065644 | 24.6%
CE530Jun25 | 0.006208 | 0.0078 | 0.0078 | 0.0067531 | 0.005478 | 0.00674 | 0.005478 | 0.0078 | 0.0067965 | 34.16%
Del CE530 | 0 | 0.0007 | 0.0007 | 9.3415e-16 | -7e-06 | 0 | -7e-06 | 0.0007 | 0.00023217 | 304.5%
COP2
CE500Apr30 | 3.8448 | 3.9136 | 3.9139 | 3.8497 | 3.8372 | 3.85 | 3.8372 | 3.9139 | 3.8682 | 1.984%
CE500Jun25 | 2.9313 | 2.9505 | 2.9506 | 2.9431 | 2.9213 | 2.94 | 2.9213 | 2.9506 | 2.9395 | 0.9966%
Del CE500 | -0.9135 | -0.9631 | -0.96334 | -0.90662 | -0.91589 | -0.91 | -0.96334 | -0.90662 | -0.92874 | 6.108%
CE530Apr30 | 3.5431 | 3.5988 | 3.5991 | 3.4414 | 3.4604 | 3.59 | 3.4414 | 3.5991 | 3.5388 | 4.457%
CE530Jun25 | 2.7197 | 2.7245 | 2.7245 | 2.7795 | 2.69 | 2.74 | 2.69 | 2.7795 | 2.7297 | 3.278%
Del CE530 | -0.82341 | -0.87433 | -0.87464 | -0.66187 | -0.7704 | -0.85 | -0.87464 | -0.66187 | -0.80911 | 26.3%
ODB (°C)
CE500Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 16.7917 | 16.96 | 16.8527 | 0.9989%
CE500Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5083 | 0.05648%
Del CE500 | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54 | 12.54 | 12.725 | 12.6556 | 1.462%
CE530Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 16.7917 | 16.96 | 16.8527 | 0.9989%
CE530Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5083 | 0.05648%
Del CE530 | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54 | 12.54 | 12.725 | 12.6556 | 1.462%
EDB (°C)
CE500Apr30 | 24.6411 | 24.9444 | 24.9444 | 24.9818 | 25 | 25 | 24.6411 | 25 | 24.9186 | 1.44%
CE500Jun25 | 24.5478 | 25 | 25 | 24.9828 | 25 | 25 | 24.5478 | 25 | 24.9218 | 1.815%
Del CE500 | -0.093296 | 0.055556 | 0.055556 | 0.0010234 | 0 | 0 | -0.093296 | 0.055556 | 0.0031398 | 4741%
CE530Apr30 | 24.365 | 24.9444 | 24.6667 | 25 | 25 | 25 | 24.365 | 25 | 24.8294 | 2.557%
CE530Jun25 | 24.3537 | 24.9444 | 24.9444 | 25 | 25 | 25 | 24.3537 | 25 | 24.8738 | 2.598%
Del CE530 | -0.011358 | 0 | 0.27778 | 7.121e-08 | 0 | 0 | -0.011358 | 0.27778 | 0.044403 | 651.2%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Table-R
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.2-10. Hourly Integrated Maxima (Total Cooling System Energy Consumption and Total Coil Load)
Energy Consumption, Compressor + Both Fans (Wh,e) | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 | 11932 | 1900-07-20 | 15 | 11548 | 2003-07-20 | 15 | 11548 | 11932 | 11695.3161 | 3.283% | #REF!
CE310 | 12594.4016 | 20-Jul | 15 | 12583 | 2002-07-20 | 15 | 12595 | 2002-07-20 | 15 | 12540.8188 | 2010-07-20 | 15 | 12653 | 1900-07-20 | 15 | 12162 | 2003-08-16 | 16 | 12162 | 12653 | 12521.3701 | 3.921%
CE320 | 13028.1986 | 20-Jul | 15 | 12916 | 2002-07-20 | 15 | 12981 | 2002-07-20 | 15 | 12954.4267 | 2010-07-20 | 15 | 13104 | 1900-07-20 | 15 | 12875 | 2003-07-20 | 14 | 12875 | 13104 | 12976.4375 | 1.765%
CE330 | 13346.701 | 20-Jul | 15 | 13212 | 2002-07-20 | 15 | 13407 | 2002-07-20 | 15 | 13314.1099 | 2010-07-20 | 15 | 13467 | 1900-07-20 | 15 | 13335 | 2003-07-20 | 15 | 13212 | 13467 | 13346.9685 | 1.911%
CE340 | 13180.9018 | 20-Jul | 15 | 13158 | 2002-07-20 | 15 | 13190 | 2002-07-20 | 15 | 13134.1703 | 2010-07-20 | 15 | 13277 | 1900-07-20 | 15 | 13101 | 2003-07-20 | 14 | 13101 | 13277 | 13173.512 | 1.336%
CE350 | 11626.889 | 20-Jul | 15 | 11654 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8619 | 2010-07-20 | 15 | 11932 | 1900-07-20 | 15 | 11546 | 2003-07-20 | 15 | 11546 | 11932 | 11710.1251 | 3.296%
CE360 | 12769.5022 | 20-Jul | 15 | 12736 | 2002-07-20 | 15 | 12726 | 2002-07-20 | 15 | 12744.2783 | 2010-07-20 | 15 | 12863 | 1900-07-20 | 15 | 12762 | 2003-07-20 | 14 | 12726 | 12863 | 12766.7967 | 1.073%
CE400 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11677 | 2004-09-18 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | 11519 | 2003-07-20 | 15 | 11519 | 11899.8597 | 11657.5455 | 3.267%
CE410 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | [6 empty] | 11549 | 2003-07-20 | 15 | 11549 | 11627.8677 | 11585.7169 | 0.6807%
CE420 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | 11548 | 2003-07-20 | 15 | 11548 | 11899.8597 | 11647.9794 | 3.021%
CE430 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | 11548 | 2003-07-20 | 15 | 11548 | 11899.8597 | 11647.9794 | 3.021%
CE440 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | 11461 | 2003-08-16 | 16 | 11461 | 11899.8597 | 11630.5794 | 3.773%
CE500 | 10166.4831 | 20-Jul | 15 | 10431 | 2002-07-20 | 15 | 10425 | 2002-07-20 | 15 | 10398.6872 | 2010-07-20 | 15 | 10177 | 1900-07-20 | 15 | 10274 | 2003-06-04 | 15 | 10166.4831 | 10431 | 10312.0284 | 2.565%
CE510 | 11204.8968 | 20-Jul | 15 | 11590 | 2002-07-20 | 15 | 11587 | 2002-07-20 | 15 | 11409.8034 | 2010-07-20 | 15 | 11186 | 1900-07-20 | 15 | 11344 | 2003-07-20 | 14 | 11186 | 11590 | 11386.95 | 3.548%
CE520 | 11035.3898 | 20-Jul | 15 | 10989 | 2002-07-20 | 15 | 11014 | 2002-07-20 | 15 | 11100.5253 | 2010-07-20 | 15 | 11044 | 1900-07-20 | 15 | 10684 | 2003-06-04 | 15 | 10684 | 11100.5253 | 10977.8192 | 3.794%
CE522 | 10430.7791 | 20-Jul | 15 | 10972 | 2002-07-20 | 15 | 10966 | 2002-07-20 | 15 | 10762.3872 | 2010-07-20 | 15 | 10639 | 1900-07-20 | 15 | 10747 | 2003-08-16 | 15 | 10430.7791 | 10972 | 10752.861 | 5.033%
CE525 | 9366.7481 | 20-Jul | 15 | 9538 | 2002-07-20 | 15 | 9531 | 2002-07-20 | 15 | 9569.5705 | 2010-07-20 | 15 | 9419 | 1900-07-20 | 15 | 9585 | 2003-08-16 | 15 | 9366.7481 | 9585 | 9501.5531 | 2.297%
CE530 | 8028.3285 | 20-Jul | 15 | 8059 | 2002-07-20 | 15 | 8055 | 2002-07-20 | 15 | 8171.0479 | 2010-07-20 | 15 | 7992 | 1900-07-20 | 15 | 8089 | 2003-08-16 | 15 | 7992 | 8171.0479 | 8065.7294 | 2.22%
CE540 | 8698.9562 | 20-Jul | 15 | 8943 | 2002-07-20 | 15 | 8939 | 2002-07-20 | 15 | 8677.4025 | 2010-07-20 | 15 | 8846 | 1900-07-20 | 15 | 8985 | 2003-08-16 | 15 | 8677.4025 | 8985 | 8848.2264 | 3.476%
CE545 | 7204.827 | 20-Jul | 15 | 7350 | 2002-07-20 | 15 | 7346 | 2002-07-20 | 15 | 7762.756 | 2010-07-20 | 15 | 7351 | 1900-07-20 | 15 | 7471 | 2003-06-04 | 15 | 7204.827 | 7762.756 | 7414.2638 | 7.525%
Senstible + Latent Coil Load (Wh,th) | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 | 32502 | 1900-07-20 | 15 | 32072 | 2003-07-20 | 15 | 31401 | 32733.2556 | 32056.2176 | 4.156%
CE310 | 37328 | 03-Sep | 15 | 36750 | 2004-09-03 | 16 | 37033 | 2004-09-03 | 16 | 37126.4795 | 2010-09-17 | 15 | 37261 | 1900-09-03 | 15 | 36991 | 2003-09-03 | 16 | 36750 | 37328 | 37081.5799 | 1.559%
CE320 | 40317.6 | 03-Sep | 16 | 53813 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9 | 39765.1828 | 2010-09-03 | 16 | 39904 | 1900-09-03 | 16 | 39920 | 2003-09-03 | 16 | 39765.1828 | 53823 | 44590.4638 | 31.53%
CE330 | 43492 | 02-Oct | 9 | 43628 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9 | 43445.0808 | 2010-10-02 | 9 | 43978 | 1900-10-02 | 9 | 42415 | 2003-07-10 | 11 | 42415 | 64572 | 46921.6801 | 47.22%
CE340 | 41651.7 | 02-Oct | 10 | 50819 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9 | 41328.2736 | 2010-10-02 | 10 | 41366 | 1900-09-03 | 15 | 41132 | 2003-09-03 | 16 | 41132 | 59549 | 45974.3289 | 40.06%
CE350 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31454 | 2001-07-20 | 15 | 32733.265 | 2010-07-20 | 15 | 32502 | 1900-07-20 | 15 | 32077 | 2003-07-20 | 15 | 31401 | 32733.265 | 32043.1658 | 4.158%
CE360 | 38857.16 | 02-Oct | 10 | 40613 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9 | 38459.7282 | 2010-10-02 | 11 | 38322 | 1900-10-02 | 10 | 38451 | 2003-10-02 | 10 | 38322 | 41019 | 39286.9814 | 6.865%
CE400 | 41178.6 | 16-Sep | 15 | 40543 | 2002-09-18 | 14 | 49838 | 2003-09-18 | 15 | 40728.1422 | 2010-09-16 | 15 |  |  |  | 40774 | 2003-09-16 | 14 | 40543 | 49838 | 42612.3484 | 21.81%
CE410 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | [6 empty] | 32073 | 2003-07-20 | 15 | 31401 | 32091.73 | 31755.1825 | 2.175%
CE420 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 |  |  |  | 32072 | 2003-07-20 | 15 | 31401 | 32733.2556 | 31967.0611 | 4.168%
CE430 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 |  |  |  | 32072 | 2003-07-20 | 15 | 31401 | 32733.2556 | 31967.0611 | 4.168%
CE440 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2003-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 |  |  |  | 31777 | 2003-07-08 | 16 | 31401 | 32733.2556 | 31908.0611 | 4.175%
CE500 | 27485.51 | 28-Oct | 15 | 27707 | 2001-08-16 | 16 | 27706 | 2001-08-16 | 16 | 27646.4256 | 2010-06-29 | 16 | 26567 | 1900-06-29 | 16 | 27555 | 2003-06-29 | 15 | 26567 | 27707 | 27444.4893 | 4.154%
CE510 | 30593.05 | 29-Apr | 19 | 31188 | 2001-07-20 | 15 | 31188 | 2001-07-20 | 15 | 31177.751 | 2010-06-17 | 14 | 29948 | 1900-06-17 | 14 | 31097 | 2003-06-17 | 13 | 29948 | 31188 | 30865.3002 | 4.017%
CE520 | 27329.6 | 28-Sep | 15 | 27878 | 2004-08-14 | 16 | 27878 | 2004-07-23 | 16 | 27652.6954 | 2010-06-29 | 16 | 26675 | 1900-07-20 | 16 | 28343 | 2003-05-23 | 15 | 26675 | 28343 | 27626.0492 | 6.038%
CE522 | 27383.59 | 12-Mai | 15 | 27868 | 2002-08-16 | 16 | 27866 | 2002-08-16 | 16 | 27658.7918 | 2010-06-29 | 16 | 26514 | 1900-06-29 | 16 | 27636 | 2003-06-29 | 15 | 26514 | 27868 | 27487.7303 | 4.926%
CE525 | 27739.77 | 26-Jul | 16 | 27466 | 2002-07-08 | 16 | 27466 | 2002-07-08 | 16 | 27576.5137 | 2010-06-29 | 16 | 26683 | 1900-06-29 | 16 | 27462 | 2003-06-29 | 15 | 26683 | 27739.77 | 27398.8806 | 3.857%
CE530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19638.7657 | 2010-07-20 | 15 | 18776 | 1900-06-04 | 15 | 19626 | 2003-07-08 | 15 | 18776 | 19834.1 | 19504.3109 | 5.425%
CE540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19726.32 | 2010-07-20 | 15 | 18794 | 1900-06-04 | 15 | 19799 | 2003-08-16 | 15 | 18794 | 19799 | 19571.0533 | 5.135%
CE545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19539.7081 | 2010-07-20 | 15 | 18764 | 1900-07-20 | 15 | 19497 | 2003-06-04 | 15 | 18764 | 20075.2 | 19470.818 | 6.734%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-11. Hourly Integrated Maxima (Sensible Coil Load and Latent Coil Load)
Sensible Coil Load (Wh,th) | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 | 23457 | 1900-07-20 | 15 | 22908 | 2003-06-04 | 15 | 22908 | 23530.8075 | 23263.5346 | 2.677%
CE310 | 23094.3 | 10-Sep | 15 | 23080 | 2004-09-10 | 16 | 23119 | 2004-06-04 | 16 | 23276.4591 | 2010-07-11 | 16 | 23078 | 1900-09-10 | 15 | 22649 | 2003-06-13 | 16 | 22649 | 23276.4591 | 23049.4598 | 2.722%
CE320 | 31315.6 | 24-Apr | 16 | 31119 | 2004-04-24 | 16 | 31072 | 2002-04-24 | 16 | 31972.0849 | 2010-04-24 | 15 | 31134 | 1900-06-03 | 16 | 30967 | 2003-04-24 | 15 | 30967 | 31972.0849 | 31263.2808 | 3.215%
CE330 | 33226.1 | 14-Jun | 14 | 33410 | 2002-06-14 | 14 | 34490 | 2002-06-14 | 15 | 34764.7794 | 2010-06-14 | 15 | 33997 | 1900-04-24 | 16 | 33421 | 2003-09-09 | 14 | 33226.1 | 34764.7794 | 33884.8132 | 4.541%
CE340 | 32828.9 | 24-Apr | 15 | 32086 | 2002-05-16 | 16 | 32086 | 2002-05-16 | 16 | 32887.7843 | 2010-04-24 | 15 | 32940 | 1900-04-24 | 16 | 32180 | 2003-04-24 | 15 | 32086 | 32940 | 32501.4474 | 2.628%
CE350 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8071 | 2010-07-20 | 15 | 23457 | 1900-07-20 | 15 | 22876 | 2003-07-10 | 15 | 22876 | 23530.8071 | 23258.2178 | 2.815%
CE360 | 32060.7 | 24-Apr | 16 | 32111 | 2003-04-24 | 16 | 32065 | 2004-04-24 | 16 | 32620.9131 | 2010-04-24 | 16 | 31981 | 1900-04-24 | 16 | 32179 | 2003-04-24 | 15 | 31981 | 32620.9131 | 32169.6022 | 1.989%
CE400 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | 22877 | 2003-07-08 | 16 | 22877 | 23530.8075 | 23218.6615 | 2.816%
CE410 | 23265.7 | 10-Sep | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | [6 empty] | 22893 | 2003-07-29 | 15 | 22893 | 23265.7 | 23141.675 | 1.611%
CE420 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | 22893 | 2003-07-29 | 15 | 22893 | 23530.8075 | 23221.8415 | 2.747%
CE430 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | 22893 | 2003-07-29 | 15 | 22893 | 23530.8075 | 23221.8415 | 2.747%
CE440 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | 22875 | 2003-08-16 | 16 | 22875 | 23530.8075 | 23218.2415 | 2.825%
CE500 | 19549.2 | 28-Oct | 15 | 20009 | 2003-06-04 | 16 | 20008 | 2002-09-10 | 16 | 19849.2901 | 2010-07-20 | 15 | 18776 | 1900-06-04 | 15 | 19818 | 2003-07-29 | 15 | 18776 | 20009 | 19668.2483 | 6.269%
CE510 | 21729.2 | 29-Apr | 19 | 22513 | 2002-07-11 | 15 | 22513 | 2003-07-11 | 15 | 22290.3117 | 2010-07-20 | 15 | 21121 | 1900-06-04 | 13 | 22269 | 2003-07-20 | 14 | 21121 | 22513 | 22072.5853 | 6.306%
CE520 | 19415.9 | 28-Sep | 15 | 20159 | 2004-05-26 | 16 | 20154 | 2004-05-26 | 16 | 19999.2936 | 2010-07-20 | 15 | 18969 | 1900-07-20 | 16 | 20378 | 2003-05-23 | 15 | 18969 | 20378 | 19845.8656 | 7.1%
CE522 | 19488.8 | 12-Mai | 15 | 20137 | 2002-07-11 | 16 | 20135 | 2002-07-11 | 16 | 19933.5062 | 2010-07-20 | 15 | 18785 | 1900-06-04 | 15 | 19920 | 2003-08-16 | 15 | 18785 | 20137 | 19733.2177 | 6.851%
CE525 | 19702.7 | 26-Jul | 16 | 19850 | 2002-04-24 | 16 | 19850 | 2002-04-24 | 16 | 19663.6722 | 2010-07-20 | 15 | 18759 | 1900-06-04 | 15 | 19661 | 2003-06-04 | 15 | 18759 | 19850 | 19581.062 | 5.572%
CE530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19638.7657 | 2010-07-20 | 15 | 18776 | 1900-06-04 | 15 | 19626 | 2003-07-08 | 15 | 18776 | 19834.1 | 19504.3109 | 5.425%
CE540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19726.32 | 2010-07-20 | 15 | 18794 | 1900-06-04 | 15 | 19799 | 2003-08-16 | 15 | 18794 | 19799 | 19571.0533 | 5.135%
CE545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19539.7081 | 2010-07-20 | 15 | 18759 | 1900-06-04 | 15 | 19497 | 2003-06-04 | 15 | 18759 | 20075.2 | 19469.9847 | 6.76%
Latent Coil Load (Wh,th) | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9394 | 2001-09-03 | 15 | 10234.8217 | 2010-07-10 | 13 | 10375 | 1900-09-03 | 15 | 10392 | 2003-09-03 | 15 | 9304 | 10392 | 9889.2536 | 11%
CE310 | 15907 | 03-Sep | 15 | 15139 | 2001-09-03 | 15 | 15270 | 2001-09-03 | 15 | 16274.8379 | 2010-08-04 | 15 | 16112 | 1900-08-04 | 15 | 16077 | 2003-09-03 | 16 | 15139 | 16274.8379 | 15796.6397 | 7.19%
CE320 | 23147.3 | 02-Oct | 10 | 31497 | 2002-10-02 | 9 | 31503 | 2002-10-02 | 9 | 22195.4712 | 2010-10-02 | 10 | 21697 | 1900-09-17 | 12 | 21929 | 2003-10-01 | 20 | 21697 | 31503 | 25328.1285 | 38.72%
CE330 | 27825.2 | 18-Sep | 16 | 26941 | 2003-09-18 | 15 | 40809 | 2002-10-02 | 9 | 27134.3149 | 2010-09-18 | 16 | 28184 | 1900-09-18 | 15 | 27488 | 2003-09-18 | 15 | 26941 | 40809 | 29730.2525 | 46.65%
CE340 | 24848.3 | 02-Oct | 9 | 30451 | 2002-10-02 | 9 | 36011 | 2002-10-02 | 9 | 23911.2415 | 2010-10-02 | 10 | 24225 | 1900-09-03 | 17 | 23794 | 2003-10-01 | 20 | 23794 | 36011 | 27206.7569 | 44.9%
CE350 | 9751.26 | 01-Oct | 13 | 9303 | 2001-09-03 | 15 | 9393 | 2001-09-03 | 15 | 10235.3532 | 2010-07-10 | 13 | 10755 | 1900-10-02 | 8 | 11603 | 2003-08-03 | 7 | 9303 | 11603 | 10173.4355 | 22.61%
CE360 | 9275.16 | 02-Oct | 10 | 10026 | 2002-10-02 | 9 | 10336 | 2002-10-02 | 9 | 8520.3176 | 2010-10-02 | 11 | 8859 | 1900-09-03 | 17 | 8934 | 2003-09-03 | 17 | 8520.3176 | 10336 | 9325.0796 | 19.47%
CE400 | 27075.3 | 16-Sep | 15 | 25578 | 2002-09-18 | 14 | 32396 | 2003-09-18 | 15 | 26317.2818 | 2010-09-16 | 14 |  |  |  | 26645 | 2003-09-16 | 14 | 25578 | 32396 | 27602.3164 | 24.7%
CE410 | 11138.9 | 16-Sep | 15 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | [6 empty] | 10377 | 2003-09-09 | 15 | 9304 | 11138.9 | 10052.725 | 18.25%
CE420 | 9751.04 | 01-Oct | 13 | 9304 | 2001-09-03 | 15 | 9394 | 2003-09-03 | 15 | 10234.8217 | 2010-07-10 | 13 |  |  |  | 10394 | 2003-09-03 | 15 | 9304 | 10394 | 9815.5723 | 11.1%
CE430 | 9635.7 | 03-Sep | 16 | 11105 | 2004-10-24 | 14 | 11101 | 2003-05-21 | 15 | 11073.7739 | 2010-10-24 | 13 |  |  |  | 10394 | 2003-09-03 | 15 | 9635.7 | 11105 | 10661.8948 | 13.78%
CE440 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | 10234.8217 | 2010-07-10 | 13 |  |  |  | 10139 | 2003-09-03 | 15 | 9304 | 10234.8217 | 9740.9043 | 9.556%
CE500 | 7965.46 | 06-Oct | 15 | 7733 | 2001-09-03 | 15 | 7733 | 2001-09-03 | 15 | 7838.7203 | 2010-06-29 | 16 | 7805 | 1900-06-29 | 16 | 7762 | 2003-06-29 | 15 | 7733 | 7965.46 | 7806.1967 | 2.978%
CE510 | 8892.56 | 15-Sep | 11 | 8723 | 2002-10-02 | 9 | 8723 | 2003-10-02 | 9 | 8954.7918 | 2010-06-17 | 14 | 8850 | 1900-06-17 | 14 | 8874 | 2003-06-17 | 13 | 8723 | 8954.7918 | 8836.2253 | 2.623%
CE520 | 7913.7 | 28-Sep | 15 | 7785 | 2001-09-03 | 15 | 7785 | 2001-09-03 | 15 | 7698.5342 | 2010-06-29 | 16 | 7726 | 1900-06-30 | 16 | 7964 | 2003-05-23 | 15 | 7698.5342 | 7964 | 7812.039 | 3.398%
CE522 | 7906.7 | 02-Mai | 15 | 7760 | 2001-09-03 | 15 | 7760 | 2001-09-03 | 15 | 7769.7702 | 2010-06-29 | 16 | 7743 | 1900-06-29 | 16 | 7745 | 2003-06-29 | 15 | 7743 | 7906.7 | 7780.745 | 2.104%
CE525 | 8037.07 | 26-Jul | 16 | 7663 | 2001-09-03 | 15 | 7663 | 2001-09-03 | 15 | 7947.3919 | 2010-06-29 | 16 | 7938 | 1900-06-29 | 16 | 7820 | 2003-06-29 | 15 | 7663 | 8037.07 | 7844.7437 | 4.768%
CE530 | 1.6431e-11 | 18-Jun | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0587 | 2010-03-16 | 10 | 179 | 1900-03-11 | 11 | 35.9 | 2003-11-01 | 20 | 0 | 179 | 35.9931 | 497.3%
CE540 | 627.186 | 11-Mar | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1654.9514 | 2010-03-11 | 10 | 845 | 1900-03-11 | 10 | 1181 | 2003-03-11 | 10 | 0 | 1654.9514 | 718.0229 | 230.5%
CE545 | 1.8119e-11 | 01-Jul | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2784e-12 | 2010-05-23 | 15 | 4 | 1900-07-20 | 15 | 0 | 2003-01-01 | 1 | 0 | 4 | 0.66667 | 600%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-12. Hourly Integrated Maxima and Minima (COP2)
Maximum COP2 | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 4.1683 | 16-Apr | 3 | 3.869 | 2002-04-30 | 16 | 3.857 | 2002-04-30 | 16 | 3.9252 | 2010-04-30 | 15 | 3.8706 | 1900-04-30 | 16 | 3.88 | 2003-04-30 | 16 | 3.857 | 4.1683 | 3.9284 | 7.925%
CE310 | 4.1433 | 30-Apr | 15 | 4.141 | 2002-04-30 | 16 | 4.128 | 2002-04-30 | 16 | 4.1729 | 2010-04-30 | 15 | 4.1276 | 1900-04-30 | 15 | 4.12 | 2003-04-30 | 15 | 4.12 | 4.1729 | 4.1388 | 1.278%
CE320 | 4.1683 | 16-Apr | 3 | 5.143 | 2002-10-02 | 9 | 4.967 | 2002-10-02 | 9 | 3.9395 | 2010-09-16 | 15 | 3.9433 | 1900-09-16 | 15 | 4.38 | 2003-12-18 | 3 | 3.9395 | 5.143 | 4.4235 | 27.21%
CE330 | 4.1683 | 16-Apr | 3 | 4.109 | 2003-06-17 | 16 | 5.595 | 2002-10-02 | 9 | 4.0715 | 2010-09-16 | 14 | 4.1219 | 1900-06-17 | 16 | 4.05 | 2003-06-17 | 16 | 4.05 | 5.595 | 4.3526 | 35.5%
CE340 | 4.1683 | 16-Apr | 3 | 4.621 | 2002-10-02 | 9 | 5.339 | 2002-10-02 | 9 | 3.9866 | 2010-09-16 | 15 | 4.0172 | 1900-09-16 | 16 | 3.95 | 2003-09-16 | 16 | 3.95 | 5.339 | 4.347 | 31.95%
CE350 | 4.1683 | 16-Apr | 3 | 3.889 | 2003-04-27 | 5 | 3.863 | 2004-10-05 | 3 | 4.5552 | 2010-10-13 | 1 | 3.9321 | 1900-10-04 | 24 | 3.88 | 2003-04-30 | 16 | 3.863 | 4.5552 | 4.0479 | 17.1%
CE360 | 4.401 | 05-Oct | 1 | 4.428 | 2002-10-04 | 24 | 4.427 | 2002-10-04 | 24 | 4.4554 | 2010-10-04 | 24 | 4.432 | 1900-10-04 | 24 | 4.44 | 2003-10-04 | 24 | 4.401 | 4.4554 | 4.4306 | 1.228%
CE400 | 4.0769 | 16-Sep | 15 | 4.088 | 2003-06-17 | 16 | 4.776 | 2003-09-18 | 15 | 4.0715 | 2010-09-16 | 14 |  |  |  | 4.05 | 2003-06-17 | 16 | 4.05 | 4.776 | 4.2125 | 17.23%
CE410 | 3.8879 | 30-Apr | 15 | 3.903 | 2002-04-30 | 15 | 3.855 | 2002-04-30 | 16 | [6 empty] | 3.84 | 2003-05-21 | 15 | 3.84 | 3.903 | 3.8715 | 1.627%
CE420 | 3.7813 | 27-Sep | 16 | 3.807 | 2003-05-21 | 15 | 3.759 | 2003-09-27 | 15 | 3.8214 | 2010-05-21 | 15 |  |  |  | 3.94 | 2003-05-21 | 13 | 3.759 | 3.94 | 3.8217 | 4.736%
CE430 | 3.7813 | 27-Sep | 16 | 3.805 | 2003-10-24 | 15 | 3.759 | 2003-09-27 | 15 | 3.7927 | 2010-05-21 | 16 |  |  |  | 3.93 | 2003-04-30 | 13 | 3.759 | 3.93 | 3.8136 | 4.484%
CE440 | 3.8835 | 12-Dez | 7 | 3.774 | 2002-09-27 | 15 | 3.759 | 2002-09-27 | 15 | 3.8018 | 2010-05-21 | 15 |  |  |  | 3.81 | 2003-04-30 | 15 | 3.759 | 3.8835 | 3.8057 | 3.271%
CE500 | 4.2751 | 13-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.198 | 2010-03-16 | 10 | 4.1846 | 1900-03-16 | 10 | 4.14 | 2003-04-30 | 16 | 4.14 | 7.367 | 4.911 | 65.71%
CE510 | 4.6925 | 05-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.6847 | 2010-10-05 | 1 | 4.6896 | 1900-10-04 | 24 | 4.53 | 2003-05-04 | 3 | 4.53 | 7.367 | 5.2108 | 54.44%
CE520 | 3.8137 | 30-Apr | 15 | 4.896 | 2004-03-16 | 10 | 4.652 | 2003-03-16 | 10 | 3.9377 | 2010-04-30 | 15 | 3.8017 | 1900-04-30 | 16 | 3.84 | 2003-04-30 | 16 | 3.8017 | 4.896 | 4.1569 | 26.32%
CE522 | 3.9855 | 16-Mar | 10 | 6.233 | 2004-03-11 | 10 | 5.678 | 2004-03-11 | 10 | 4.0424 | 2010-04-30 | 15 | 3.9858 | 1900-04-30 | 16 | 4 | 2003-04-30 | 16 | 3.9855 | 6.233 | 4.6541 | 48.29%
CE525 | 4.7178 | 13-Oct | 1 | 6.325 | 2004-04-12 | 9 | 6.031 | 2004-03-16 | 10 | 4.704 | 2010-03-16 | 10 | 4.6381 | 1900-03-16 | 10 | 4.4 | 2003-03-16 | 10 | 4.4 | 6.325 | 5.136 | 37.48%
CE530 | 4.0061 | 02-Nov | 1 | 3.981 | 2004-03-11 | 10 | 3.85 | 2004-10-13 | 9 | 3.925 | 2010-03-16 | 10 | 3.84 | 1900-03-16 | 10 | 3.88 | 2003-03-16 | 10 | 3.84 | 4.0061 | 3.9137 | 4.242%
CE540 | 3.456 | 30-Apr | 15 | 3.456 | 2004-04-30 | 16 | 3.455 | 2004-04-30 | 16 | 3.6959 | 2010-03-16 | 10 | 3.6667 | 1900-03-11 | 22 | 3.69 | 2003-10-17 | 5 | 3.455 | 3.6959 | 3.5699 | 6.748%
CE545 | 4.2505 | 16-Mar | 10 | 4.275 | 2004-03-16 | 10 | 4.428 | 2004-03-16 | 10 | 4.1661 | 2010-03-16 | 10 | 4.1565 | 1900-03-16 | 10 | 4.17 | 2003-03-16 | 10 | 4.1565 | 4.428 | 4.241 | 6.402%
Minimum COP2 | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 2.7931 | 24-Apr | 17 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7815 | 2010-06-13 | 17 | 2.7856 | 1900-06-13 | 17 | 2.81 | 2003-06-14 | 12 | 2.7815 | 2.81 | 2.7949 | 1.019%
CE310 | 2.8652 | 01-Dec | 15 | 2.85 | 2002-12-01 | 14 | 2.851 | 2002-12-01 | 12 | 2.8927 | 2010-12-01 | 15 | 2.8726 | 1900-12-01 | 15 | 2.87 | 2003-12-01 | 14 | 2.85 | 2.8927 | 2.8669 | 1.488%
CE320 | 2.8252 | 31-Mar | 14 | 2.801 | 2002-12-01 | 14 | 2.805 | 2003-12-01 | 15 | 2.8415 | 2010-03-31 | 15 | 2.8145 | 1900-03-31 | 15 | 2.83 | 2003-03-31 | 14 | 2.801 | 2.8415 | 2.8195 | 1.437%
CE330 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8441 | 2010-03-31 | 15 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 2.798 | 2.8441 | 2.8219 | 1.633%
CE340 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8441 | 2010-03-31 | 15 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 2.798 | 2.8441 | 2.8219 | 1.633%
CE350 | 2.7904 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7815 | 2010-06-13 | 17 | 2.7859 | 1900-06-13 | 17 | 2.81 | 2003-06-14 | 12 | 2.7815 | 2.81 | 2.7945 | 1.019%
CE360 | 2.8252 | 31-Mar | 14 | 2.799 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8441 | 2010-03-31 | 15 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 2.799 | 2.8441 | 2.8221 | 1.598%
CE400 | 2.7819 | 31-Mar | 19 | 2.734 | 2002-12-03 | 15 | 2.735 | 2003-12-03 | 13 | 2.7815 | 2010-06-13 | 17 |  |  |  | 2.81 | 2003-06-14 | 12 | 2.734 | 2.81 | 2.7685 | 2.745%
CE410 | 2.7858 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | [6 empty] | 2.81 | 2003-06-14 | 12 | 2.7858 | 2.81 | 2.7987 | 0.8635%
CE420 | 2.7931 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7815 | 2010-06-13 | 17 |  |  |  | 2.81 | 2003-06-14 | 12 | 2.7815 | 2.81 | 2.7967 | 1.018%
CE430 | 2.7711 | 30-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7815 | 2010-06-13 | 17 |  |  |  | 2.81 | 2003-06-14 | 12 | 2.734 | 2.81 | 2.7663 | 2.747%
CE440 | 2.7825 | 31-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7815 | 2010-06-13 | 17 |  |  |  | 2.81 | 2003-04-08 | 13 | 2.734 | 2.81 | 2.7686 | 2.745%
CE500 | 2.6852 | 30-Jul | 12 | 2.693 | 2002-07-29 | 12 | 2.652 | 2004-03-30 | 17 | 2.7055 | 2010-07-30 | 12 | 2.6665 | 1900-07-30 | 12 | 2.71 | 2003-07-29 | 12 | 2.652 | 2.71 | 2.6854 | 2.16%
CE510 | 2.888 | 31-Mar | 15 | 2.817 | 2004-04-05 | 17 | 2.652 | 2004-03-30 | 17 | 2.8653 | 2010-03-31 | 18 | 2.8817 | 1900-03-31 | 15 | 2.9 | 2003-03-31 | 14 | 2.652 | 2.9 | 2.834 | 8.751%
CE520 | 2.4417 | 30-Jul | 12 | 2.463 | 2004-04-05 | 17 | 2.394 | 2004-04-05 | 17 | 2.5316 | 2010-07-30 | 12 | 2.3333 | 1900-01-28 | 10 | 2.47 | 2003-07-30 | 12 | 2.3333 | 2.5316 | 2.4389 | 8.131%
CE522 | 2.5689 | 08-Jul | 17 | 2.572 | 2002-07-29 | 12 | 2.562 | 2004-03-31 | 17 | 2.6134 | 2010-07-30 | 12 | 2.4286 | 1900-03-30 | 17 | 2.59 | 2003-07-29 | 12 | 2.4286 | 2.6134 | 2.5558 | 7.231%
CE525 | 2.9111 | 14-Jul | 17 | 2.939 | 2003-07-30 | 12 | 2.814 | 2004-03-31 | 17 | 2.9396 | 2010-07-30 | 12 | 2.8941 | 1900-07-29 | 12 | 2.9 | 2003-07-29 | 12 | 2.814 | 2.9396 | 2.8996 | 4.332%
CE530 | 2.5013 | 30-Jul | 12 | 2.495 | 2002-07-29 | 12 | 2.498 | 2002-07-29 | 12 | 2.532 | 2010-07-30 | 12 | 2.4733 | 1900-07-29 | 12 | 2.52 | 2003-07-29 | 12 | 2.4733 | 2.532 | 2.5033 | 2.344%
CE540 | 2.253 | 30-Jul | 12 | 2.261 | 2003-07-29 | 12 | 2.262 | 2012-07-30 | 12 | 2.3828 | 2010-07-30 | 12 | 2.1429 | 1900-04-05 | 20 | 2.28 | 2003-07-29 | 12 | 2.1429 | 2.3828 | 2.2636 | 10.6%
CE545 | 2.7325 | 14-Jul | 17 | 2.72 | 2003-07-29 | 12 | 2.722 | 2002-07-30 | 12 | 2.66 | 2010-07-30 | 12 | 2.692 | 1900-07-29 | 12 | 2.72 | 2003-07-29 | 12 | 2.66 | 2.7325 | 2.7078 | 2.681%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-13. Hourly Integrated Maxima and Minima (IDB)
Maximum IDB (°C) | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0025 | 2010-09-23 | 8 | 25.05 | 1900-02-20 | 17 | 26.19 | 2003-11-03 | 15 | 25.0025 | 26.1999 | 25.4437 | 4.706%
CE310 | 27.0778 | 20-Jul | 15 | 26.89 | 2004-07-20 | 16 | 26.72 | 2002-07-20 | 16 | 26.4747 | 2010-07-20 | 16 | 26.62 | 1900-07-20 | 15 | 27.19 | 2003-07-08 | 15 | 26.4747 | 27.19 | 26.8287 | 2.666%
CE320 | 32.3604 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.5 | 2003-07-08 | 16 | 31.7089 | 2010-07-20 | 15 | 32.32 | 1900-07-20 | 15 | 31.65 | 2003-07-08 | 15 | 31.5 | 32.3604 | 31.8582 | 2.701%
CE330 | 32.2321 | 20-Jul | 15 | 31.72 | 2004-07-08 | 16 | 32 | 2003-07-20 | 16 | 31.0686 | 2010-07-08 | 16 | 31.9 | 1900-07-20 | 15 | 31.3 | 2003-07-08 | 15 | 31.0686 | 32.2321 | 31.7035 | 3.67%
CE340 | 32.3066 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.56 | 2003-07-08 | 16 | 31.4977 | 2010-07-20 | 15 | 32.15 | 1900-07-20 | 15 | 31.58 | 2003-07-08 | 15 | 31.4977 | 32.3066 | 31.7841 | 2.545%
CE350 | 34.5841 | 01-Oct | 24 | 34.94 | 2003-06-23 | 24 | 34.94 | 2004-06-24 | 24 | 35.0021 | 2010-10-01 | 2 | 35 | 1900-04-21 | 1 | 35 | 2003-04-21 | 2 | 34.5841 | 35.0021 | 34.911 | 1.197%
CE360 | 33.7585 | 10-Jul | 13 | 32.78 | 2002-07-20 | 15 | 32.56 | 2004-07-20 | 16 | 32.5106 | 2010-07-10 | 13 | 33 | 1900-07-20 | 15 | 33.13 | 2003-07-10 | 12 | 32.5106 | 33.7585 | 32.9565 | 3.787%
CE400 | 27.1148 | 16-Sep | 15 | 27.56 | 2003-09-16 | 16 | 28.83 | 2002-09-18 | 16 | 26.9099 | 2010-09-16 | 16 |  |  |  | 26.04 | 2003-08-15 | 15 | 26.04 | 28.83 | 27.2909 | 10.22%
CE410 | 26.8256 | 23-Oct | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | [6 empty] | 26.19 | 2003-11-03 | 15 | 25.11 | 26.8256 | 25.8089 | 6.647%
CE420 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0025 | 2010-09-23 | 8 |  |  |  | 26.23 | 2003-10-20 | 15 | 25.0025 | 26.23 | 25.5305 | 4.808%
CE430 | 27.1992 | 01-Nov | 16 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.003 | 2010-05-18 | 19 |  |  |  | 26.45 | 2003-10-23 | 15 | 25.003 | 27.1992 | 25.7744 | 8.521%
CE440 | 27.0452 | 28-Apr | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.003 | 2010-04-24 | 19 |  |  |  | 26.26 | 2003-10-23 | 15 | 25.003 | 27.0452 | 25.7056 | 7.945%
CE500 | 25.8054 | 30-Apr | 15 | 25.11 | 2001-04-21 | 16 | 25.11 | 2001-04-21 | 16 | 24.9998 | 2010-03-31 | 18 | 25.02 | 1900-03-30 | 17 | 25 | 2003-03-11 | 11 | 24.9998 | 25.8054 | 25.1742 | 3.2%
CE510 | 26.1003 | 09-Jul | 15 | 25.11 | 2001-04-21 | 3 | 25.11 | 2001-04-21 | 3 | 24.9998 | 2010-03-31 | 18 | 25.02 | 1900-03-30 | 17 | 25 | 2003-04-24 | 12 | 24.9998 | 26.1003 | 25.2234 | 4.363%
CE520 | 16.1232 | 15-Aug | 15 | 16.11 | 2002-08-16 | 16 | 15.94 | 2004-07-10 | 16 | 15.0005 | 2010-04-16 | 1 | 15.98 | 1900-07-20 | 15 | 18.62 | 2003-06-04 | 16 | 15.0005 | 18.62 | 16.2956 | 22.21%
CE522 | 21.0091 | 16-Jul | 15 | 20.11 | 2001-04-21 | 15 | 20.11 | 2003-04-21 | 15 | 20.0004 | 2010-04-16 | 20 | 20.05 | 1900-03-13 | 22 | 20.93 | 2003-04-21 | 15 | 20.0004 | 21.0091 | 20.3683 | 4.952%
CE525 | 36.08 | 10-Mai | 16 | 35.06 | 2003-04-21 | 16 | 35.06 | 2003-04-21 | 16 | 34.9995 | 2010-03-11 | 12 | 35 | 1900-03-11 | 10 | 35 | 2003-03-11 | 11 | 34.9995 | 36.08 | 35.1999 | 3.07%
CE530 | 26.116 | 04-Jun | 15 | 25.06 | 2001-04-21 | 16 | 25.06 | 2001-04-21 | 16 | 25.0003 | 2010-03-30 | 17 | 25.02 | 1900-03-30 | 17 | 25 | 2003-03-11 | 11 | 25 | 26.116 | 25.2094 | 4.427%
CE540 | 16.1465 | 21-Sep | 16 | 15.11 | 2004-05-31 | 16 | 15.11 | 2004-05-31 | 16 | 15.0005 | 2010-03-25 | 8 | 15.05 | 1900-01-27 | 20 | 15 | 2003-03-11 | 10 | 15 | 16.1465 | 15.2362 | 7.525%
CE545 | 35.6715 | 20-Jul | 15 | 35 | 2003-04-21 | 15 | 35 | 2004-04-21 | 15 | 35 | 2010-07-09 | 22 | 35 | 1900-03-11 | 10 | 35 | 2003-03-11 | 11 | 35 | 35.6715 | 35.1119 | 1.912%
Minimum IDB (°C) | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.2263 | 23.1%
CE310 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7174 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.2262 | 23.1%
CE320 | 7.93 | 06-Jan | 6 | 10.83 | 2001-01-06 | 7 | 10.78 | 2001-01-06 | 7 | 7.7537 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 10.83 | 8.714 | 44.07%
CE330 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.716 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.226 | 23.1%
CE340 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.716 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.226 | 23.1%
CE350 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.2263 | 23.1%
CE360 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7177 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.2263 | 23.1%
CE400 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.2715 | 22.97%
CE410 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | [6 empty] | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.16 | 23.28%
CE420 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.2715 | 22.97%
CE430 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 8.2715 | 22.97%
CE440 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | 7 | 2003-01-06 | 5 | 7 | 8.89 | 8.2735 | 22.84%
CE500 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9388 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | 24.04 | 2003-04-15 | 5 | 7.94 | 24.04 | 11.0093 | 146.2%
CE510 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9388 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | 24.04 | 2003-04-15 | 5 | 7.94 | 24.04 | 11.0093 | 146.2%
CE520 | 8.3053 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.835 | 2010-12-21 | 1 | 8.51 | 1900-12-20 | 20 | 13.57 | 2003-11-01 | 7 | 7.89 | 13.57 | 9.2034 | 61.72%
CE522 | 8.4141 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.8978 | 2010-12-21 | 1 | 8.54 | 1900-12-20 | 20 | 15.98 | 2003-04-12 | 19 | 7.94 | 15.98 | 9.657 | 83.26%
CE525 | 8.4442 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 9.0147 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | 33.01 | 2003-04-01 | 8 | 7.94 | 33.01 | 12.5198 | 200.2%
CE530 | 8.4215 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9381 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | 24.04 | 2003-04-15 | 5 | 7.94 | 24.04 | 11.0083 | 146.3%
CE540 | 8.2278 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.8327 | 2010-12-21 | 1 | 8.51 | 1900-12-20 | 20 | 14.95 | 2003-12-19 | 1 | 7.89 | 14.95 | 9.4201 | 74.95%
CE545 | 8.4486 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 9.0132 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | 33.01 | 2003-04-01 | 8 | 7.94 | 33.01 | 12.5203 | 200.2%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-14. Hourly Integrated Maxima and Minima (Zone Humidity Ratio)
Maximum Humidity Ratio | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 0.013284 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.013626 | 2010-11-16 | 17 | 0.013457 | 1900-11-16 | 16 | 0.0134 | 2003-11-16 | 16 | 0.013284 | 0.0138 | 0.013545 | 3.807%
CE310 | 0.01575 | 01-Oct | 23 | 0.0188 | 2002-10-15 | 9 | 0.0189 | 2002-10-15 | 9 | 0.015637 | 2010-10-01 | 8 | 0.015432 | 1900-10-02 | 8 | 0.0157 | 2003-10-02 | 8 | 0.015432 | 0.0189 | 0.016703 | 20.76%
CE320 | 0.018017 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0176 | 2002-07-10 | 12 | 0.017807 | 2010-07-10 | 13 | 0.017547 | 1900-07-10 | 12 | 0.0177 | 2003-07-10 | 12 | 0.017547 | 0.018017 | 0.017729 | 2.651%
CE330 | 0.017651 | 10-Jul | 12 | 0.0178 | 2003-10-02 | 9 | 0.0177 | 2002-07-10 | 13 | 0.017934 | 2010-07-10 | 12 | 0.017045 | 1900-07-10 | 13 | 0.0177 | 2003-07-10 | 12 | 0.017045 | 0.017934 | 0.017638 | 5.038%
CE340 | 0.017871 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0174 | 2002-07-10 | 12 | 0.017787 | 2010-07-10 | 12 | 0.017272 | 1900-07-10 | 13 | 0.0177 | 2003-07-10 | 12 | 0.017272 | 0.017871 | 0.017622 | 3.401%
CE350 | 0.016758 | 01-Oct | 24 | 0.0199 | 2002-08-02 | 22 | 0.0199 | 2002-08-02 | 22 | 0.01719 | 2010-10-02 | 1 | 0.016479 | 1900-10-02 | 2 | 0.0166 | 2003-10-02 | 1 | 0.016479 | 0.0199 | 0.017805 | 19.21%
CE360 | 0.013433 | 10-Jul | 13 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01386 | 2010-07-10 | 13 | 0.013457 | 1900-11-16 | 16 | 0.0134 | 2003-11-16 | 16 | 0.0134 | 0.01386 | 0.013608 | 3.382%
CE400 | 0.016944 | 05-Apr | 22 | 0.017 | 2002-04-05 | 21 | 0.017 | 2003-04-05 | 21 | 0.016876 | 2010-04-05 | 22 |  |  |  | 0.0173 | 2003-04-22 | 6 | 0.016876 | 0.0173 | 0.017024 | 2.489%
CE410 | 0.016835 | 05-Apr | 22 | 0.0169 | 2002-04-02 | 5 | 0.0169 | 2002-04-02 | 5 | [6 empty] | 0.0173 | 2003-04-22 | 6 | 0.016835 | 0.0173 | 0.016984 | 2.735%
CE420 | 0.014297 | 02-Apr | 10 | 0.0147 | 2003-04-01 | 21 | 0.0141 | 2002-04-17 | 3 | 0.014593 | 2010-04-02 | 18 |  |  |  | 0.0147 | 2003-04-02 | 18 | 0.0141 | 0.0147 | 0.014478 | 4.144%
CE430 | 0.016231 | 02-Apr | 5 | 0.0156 | 2002-04-02 | 4 | 0.0156 | 2003-04-02 | 4 | 0.016135 | 2010-04-02 | 5 |  |  |  | 0.0158 | 2003-04-02 | 5 | 0.0156 | 0.016231 | 0.015873 | 3.973%
CE440 | 0.013313 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.013626 | 2010-11-16 | 17 |  |  |  | 0.0134 | 2003-11-16 | 16 | 0.013313 | 0.0138 | 0.013568 | 3.591%
CE500 | 0.01172 | 11-Jul | 15 | 0.0119 | 2004-07-20 | 15 | 0.0118 | 2004-04-06 | 10 | 0.011685 | 2010-07-20 | 15 | 0.011713 | 1900-07-20 | 15 | 0.0115 | 2003-03-11 | 10 | 0.0115 | 0.0119 | 0.01172 | 3.413%
CE510 | 0.011871 | 07-Sep | 15 | 0.0119 | 2001-07-20 | 15 | 0.0119 | 2001-07-20 | 15 | 0.011689 | 2010-07-20 | 15 | 0.011716 | 1900-07-20 | 15 | 0.0115 | 2003-03-11 | 10 | 0.0115 | 0.0119 | 0.011763 | 3.401%
CE520 | 0.0075403 | 07-Sep | 15 | 0.0077 | 2004-07-10 | 16 | 0.0078 | 2004-03-29 | 10 | 0.0070236 | 2010-07-20 | 15 | 0.007566 | 1900-07-20 | 15 | 0.0106 | 2003-01-05 | 16 | 0.0070236 | 0.0106 | 0.0080383 | 44.49%
CE522 | 0.0094264 | 20-Jul | 16 | 0.0095 | 2003-06-04 | 15 | 0.0138 | 2004-04-06 | 10 | 0.009111 | 2010-07-20 | 15 | 0.009398 | 1900-07-20 | 15 | 0.0107 | 2003-01-01 | 2 | 0.009111 | 0.0138 | 0.010323 | 45.43%
CE525 | 0.017932 | 10-Mai | 16 | 0.018 | 2004-07-20 | 15 | 0.018 | 2002-07-20 | 15 | 0.018486 | 2010-07-20 | 15 | 0.017626 | 1900-07-20 | 15 | 0.0173 | 2003-07-20 | 15 | 0.0173 | 0.018486 | 0.017891 | 6.629%
CE530 | 0.0069892 | 01-Jan | 1 | 0.0081 | 2001-07-20 | 15 | 0.0081 | 2004-07-20 | 15 | 0.0067755 | 2010-03-11 | 1 | 0.005491 | 1900-04-01 | 1 | 0.00677 | 2003-10-26 | 9 | 0.005491 | 0.0081 | 0.0070376 | 37.07%
CE540 | 0.006084 | 01-Jan | 1 | 0.005 | 2003-06-04 | 13 | 0.0063 | 2004-04-08 | 8 | 0.0067755 | 2010-03-11 | 1 | 0.003256 | 1900-04-01 | 1 | 0.00634 | 2003-03-11 | 9 | 0.003256 | 0.0067755 | 0.0056259 | 62.56%
CE545 | 0.0069892 | 01-Jan | 1 | 0.0122 | 2004-07-20 | 15 | 0.0122 | 2004-07-20 | 15 | 0.0067755 | 2010-12-31 | 7 | 0.006689 | 1900-04-01 | 1 | 0.00763 | 2003-11-05 | 9 | 0.006689 | 0.0122 | 0.0087473 | 63%
Minimum Humidity Ratio | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018571 | 14.54%
CE310 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019433 | 2010-01-05 | 7 | 0.002019 | 1900-01-04 | 7 | 0.00196 | 2003-01-05 | 7 | 0.0017 | 0.002019 | 0.0018665 | 17.09%
CE320 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019336 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018581 | 14.53%
CE330 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018571 | 14.54%
CE340 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018571 | 14.54%
CE350 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018571 | 14.54%
CE360 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018571 | 14.54%
CE400 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018349 | 14.71%
CE410 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | [6 empty] | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018117 | 14.9%
CE420 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018349 | 14.71%
CE430 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 0.0018349 | 14.71%
CE440 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | 0.00197 | 2003-01-05 | 7 | 0.0017 | 0.00197 | 0.0018349 | 14.71%
CE500 | 0.0068276 | 20-Dec | 22 | [6 empty] | 0.0070048 | 2010-12-20 | 12 | 0.006908 | 1900-12-20 | 20 | 0.0103 | 2003-11-02 | 2 | 0.0068276 | 0.0103 | 0.0077601 | 44.75%
CE510 | 0.0068276 | 20-Dec | 22 | [6 empty] | 0.0070048 | 2010-12-20 | 12 | 0.006908 | 1900-12-20 | 20 | 0.0105 | 2003-04-02 | 22 | 0.0068276 | 0.0105 | 0.0078101 | 47.02%
CE520 | 0.006103 | 26-Nov | 2 | [6 empty] | 0.0065213 | 2010-11-10 | 9 | 0.006525 | 1900-11-27 | 23 | 0.00657 | 2003-11-01 | 7 | 0.006103 | 0.00657 | 0.0064298 | 7.264%
CE522 | 0.0068215 | 20-Dec | 22 | [6 empty] | 0.0069847 | 2010-12-20 | 12 | 0.006908 | 1900-12-20 | 20 | 0.00783 | 2003-04-02 | 21 | 0.0068215 | 0.00783 | 0.007136 | 14.13%
CE525 | 0.0068356 | 20-Dec | 22 | [6 empty] | 0.0070421 | 2010-12-20 | 12 | 0.006909 | 1900-12-20 | 20 | 0.0154 | 2003-11-02 | 2 | 0.0068356 | 0.0154 | 0.0090467 | 94.67%
CE530 | 0.006208 | 01-Apr | 1 | [6 empty] | 0.0067348 | 2010-10-18 | 12 | 0.005454 | 1900-11-01 | 21 | 0.00663 | 2003-04-01 | 5 | 0.005454 | 0.0067348 | 0.0062567 | 20.47%
CE540 | 0.0041096 | 05-Oct | 3 | [6 empty] | 0.0038186 | 2010-10-18 | 9 | 0.003253 | 1900-04-29 | 23 | 0.0042 | 2003-10-15 | 5 | 0.003253 | 0.0042 | 0.0038453 | 24.63%
CE545 | 0.006208 | 01-Apr | 1 | [6 empty] | 0.0067755 | 2010-04-01 | 2 | 0.006685 | 1900-07-20 | 15 | 0.007 | 2003-04-01 | 8 | 0.006208 | 0.007 | 0.0066671 | 11.88%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-15. Hourly Integrated Maxima and Minima (Relative Humidity)
Maximum Relative Humidity | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 68.3673 | 2010-11-16 | 17 | 68 | 1900-11-16 | 16 | 67.44 | 2003-11-16 | 16 | 67.44 | 69.35 | 68.4661 | 2.79%
CE310 | 77.7029 | 02-Oct | 4 | 100.18 | 2002-10-15 | 9 | 100.7 | 2002-10-15 | 9 | 78.6439 | 2010-10-02 | 8 | 77 | 1900-06-12 | 8 | 78.19 | 2003-10-02 | 8 | 77 | 100.7 | 85.4028 | 27.75%
CE320 | 81.8358 | 18-Sep | 10 | 83.41 | 2004-10-02 | 9 | 83.67 | 2003-04-22 | 18 | 82.9666 | 2010-09-18 | 10 | 83 | 1900-09-03 | 17 | 81.88 | 2003-09-16 | 20 | 81.8358 | 83.67 | 82.7937 | 2.215%
CE330 | 76.6591 | 22-Sep | 20 | 78.46 | 2004-10-02 | 9 | 77.94 | 2003-09-18 | 9 | 76.8755 | 2010-09-03 | 10 | 76 | 1900-06-10 | 18 | 78.7 | 2003-09-02 | 12 | 76 | 78.7 | 77.4391 | 3.487%
CE340 | 79.9293 | 18-Sep | 10 | 81.37 | 2004-09-18 | 9 | 81.26 | 2003-04-22 | 18 | 80.796 | 2010-09-18 | 10 | 80 | 1900-09-03 | 17 | 80.25 | 2003-09-16 | 20 | 79.9293 | 81.37 | 80.6009 | 1.787%
CE350 | 68.7892 | 16-Nov | 17 | 81.12 | 2003-08-07 | 21 | 81.12 | 2003-08-07 | 21 | 68.3673 | 2010-11-16 | 17 | 70 | 1900-10-02 | 8 | 72.65 | 2003-08-03 | 7 | 68.3673 | 81.12 | 73.6744 | 17.31%
CE360 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 68.3671 | 2010-11-16 | 17 | 68 | 1900-11-16 | 16 | 67.44 | 2003-11-16 | 16 | 67.44 | 69.35 | 68.4661 | 2.79%
CE400 | 83.7534 | 05-Apr | 22 | 85.57 | 2002-04-05 | 21 | 85.57 | 2003-04-05 | 21 | 84.6363 | 2010-04-05 | 22 |  |  |  | 86.31 | 2003-04-22 | 6 | 83.7534 | 86.31 | 85.1679 | 3.002%
CE410 | 83.2247 | 05-Apr | 22 | 84.79 | 2002-04-02 | 5 | 84.79 | 2002-04-02 | 5 | [6 empty] | 86.18 | 2003-04-22 | 6 | 83.2247 | 86.18 | 84.7462 | 3.487%
CE420 | 70.8411 | 02-Apr | 10 | 74.51 | 2003-04-17 | 7 | 71.53 | 2002-04-17 | 3 | 73.284 | 2010-04-02 | 18 |  |  |  | 73.85 | 2003-04-02 | 18 | 70.8411 | 74.51 | 72.803 | 5.039%
CE430 | 80.7087 | 02-Apr | 5 | 78.43 | 2002-04-02 | 4 | 78.43 | 2003-04-02 | 4 | 80.7427 | 2010-04-02 | 5 |  |  |  | 78.94 | 2003-04-02 | 5 | 78.43 | 80.7427 | 79.4503 | 2.911%
CE440 | 68.7242 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 68.3673 | 2010-11-16 | 17 |  |  |  | 67.51 | 2003-11-16 | 16 | 67.51 | 69.35 | 68.5603 | 2.684%
CE500 | 100 | 21-Nov | 24 | [6 empty] | 100 | 2010-11-21 | 9 | 100 | 1900-11-14 | 5 | 60.08 | 2003-04-01 | 5 | 60.08 | 100 | 90.02 | 44.35%
CE510 | 100 | 21-Nov | 24 | [6 empty] | 100 | 2010-11-21 | 9 | 100 | 1900-11-14 | 5 | 57.51 | 2003-04-01 | 5 | 57.51 | 100 | 89.3775 | 47.54%
CE520 | 90.2299 | 20-Dec | 22 | [6 empty] | 93.8137 | 2010-12-20 | 11 | 95 | 1900-12-20 | 17 | 71.77 | 2003-08-16 | 17 | 71.77 | 95 | 87.7034 | 26.49%
CE522 | 100 | 18-Dec | 8 | [6 empty] | 100 | 2010-12-15 | 22 | 100 | 1900-12-15 | 1 | 71.32 | 2003-04-05 | 17 | 71.32 | 100 | 92.83 | 30.9%
CE525 | 100 | 12-Nov | 20 | [6 empty] | 100 | 2010-11-12 | 19 | 100 | 1900-11-11 | 23 | 51.12 | 2003-04-01 | 8 | 51.12 | 100 | 87.78 | 55.68%
CE530 | 91.0445 | 20-Dec | 22 | [6 empty] | 96.1602 | 2010-12-20 | 11 | 79 | 1900-12-20 | 8 | 36.01 | 2003-04-20 | 21 | 36.01 | 96.1602 | 75.5537 | 79.61%
CE540 | 61.275 | 20-Dec | 22 | [6 empty] | 55.1794 | 2010-12-20 | 11 | 47 | 1900-12-20 | 6 | 39.96 | 2003-04-18 | 18 | 39.96 | 61.275 | 50.8536 | 41.91%
CE545 | 90.8772 | 20-Dec | 22 | [6 empty] | 96.2348 | 2010-12-20 | 11 | 97 | 1900-12-20 | 4 | 24.14 | 2003-12-24 | 1 | 24.14 | 97 | 77.063 | 94.55%
Minimum Relative Humidity | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | EnergyPlus |  |  | CODYRUN |  |  | HOT3000 | [5 empty] | (Max-Min) |  | Tested Prg
Case | TUD | Date | Hour | [6 empty] | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | Mean | /Mean* |  | Org | Date | Hour
CE300 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4023 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 13.6023 | 22.28%
CE310 | 13.3898 | 06-Nov | 6 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 15.5023 | 2010-11-06 | 8 | 16 | 1900-11-06 | 8 | 15.93 | 2003-11-06 | 8 | 11.97 | 16 | 14.127 | 28.53%
CE320 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.6416 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | 12.92 | 2003-12-20 | 5 | 11.97 | 15 | 13.3055 | 22.77%
CE330 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4025 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 13.6023 | 22.28%
CE340 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4025 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 13.6023 | 22.28%
CE350 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4023 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 13.6023 | 22.28%
CE360 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4023 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 13.6022 | 22.28%
CE400 | 13.209 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 2010-11-06 | 6 |  |  |  | 14.57 | 2003-11-06 | 5 | 11.97 | 14.57 | 13.1289 | 19.8%
CE410 | 13.2091 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | [6 empty] | 14.58 | 2003-11-06 | 5 | 11.97 | 14.58 | 12.9323 | 20.18%
CE420 | 13.2099 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9257 | 2010-11-06 | 6 |  |  |  | 14.59 | 2003-11-06 | 5 | 11.97 | 14.59 | 13.1331 | 19.95%
CE430 | 13.2078 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 2010-11-06 | 6 |  |  |  | 14.58 | 2003-11-06 | 5 | 11.97 | 14.58 | 13.1307 | 19.88%
CE440 | 13.2069 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 2010-11-06 | 6 |  |  |  | 14.54 | 2003-11-06 | 5 | 11.97 | 14.54 | 13.1225 | 19.58%
CE500 | 53.4054 | 30-Apr | 15 | [6 empty] | 55.1668 | 2010-04-30 | 4 | 54 | 1900-10-04 | 24 | 52.83 | 2003-10-05 | 1 | 52.83 | 55.1668 | 53.8505 | 4.339%
CE510 | 52.0879 | 04-Oct | 23 | [6 empty] | 55.2884 | 2010-05-04 | 3 | 54 | 1900-10-04 | 23 | 53.15 | 2003-05-04 | 4 | 52.0879 | 55.2884 | 53.6316 | 5.968%
CE520 | 61.2679 | 25-Nov | 24 | [6 empty] | 61.7266 | 2010-11-27 | 24 | 61 | 1900-11-27 | 22 | 61.9 | 2003-07-20 | 15 | 61 | 61.9 | 61.4736 | 1.464%
CE522 | 58.5054 | 30-Apr | 15 | [6 empty] | 59.1798 | 2010-04-30 | 4 | 60 | 1900-10-04 | 23 | 57.97 | 2003-10-05 | 1 | 57.97 | 60 | 58.9138 | 3.446%
CE525 | 45.5284 | 30-Apr | 15 | [6 empty] | 47.8518 | 2010-10-05 | 2 | 44 | 1900-05-04 | 4 | 44.4 | 2003-10-05 | 1 | 44 | 47.8518 | 45.4451 | 8.476%
CE530 | 29.5934 | 04-Jun | 15 | [6 empty] | 34.0277 | 2010-04-18 | 18 | 28 | 1900-04-01 | 10 | 33.68 | 2003-04-01 | 13 | 28 | 34.0277 | 31.3253 | 19.24%
CE540 | 36.4749 | 21-Sep | 16 | [6 empty] | 36.0017 | 2010-09-28 | 16 | 31 | 1900-04-01 | 1 | 39.74 | 2003-10-05 | 1 | 31 | 39.74 | 35.8042 | 24.41%
CE545 | 17.1244 | 20-Jul | 15 | [6 empty] | 19.227 | 2010-04-18 | 17 | 19 | 1900-04-01 | 10 | 20.14 | 2003-04-01 | 12 | 17.1244 | 20.14 | 18.8728 | 15.98%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Table-S
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.2-16. June 28 Hourly Output - Case CE300
| TRNSYS-TUD | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
|  | Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
| Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
| 1 | 2055.7697 | 256.5326 | 8131.73 | 6189.34 | 1942.39 | 0.0090778 | 3.5167 | 18.05 | 23.4068 | 16.9641 | 0.011255
| 2 | 2053.6706 | 256.5271 | 8115.8 | 6201.56 | 1914.24 | 0.0090138 | 3.513 | 18.05 | 23.3748 | 16.9046 | 0.011255
| 3 | 2054.4923 | 256.5356 | 8127.89 | 6194.38 | 1933.51 | 0.0090644 | 3.517 | 18.05 | 23.3833 | 16.9418 | 0.011255
| 4 | 1830.0824 | 229.5857 | 7224.15 | 5548.55 | 1675.6 | 0.0089864 | 3.5074 | 17.8 | 23.3739 | 16.8619 | 0.011075
| 5 | 2029.3426 | 256.394 | 8104.85 | 6318.9 | 1785.95 | 0.0088405 | 3.5458 | 17.5 | 23.3503 | 16.6966 | 0.01061
| 6 | 1839.4317 | 229.5597 | 7130.87 | 5686.24 | 1444.63 | 0.0086578 | 3.4465 | 18.3 | 23.4171 | 16.5734 | 0.010568
| 7 | 2667.2444 | 308.5446 | 9711.38 | 7596.88 | 2114.5 | 0.0091531 | 3.2635 | 22.2 | 24.0395 | 17.3192 | 0.012071
| 8 | 3552.7185 | 384.0455 | 12121.31 | 9558.23 | 2563.08 | 0.0095303 | 3.079 | 26.1 | 24.5724 | 17.7945 | 0.012173
| 9 | 4364.7758 | 458.1014 | 14555.62 | 11757.9 | 2797.72 | 0.0096727 | 3.018 | 28.05 | 25.0937 | 17.973 | 0.011538
| 10 | 4441.0633 | 457.9932 | 14639.38 | 11506.4 | 3132.98 | 0.010058 | 2.9882 | 28.9 | 25.2815 | 18.3972 | 0.012388
| 11 | 4999.595 | 506.3045 | 16374.09 | 12342.2 | 4031.89 | 0.010408 | 2.9739 | 30 | 25.3592 | 18.8246 | 0.013776
| 12 | 5316.7711 | 529.3648 | 17248.4 | 12810 | 4438.4 | 0.010684 | 2.9504 | 30.85 | 25.5877 | 19.1202 | 0.014041
| 13 | 6188.5477 | 616.6094 | 20498.21 | 16816.1 | 3682.11 | 0.010087 | 3.0122 | 30.85 | 26.53 | 18.8377 | 0.012315
| 14 | 6210.9293 | 616.1242 | 20234.06 | 17283.5 | 2950.56 | 0.0097987 | 2.9638 | 31.4 | 26.5617 | 18.5548 | 0.011543
| 15 | 7922.4534 | 781.0016 | 26687.28 | 22882.4 | 3804.88 | 0.0095792 | 3.0663 | 31.95 | 26.7812 | 18.5486 | 0.012069
| 16 | 7964.823 | 781.0124 | 26722.68 | 22284.7 | 4437.98 | 0.0096663 | 3.0555 | 32.2 | 26.5632 | 18.673 | 0.013324
| 17 | 5420.7775 | 529.4985 | 17231.33 | 13048.3 | 4183.03 | 0.01077 | 2.8959 | 31.95 | 26.198 | 19.4032 | 0.014505
| 18 | 5409.9868 | 529.3784 | 17505.88 | 12720.6 | 4785.28 | 0.011184 | 2.9474 | 31.4 | 26.2263 | 19.7724 | 0.015234
| 19 | 5260.0345 | 529.2289 | 17661.69 | 12490.8 | 5170.89 | 0.011131 | 3.0508 | 29.7 | 25.7001 | 19.5753 | 0.015134
| 20 | 4880.3429 | 506.2207 | 16989.81 | 11655.3 | 5334.51 | 0.010991 | 3.1541 | 27.75 | 25.1673 | 19.3718 | 0.015748
| 21 | 3938.7143 | 409.0843 | 13539.94 | 8882.19 | 4657.75 | 0.01114 | 3.1142 | 27.2 | 24.6544 | 19.438 | 0.016886
| 22 | 3923.9563 | 409.5326 | 13564.54 | 8880.28 | 4684.26 | 0.011177 | 3.1302 | 26.95 | 24.7445 | 19.4846 | 0.016863
| 23 | 4122.5716 | 433.8551 | 14531.34 | 9449.35 | 5081.99 | 0.011176 | 3.1892 | 26.4 | 24.6707 | 19.4693 | 0.016867
| 24 | 3877.3845 | 409.5808 | 13691.76 | 8806.54 | 4885.22 | 0.011275 | 3.1938 | 26.1 | 24.7257 | 19.5725 | 0.017112
| DOE-2.2 | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
|  | Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
| Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
| 1 | 1897 | 237 | 7552.3077 | 5889.2583 | 1663.0494 | 0.0094 | 3.539 | 17.7778 | 23.8333 | 17.34 | 0.0114
| 2 | 1941 | 240 | 7630.2723 | 6069.8079 | 1560.4644 | 0.0093 | 3.4985 | 18.3333 | 23.9444 | 17.29 | 0.0112
| 3 | 1897 | 237 | 7550.256 | 5881.3446 | 1668.9114 | 0.0094 | 3.5381 | 17.7778 | 23.8333 | 17.34 | 0.0114
| 4 | 1891 | 237 | 7533.8424 | 5878.1205 | 1655.7219 | 0.0094 | 3.5403 | 17.7778 | 23.8333 | 17.34 | 0.0114
| 5 | 1697 | 215 | 6797.8683 | 5675.2953 | 1122.573 | 0.0089 | 3.5554 | 17.2222 | 23.7778 | 16.85 | 0.0103
| 6 | 2126 | 259 | 8136.1629 | 6438.5277 | 1697.6352 | 0.0092 | 3.4114 | 19.4444 | 24.1111 | 17.3 | 0.0113
| 7 | 3198 | 352 | 11075.9559 | 8342.2122 | 2733.7437 | 0.01 | 3.12 | 25 | 24.9444 | 18.39 | 0.0133
| 8 | 3135 | 332 | 10290.741 | 9069.9795 | 1220.7615 | 0.0094 | 2.9682 | 27.2222 | 25.2778 | 17.78 | 0.0109
| 9 | 4528 | 469 | 14785.7226 | 11872.6017 | 2913.1209 | 0.0099 | 2.9589 | 28.8889 | 25.5556 | 18.36 | 0.0117
| 10 | 4651 | 479 | 15339.9747 | 12039.0825 | 3300.8922 | 0.0103 | 2.9902 | 28.8889 | 25.5556 | 18.68 | 0.0125
| 11 | 5434 | 537 | 17455.2774 | 12811.9872 | 4643.2902 | 0.0109 | 2.9233 | 31.1111 | 25.8889 | 19.48 | 0.0148
| 12 | 5019 | 498 | 16215.1713 | 12612.093 | 3603.0783 | 0.0108 | 2.9391 | 30.5556 | 25.8333 | 19.23 | 0.0134
| 13 | 6040 | 597 | 19722.9921 | 17139.0225 | 2583.9696 | 0.0101 | 2.9717 | 31.1111 | 25.9444 | 18.56 | 0.0115
| 14 | 6420 | 633 | 20808.3414 | 17638.1718 | 3170.1696 | 0.01 | 2.9503 | 31.6667 | 26.0556 | 18.6 | 0.0121
| 15 | 7671 | 751 | 25387.1496 | 22196.463 | 3190.6866 | 0.0098 | 3.0144 | 32.2222 | 26.1111 | 18.46 | 0.0119
| 16 | 8190 | 800 | 27581.0031 | 22527.9591 | 5053.044 | 0.01 | 3.068 | 32.2222 | 26.1667 | 18.84 | 0.0144
| 17 | 5715 | 561 | 18204.7341 | 13599.2538 | 4605.4803 | 0.0107 | 2.9007 | 31.6667 | 26.0556 | 19.35 | 0.0146
| 18 | 5536 | 544 | 17933.3235 | 12829.8663 | 5103.4572 | 0.0112 | 2.9496 | 31.1111 | 25.9444 | 19.75 | 0.0157
| 19 | 4711 | 481 | 16012.053 | 11875.5327 | 4136.5203 | 0.011 | 3.084 | 28.3333 | 25.5 | 19.32 | 0.0143
| 20 | 4859 | 504 | 17082.1611 | 11532.3126 | 5549.8485 | 0.0114 | 3.1852 | 27.2222 | 25.3333 | 19.76 | 0.0164
| 21 | 3913 | 405 | 13435.4109 | 9302.4078 | 4133.0031 | 0.0113 | 3.1115 | 27.2222 | 25.3333 | 19.76 | 0.0164
| 22 | 3825 | 399 | 13280.361 | 8973.5496 | 4306.8114 | 0.0114 | 3.144 | 26.6667 | 25.2222 | 19.8 | 0.0167
| 23 | 3750 | 395 | 13191.8448 | 8787.4311 | 4404.4137 | 0.0115 | 3.1826 | 26.1111 | 25.1111 | 19.84 | 0.0169
| 24 | 3880 | 407 | 13724.4075 | 8799.1551 | 4925.2524 | 0.0117 | 3.2014 | 26.1111 | 25.1111 | 20.14 | 0.0178
Table B16.5.2-16. J u n e 2 8 H o u r l y O u t p u t - C a s e C E 3 0 0 (continued)
| DOE-2.1E-E | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
|  | Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
| Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
| 1 | 1894 | 237 | 7544.9802 | 5886.9135 | 1658.0667 | 0.0094 | 3.5406 | 17.7778 | 23.8333 | 17.34 | 0.0114
| 2 | 1941 | 241 | 7627.0482 | 6067.17 | 1559.8782 | 0.0093 | 3.4954 | 18.3333 | 23.9444 | 17.29 | 0.0112
| 3 | 1894 | 237 | 7546.1526 | 5878.1205 | 1668.0321 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114
| 4 | 1890 | 236 | 7528.2735 | 5873.4309 | 1654.8426 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114
| 5 | 1694 | 215 | 6753.024 | 5671.7781 | 1081.2459 | 0.009 | 3.5375 | 17.2222 | 23.7778 | 16.94 | 0.0103
| 6 | 2133 | 259 | 8185.1106 | 6438.5277 | 1746.5829 | 0.0092 | 3.4219 | 19.4444 | 24.1111 | 17.3 | 0.0113
| 7 | 3223 | 353 | 11232.7644 | 8347.7811 | 2884.9833 | 0.0098 | 3.1412 | 25 | 24.9444 | 18.23 | 0.0133
| 8 | 3145 | 335 | 10271.6895 | 9069.1002 | 1202.5893 | 0.0094 | 2.9516 | 27.2222 | 25.2778 | 17.78 | 0.0109
| 9 | 4526 | 467 | 14844.0495 | 11875.2396 | 2968.8099 | 0.0099 | 2.973 | 28.8889 | 25.5556 | 18.28 | 0.0117
| 10 | 4655 | 478 | 15392.7327 | 12041.1342 | 3351.5985 | 0.0102 | 2.9988 | 28.8889 | 25.5556 | 18.6 | 0.0125
| 11 | 5456 | 536 | 17605.0515 | 12817.5561 | 4787.4954 | 0.0107 | 2.9381 | 31.1111 | 25.8889 | 19.33 | 0.0148
| 12 | 5015 | 498 | 16187.6199 | 12610.9206 | 3576.6993 | 0.0108 | 2.9363 | 30.5556 | 25.8333 | 19.23 | 0.0134
| 13 | 6036 | 600 | 19620.9933 | 17135.2122 | 2485.7811 | 0.0102 | 2.9568 | 31.1111 | 25.9444 | 18.64 | 0.0115
| 14 | 6429 | 635 | 20819.1861 | 17639.0511 | 3180.135 | 0.01 | 2.9472 | 31.6667 | 26.0556 | 18.6 | 0.0121
| 15 | 7683 | 754 | 25392.7185 | 22196.7561 | 3195.9624 | 0.0098 | 3.0097 | 32.2222 | 26.1111 | 18.46 | 0.0119
| 16 | 8222 | 803 | 27721.1049 | 22533.2349 | 5187.87 | 0.0098 | 3.0716 | 32.2222 | 26.1667 | 18.76 | 0.0144
| 17 | 5696 | 556 | 18244.5957 | 13600.1331 | 4644.4626 | 0.0107 | 2.9182 | 31.6667 | 26.0556 | 19.35 | 0.0146
| 18 | 5531 | 541 | 17977.8747 | 12831.6249 | 5146.2498 | 0.0112 | 2.9608 | 31.1111 | 25.9444 | 19.68 | 0.0157
| 19 | 4689 | 479 | 15914.4507 | 11871.1362 | 4043.3145 | 0.0111 | 3.0794 | 28.3333 | 25.5 | 19.4 | 0.0143
| 20 | 4855 | 503 | 17120.2641 | 11534.0712 | 5586.1929 | 0.0113 | 3.1953 | 27.2222 | 25.3333 | 19.76 | 0.0164
| 21 | 3918 | 406 | 13445.0832 | 9302.7009 | 4142.3823 | 0.0113 | 3.1094 | 27.2222 | 25.3333 | 19.76 | 0.0164
| 22 | 3823 | 399 | 13285.0506 | 8973.8427 | 4311.2079 | 0.0114 | 3.1466 | 26.6667 | 25.2222 | 19.8 | 0.0167
| 23 | 3748 | 394 | 13192.1379 | 8787.4311 | 4404.7068 | 0.0115 | 3.185 | 26.1111 | 25.1111 | 19.84 | 0.0169
| 24 | 3880 | 407 | 13754.3037 | 8799.7413 | 4954.5624 | 0.0117 | 3.2084 | 26.1111 | 25.1111 | 20.06 | 0.0178
| EnergyPlus | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
|  | Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
| Hour | (Wh) * | (Wh) * | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
| 1 | 2118.6889 |  | 7471.7175 | 5810.748 | 1660.9695 | 0.0094054 | 3.5266 | 17.9875 | 23.9453 |  | 0.011192
| 2 | 2131.2588 |  | 7494.4102 | 5853.1492 | 1641.261 | 0.0093664 | 3.5164 | 18.1125 | 23.9638 |  | 0.011286
| 3 | 2112.6225 |  | 7446.5844 | 5809.4072 | 1637.1772 | 0.0093723 | 3.5248 | 17.9875 | 23.9453 |  | 0.01119
| 4 | 2074.7396 |  | 7331.9994 | 5743.5733 | 1588.4261 | 0.0093141 | 3.5339 | 17.8 | 23.9171 |  | 0.011051
| 5 | 1997.2205 |  | 7091.0224 | 5614.133 | 1476.8894 | 0.0091917 | 3.5504 | 17.425 | 23.8615 |  | 0.010479
| 6 | 2141.5966 |  | 7425.0625 | 6015.0762 | 1409.9863 | 0.0090454 | 3.4671 | 18.575 | 24.0337 |  | 0.010637
| 7 | 2869.5781 |  | 9216 | 7532.4754 | 1683.5246 | 0.0093227 | 3.2116 | 22.9 | 24.6841 |  | 0.012265
| 8 | 3498.5394 |  | 10609.4108 | 8756.6552 | 1852.7556 | 0.0096417 | 3.0325 | 26.375 | 25.2076 |  | 0.011777
| 9 | 4681.7762 |  | 14032.3459 | 11767.1681 | 2265.1778 | 0.0098152 | 2.9972 | 28.2625 | 25.4902 |  | 0.011572
| 10 | 4947.6011 |  | 14777.6894 | 11996.3298 | 2781.3597 | 0.010197 | 2.9868 | 28.9 | 25.5859 |  | 0.012393
| 11 | 5406.6429 |  | 15905.4096 | 12488.0938 | 3417.3158 | 0.010626 | 2.9418 | 30.275 | 25.7944 |  | 0.013955
| 12 | 5632.385 |  | 16521.8755 | 12670.959 | 3850.9165 | 0.010942 | 2.9334 | 30.7875 | 25.8706 |  | 0.013752
| 13 | 7132.8035 |  | 21588.4217 | 17401.2828 | 4187.139 | 0.010387 | 3.0266 | 30.9125 | 25.8841 |  | 0.011978
| 14 | 6983.3064 |  | 20677.8576 | 17591.92 | 3085.9376 | 0.0099642 | 2.961 | 31.475 | 25.9682 |  | 0.011517
| 15 | 8572.0438 |  | 26132.9897 | 22480.6555 | 3652.3342 | 0.0098097 | 3.0486 | 32.0125 | 26.0506 |  | 0.012075
| 16 | 8732.6963 |  | 26664.6248 | 22557.3408 | 4107.284 | 0.0099222 | 3.0534 | 32.2 | 26.0819 |  | 0.013479
| 17 | 5718.3243 |  | 16344.6134 | 13061.4841 | 3283.1293 | 0.010633 | 2.8583 | 31.8875 | 26.0383 |  | 0.014485
| 18 | 5880.5828 |  | 17193.4049 | 12869.5918 | 4323.8131 | 0.011174 | 2.9238 | 31.325 | 25.9541 |  | 0.015265
| 19 | 5555.1112 |  | 16877.6217 | 12169.8539 | 4707.7678 | 0.011312 | 3.0382 | 29.35 | 25.6545 |  | 0.014908
| 20 | 5259.2137 |  | 16536.4933 | 11555.6363 | 4980.857 | 0.011348 | 3.1443 | 27.6125 | 25.3924 |  | 0.015925
| 21 | 4325.7083 |  | 13445.4149 | 9062.7383 | 4382.6766 | 0.011561 | 3.1083 | 27.2 | 25.332 |  | 0.016792
| 22 | 4278.8801 |  | 13386.5014 | 8952.5422 | 4433.9592 | 0.0116 | 3.1285 | 26.8875 | 25.2853 |  | 0.016752
| 23 | 4172.5901 |  | 13190.5663 | 8753.473 | 4437.0933 | 0.011611 | 3.1612 | 26.325 | 25.2003 |  | 0.016764
| 24 | 4151.9737 |  | 13196.202 | 8673.9655 | 4522.2365 | 0.011664 | 3.1783 | 26.1 | 25.1665 |  | 0.017059
* For EnergyPlus results, the reported compressor energy includes the condenser fan energy.
Table B16.5.2-16. J u n e 2 8 H o u r l y O u t p u t - C a s e C E 3 0 0 (continued)
| CODYRUN | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
|  | Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
| Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
| 1 | 1886 | 237 | 7472 | 5788 | 1684 | 0.009276 | 3.5195 | 17.8 | 23.92 | 17.155 | 0.0111
| 2 | 1964 | 244 | 7707 | 5961 | 1747 | 0.009302 | 3.4905 | 18.3 | 24 | 17.238 | 0.011462
| 3 | 1881 | 236 | 7445 | 5788 | 1657 | 0.009239 | 3.5168 | 17.8 | 23.92 | 17.12 | 0.0111
| 4 | 1878 | 236 | 7432 | 5788 | 1644 | 0.009201 | 3.5156 | 17.8 | 23.92 | 17.102 | 0.0111
| 5 | 1756 | 224 | 7000 | 5580 | 1420 | 0.008969 | 3.5354 | 17.2 | 23.83 | 16.787 | 0.01018
| 6 | 2075 | 253 | 7915 | 6341 | 1574 | 0.009012 | 3.3999 | 19.4 | 24.16 | 17.032 | 0.011001
| 7 | 3035 | 334 | 10450 | 8277 | 2173 | 0.00949 | 3.1018 | 25 | 25 | 17.911 | 0.01314
| 8 | 3303 | 352 | 10813 | 9038 | 1775 | 0.009314 | 2.9584 | 27.2 | 25.33 | 17.646 | 0.011075
| 9 | 4483 | 463 | 14631 | 11971 | 2660 | 0.009708 | 2.9581 | 28.9 | 25.59 | 18.118 | 0.011995
| 10 | 4594 | 472 | 15099 | 11971 | 3128 | 0.010041 | 2.9805 | 28.9 | 25.59 | 18.442 | 0.01276
| 11 | 5238 | 516 | 16722 | 12731 | 3991 | 0.010588 | 2.9062 | 31.1 | 25.91 | 19.142 | 0.014809
| 12 | 5066 | 504 | 16258 | 12559 | 3699 | 0.01058 | 2.9189 | 30.6 | 25.84 | 18.935 | 0.013253
| 13 | 6442 | 642 | 21090 | 17422 | 3669 | 0.009975 | 2.9771 | 31.1 | 25.91 | 18.326 | 0.011329
| 14 | 6523 | 645 | 21067 | 17629 | 3438 | 0.009778 | 2.939 | 31.7 | 26 | 18.269 | 0.011729
| 15 | 8000 | 785 | 26636 | 22491 | 4145 | 0.009579 | 3.032 | 32.2 | 26.08 | 18.239 | 0.012379
| 16 | 8169 | 799 | 27416 | 22491 | 4925 | 0.009733 | 3.0571 | 32.2 | 26.08 | 18.557 | 0.014232
| 17 | 5306 | 519 | 16702 | 12939 | 3763 | 0.01044 | 2.8673 | 31.7 | 26 | 19.063 | 0.01473
| 18 | 5381 | 528 | 17312 | 12729 | 4582 | 0.010912 | 2.9298 | 31.1 | 25.91 | 19.458 | 0.015684
| 19 | 4791 | 492 | 16232 | 11761 | 4470 | 0.010914 | 3.0725 | 28.3 | 25.5 | 19.199 | 0.014539
| 20 | 4809 | 498 | 16867 | 11381 | 5486 | 0.011269 | 3.1783 | 27.2 | 25.33 | 19.65 | 0.016878
| 21 | 3939 | 408 | 13484 | 9036 | 4447 | 0.011348 | 3.1019 | 27.2 | 25.33 | 19.706 | 0.016878
| 22 | 3852 | 402 | 13322 | 8864 | 4459 | 0.011383 | 3.1316 | 26.7 | 25.25 | 19.697 | 0.016832
| 23 | 3752 | 395 | 13139 | 8656 | 4482 | 0.011416 | 3.1683 | 26.1 | 25.16 | 19.694 | 0.016889
| 24 | 3794 | 399 | 13323 | 8656 | 4666 | 0.011507 | 3.1774 | 26.1 | 25.16 | 19.805 | 0.017329
| HOT3000 | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
|  | Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
| Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
| 1 | 1942.81 | 240.938 | 7667.56 | 5870.06 | 1797.5 | 0.0092502 | 3.5112 | 17.8 | 23.9367 | 17.3042 | 0.011072
| 2 | 1950.53 | 241.104 | 7674.46 | 5871.7 | 1802.77 | 0.0092582 | 3.5017 | 18.3 | 23.9367 | 17.31 | 0.011432
| 3 | 1902.33 | 236.85 | 7527.94 | 5782.88 | 1745.07 | 0.0092068 | 3.5191 | 17.8 | 23.8958 | 17.2367 | 0.011072
| 4 | 1845.43 | 231.118 | 7317.22 | 5683.06 | 1634.17 | 0.0091047 | 3.5238 | 17.8 | 23.8375 | 17.0785 | 0.011072
| 5 | 1914.46 | 238.687 | 7514.35 | 5955.01 | 1559.34 | 0.0089519 | 3.4899 | 17.2 | 23.9757 | 17.0075 | 0.010155
| 6 | 2506.57 | 292.588 | 9222.93 | 7311.79 | 1911.15 | 0.0091583 | 3.2949 | 19.4 | 24.5756 | 17.5412 | 0.01097
| 7 | 3170.95 | 342.969 | 10769.5 | 8646.87 | 2122.59 | 0.0094778 | 3.0648 | 25 | 25.1643 | 17.9926 | 0.013099
| 8 | 3433.96 | 360.598 | 11186.4 | 9298.63 | 1887.81 | 0.0093737 | 2.948 | 27.2 | 25.4533 | 17.9591 | 0.011039
| 9 | 4489.15 | 460.788 | 14744.4 | 11923.2 | 2821.19 | 0.0097161 | 2.9787 | 28.9 | 25.5785 | 18.3251 | 0.011957
| 10 | 4853.28 | 489.455 | 15882.1 | 12287.1 | 3595.03 | 0.010237 | 2.9726 | 28.9 | 25.7393 | 18.8543 | 0.012719
| 11 | 5164.22 | 508.218 | 16614.5 | 12561.8 | 4052.76 | 0.010622 | 2.929 | 31.1 | 25.8631 | 19.1876 | 0.014761
| 12 | 5004.96 | 496.504 | 16029.6 | 12561.3 | 3468.23 | 0.010433 | 2.9137 | 30.6 | 25.8628 | 18.8671 | 0.013211
| 13 | 6454.59 | 639.274 | 21179.7 | 17430.7 | 3749.01 | 0.0099715 | 2.9856 | 31.1 | 25.9424 | 18.518 | 0.011293
| 14 | 6503.4 | 639.953 | 21055.4 | 17608.6 | 3446.79 | 0.0097436 | 2.9476 | 31.7 | 26.022 | 18.4421 | 0.011692
| 15 | 8040.55 | 784.905 | 27069.8 | 22350.4 | 4719.45 | 0.0097834 | 3.0672 | 32.2 | 26.1296 | 18.6471 | 0.01234
| 16 | 8133.59 | 793.61 | 27623.3 | 22292 | 5331.25 | 0.0098255 | 3.0943 | 32.2 | 26.0323 | 18.7965 | 0.014188
| 17 | 5211.79 | 509.581 | 16551 | 12739.1 | 3811.95 | 0.010257 | 2.8928 | 31.7 | 25.943 | 19.1104 | 0.014684
| 18 | 5122.29 | 506.956 | 16829.6 | 12180.9 | 4648.77 | 0.010859 | 2.9897 | 31.1 | 25.6955 | 19.3936 | 0.015634
| 19 | 4831.72 | 492.97 | 16635.3 | 11540.7 | 5094.59 | 0.011024 | 3.1242 | 28.3 | 25.4093 | 19.5323 | 0.014493
| 20 | 4874.85 | 501.239 | 17131.1 | 11359.2 | 5771.92 | 0.011357 | 3.1865 | 27.2 | 25.3281 | 19.7431 | 0.016824
| 21 | 3935.62 | 405.543 | 13524.8 | 8931.39 | 4593.42 | 0.011378 | 3.1155 | 27.2 | 25.291 | 19.7437 | 0.016824
| 22 | 3844.33 | 398.939 | 13355.8 | 8747.22 | 4608.6 | 0.011398 | 3.1475 | 26.7 | 25.2092 | 19.7887 | 0.016777
| 23 | 3807.46 | 397.275 | 13343.3 | 8646.75 | 4696.56 | 0.01145 | 3.1734 | 26.1 | 25.1645 | 19.8355 | 0.016835
| 24 | 3664.17 | 385.64 | 12972.7 | 8359.6 | 4613.06 | 0.011462 | 3.2033 | 26.1 | 25.0374 | 19.7678 | 0.017273
Table B16.5.2-16. J u n e 2 8 H o u r l y O u t p u t - C a s e C E 3 0 0 (continued)
| Tested Prg | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
|  | Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
| Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24

## Table-T
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.5.2-17. Delta Annual Space Cooling Electricity Consumptions (Total, Compressor)
Total (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 4339.6026 | 4629 | 4629 | 4544.7265 | 4543.158 | 4538 | 4339.6026 | 4629 | 4537.2479 | 6.378%
CE320-CE300 | 4425.8798 | 3995 | 4037 | 4333.4627 | 4424.404 | 4387 | 3995 | 4425.8798 | 4267.1244 | 10.1%
CE330-CE300 | 5329.5231 | 4958 | 4683 | 5397.736 | 5558.726 | 5260 | 4683 | 5558.726 | 5197.8309 | 16.85%
CE330-CE320 | 903.6433 | 963 | 646 | 1064.2734 | 1134.322 | 873 | 646 | 1134.322 | 930.7065 | 52.47%
CE340-CE300 | 4985.5179 | 4608 | 4510 | 5037.381 | 5088.85 | 4877 | 4510 | 5088.85 | 4851.1248 | 11.93%
CE330-CE340 | 344.0053 | 350 | 173 | 360.355 | 469.876 | 383 | 173 | 469.876 | 346.706 | 85.63%
CE350-CE300 | -3396.7978 | -4203 | -4207 | -3600.5239 | -3389.819 | -3328 | -4207 | -3328 | -3687.5234 | 23.84%
CE360-CE300 | 19665.0145 | 19314 | 19261 | 19959.0734 | 19866.847 | 19998 | 19261 | 19998 | 19677.3225 | 3.745%
CE400-CE300 | -3588.6237 | -3904 | -3879 | -3732.9566 |  | -3657 | -3904 | -3588.6237 | -3752.3161 | 8.405%
CE410-CE300 | -3555.3454 | -3082 | -3056 |  |  | -3567 | -3567 | -3056 | -3315.0863 | 15.41%
CE420-CE300 | -2246.7696 | -2220 | -1845 | -2010.1329 |  | -1862 | -2246.7696 | -1845 | -2036.7805 | 19.73%
CE430-CE300 | -3095.7459 | -2818 | -2944 | -2973.2406 |  | -3252 | -3252 | -2818 | -3016.5973 | 14.39%
CE440-CE300 | -1942.4562 | -1718 | -1782 | -1713.9923 |  | -1822 | -1942.4562 | -1713.9923 | -1795.6897 | 12.72%
CE500-CE300 | -13295.8902 | -11933 | -11933 | -11711.0294 | -12653.458 | -11932 | -13295.8902 | -11711.0294 | -12243.0629 | 12.94%
CE510-CE500 | 17217.9243 | 18099 | 18100 | 17736.3726 | 17414.1 | 17794 | 17217.9243 | 18100 | 17726.8995 | 4.976%
CE525-CE520 | -4665.708 | -4981 | -4969 | -4315.6173 | -4889.357 | -4458 | -4981 | -4315.6173 | -4713.1137 | 14.12%
CE530-CE500 | -5056.616 | -5277 | -5285 | -5292.6649 | -4880.485 | -5263 | -5292.6649 | -4880.485 | -5175.7943 | 7.964%
CE545-CE540 | -3743.2989 | -4076 | -4083 | -2425.3866 | -3745.491 | -3825 | -4083 | -2425.3866 | -3649.6961 | 45.42%
Compressor (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 3986.0911 | 4244 | 4244 |  | 4166.82 | 4177 | 3986.0911 | 4244 | 4163.5822 | 6.194%
CE320-CE300 | 4079.6031 | 3681 | 3721 |  | 4076.025 | 4036 | 3681 | 4079.6031 | 3918.7256 | 10.17%
CE330-CE300 | 4946.1978 | 4603 | 4352 |  | 5157.732 | 4899 | 4352 | 5157.732 | 4791.586 | 16.82%
CE330-CE320 | 866.5947 | 922 | 631 |  | 1081.707 | 863 | 631 | 1081.707 | 872.8603 | 51.64%
CE340-CE300 | 4609.403 | 4260 | 4172 |  | 4702.789 | 4524 | 4172 | 4702.789 | 4453.6384 | 11.92%
CE330-CE340 | 336.7947 | 343 | 180 |  | 454.943 | 375 | 180 | 454.943 | 337.9475 | 81.36%
CE350-CE300 | -3036.6939 | -3767 | -3772 |  | -3031.946 | -2985 | -3772 | -2985 | -3318.528 | 23.72%
CE360-CE300 | 17752.3056 | 17430 | 17382 |  | 17927.161 | 18065 | 17382 | 18065 | 17711.2933 | 3.856%
CE400-CE300 | -3174.5856 | -3463 | -3442 |  |  | -3247 | -3463 | -3174.5856 | -3331.6464 | 8.657%
CE410-CE300 | -3149.0399 | -2746 | -2723 |  |  | -3191 | -3191 | -2723 | -2952.26 | 15.85%
CE420-CE300 | -1994.9489 | -1973 | -1639 |  |  | -1662 | -1994.9489 | -1639 | -1817.2372 | 19.59%
CE430-CE300 | -2754.9132 | -2510 | -2622 |  |  | -2910 | -2910 | -2510 | -2699.2283 | 14.82%
CE440-CE300 | -1724.4011 | -1527 | -1584 |  |  | -1627 | -1724.4011 | -1527 | -1615.6003 | 12.22%
CE500-CE300 | -4499.2388 | -3096 | -3095 |  | -3912.149 | -3354 | -4499.2388 | -3095 | -3591.2776 | 39.1%
CE510-CE500 | 13805.7311 | 14303 | 14304 |  | 13913.445 | 14230 | 13805.7311 | 14304 | 14111.2352 | 3.531%
CE525-CE520 | -2963.4018 | -3241 | -3233 |  | -3148.17 | -2742 | -3241 | -2742 | -3065.5144 | 16.28%
CE530-CE500 | -4197.3004 | -4346 | -4354 |  | -4001.924 | -4350 | -4354 | -4001.924 | -4249.8449 | 8.284%
CE545-CE540 | -2398.8748 | -2713 | -2720 |  | -2413.197 | -2449 | -2720 | -2398.8748 | -2538.8144 | 12.65%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-18. Delta Annual Space Cooling Electricity Consumptions (Fans)
Supply Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE320-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE330-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE330-CE320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE340-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE360-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE400-CE300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | ----
CE410-CE300 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | ----
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | ----
CE430-CE300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | ----
CE440-CE300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | ----
CE500-CE300 | -8316.0984 | -8511 | -8511 | -8233.7654 | -8326.688 | -8241 | -8511 | -8233.7654 | -8356.592 | 3.318%
CE510-CE500 | 1951.1712 | 2262 | 2262 | 2034.3391 | 2001.783 | 2038 | 1951.1712 | 2262 | 2091.5489 | 14.86%
CE525-CE520 | -973.4182 | -988 | -986 | -838.7733 | -995.563 | -979 | -995.563 | -838.7733 | -960.1258 | 16.33%
CE530-CE500 | -491.3766 | -536 | -536 | -538.1091 | -502.376 | -522 | -538.1091 | -491.3766 | -520.9769 | 8.97%
CE545-CE540 | -768.7729 | -757 | -757 | -438.3434 | -761.749 | -787 | -787 | -438.3434 | -711.6442 | 48.99%
Condenser Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 353.5115 | 385 | 385 |  | 376.338 | 368 | 353.5115 | 385 | 373.5699 | 8.429%
CE320-CE300 | 346.2767 | 314 | 316 |  | 348.379 | 358 | 314 | 358 | 336.5311 | 13.07%
CE330-CE300 | 383.3254 | 355 | 331 |  | 400.994 | 370 | 331 | 400.994 | 368.0639 | 19.02%
CE330-CE320 | 37.0487 | 41 | 15 |  | 52.615 | 12 | 12 | 52.615 | 31.5327 | 128.8%
CE340-CE300 | 376.1148 | 348 | 338 |  | 386.061 | 361 | 338 | 386.061 | 361.8352 | 13.28%
CE330-CE340 | 7.2105 | 7 | -7 |  | 14.933 | 9 | -7 | 14.933 | 6.2287 | 352.1%
CE350-CE300 | -360.1038 | -436 | -435 |  | -357.873 | -353 | -436 | -353 | -388.3954 | 21.37%
CE360-CE300 | 1912.7089 | 1884 | 1879 |  | 1939.686 | 1949 | 1879 | 1949 | 1912.879 | 3.659%
CE400-CE300 | -414.0381 | -441 | -437 |  |  | -421 | -441 | -414.0381 | -428.2595 | 6.296%
CE410-CE300 | -406.3054 | -336 | -333 |  |  | -387 | -406.3054 | -333 | -365.5764 | 20.05%
CE420-CE300 | -251.8207 | -247 | -206 |  |  | -208 | -251.8207 | -206 | -228.2052 | 20.08%
CE430-CE300 | -340.8327 | -308 | -322 |  |  | -353 | -353 | -308 | -330.9582 | 13.6%
CE440-CE300 | -218.0552 | -191 | -198 |  |  | -203 | -218.0552 | -191 | -202.5138 | 13.36%
CE500-CE300 | -480.5531 | -326 | -327 |  | -414.621 | -347 | -480.5531 | -326 | -379.0348 | 40.78%
CE510-CE500 | 1461.0219 | 1534 | 1534 |  | 1498.872 | 1526 | 1461.0219 | 1534 | 1510.7788 | 4.83%
CE525-CE520 | -728.888 | -752 | -750 |  | -745.624 | -733 | -752 | -728.888 | -741.9024 | 3.115%
CE530-CE500 | -367.939 | -395 | -395 |  | -376.185 | -391 | -395 | -367.939 | -385.0248 | 7.028%
CE545-CE540 | -575.6512 | -606 | -606 |  | -570.545 | -589 | -606 | -570.545 | -589.4392 | 6.015%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-19. Delta Annual Cooling Coil Loads
Sensible Coil Load (kWh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | -405.371 | 504.132 | 507.9423 | -26.7995 | -24.393 | -108 | -405.371 | 507.9423 | 74.5851 | 1225%
CE320-CE300 | 6197.4569 | 6900.1602 | 6942.0735 | 6791.4957 | 6799.339 | 7543 | 6197.4569 | 7543 | 6862.2542 | 19.61%
CE330-CE300 | 6421.6281 | 7514.2047 | 7522.9977 | 8526.6982 | 7439.994 | 6631 | 6421.6281 | 8526.6982 | 7342.7538 | 28.67%
CE330-CE320 | 224.1712 | 614.0445 | 580.9242 | 1735.2025 | 640.655 | -912 | -912 | 1735.2025 | 480.4996 | 550.9%
CE340-CE300 | 6370.8576 | 7256.5698 | 7305.8106 | 7633.8781 | 7171.095 | 6215 | 6215 | 7633.8781 | 6992.2019 | 20.29%
CE330-CE340 | 50.7704 | 257.6349 | 217.1871 | 892.82 | 268.899 | 416 | 50.7704 | 892.82 | 350.5519 | 240.2%
CE350-CE300 | -6290.9181 | -8112.4218 | -8128.2492 | -6706.9451 | -6620.663 | -6423 | -8128.2492 | -6290.9181 | -7047.0329 | 26.07%
CE360-CE300 | 78315.0867 | 79122.9312 | 79134.9483 | 80035.2385 | 78996.242 | 79506 | 78315.0867 | 80035.2385 | 79185.0745 | 2.172%
CE400-CE300 | -14709.3889 | -14377.7274 | -14367.762 | -14564.2107 |  | -14010 | -14709.3889 | -14010 | -14405.8178 | 4.855%
CE410-CE300 | -10985.1029 | -8138.2146 | -8144.9559 |  |  | -9606 | -10985.1029 | -8138.2146 | -9218.5683 | 30.88%
CE420-CE300 | -6271.9238 | -6130.7727 | -5192.5596 | -5728.0295 |  | -5207 | -6271.9238 | -5192.5596 | -5706.0571 | 18.92%
CE430-CE300 | -8798.4022 | -8065.5258 | -8350.7121 | -8513.3758 |  | -9048 | -9048 | -8065.5258 | -8555.2032 | 11.48%
CE440-CE300 | -5785.676 | -5204.2836 | -5312.7306 | -5191.7822 |  | -5406 | -5785.676 | -5191.7822 | -5380.0945 | 11.04%
CE500-CE300 | -11617.9484 | -8147.0076 | -8158.7316 | -7760.7172 | -10335.24 | -7661 | -11617.9484 | -7661 | -8946.7741 | 44.23%
CE510-CE500 | 43046.1977 | 45710.1174 | 45709.8243 | 45090.7524 | 43050.834 | 45083 | 43046.1977 | 45710.1174 | 44615.121 | 5.971%
CE525-CE520 | -130.6037 | -883.9896 | -882.231 | -1056.6213 | -201.619 | -949 | -1056.6213 | -130.6037 | -684.0108 | 135.4%
CE530-CE500 | 2.048 | -1076.2632 | -1075.9701 | -546.8842 | 0 | -528 | -1076.2632 | 2.048 | -537.5116 | 200.6%
CE545-CE540 | -130.4955 | -808.6629 | -808.6629 | -676.1559 | -201.642 | -792 | -808.6629 | -130.4955 | -569.6032 | 119.1%
Latent Coil Load(kWh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 19320.6351 | 19607.2176 | 19612.2003 | 19156.4402 | 19575.693 | 19111 | 19111 | 19612.2003 | 19397.1977 | 2.584%
CE320-CE300 | 13167.3536 | 12172.7361 | 12259.2006 | 11974.1143 | 12597.449 | 11157 | 11157 | 13167.3536 | 12221.3089 | 16.45%
CE330-CE300 | 18164.3759 | 15932.3298 | 16178.5338 | 16366.7125 | 18528.23 | 17119 | 15932.3298 | 18528.23 | 17048.197 | 15.23%
CE330-CE320 | 4997.0223 | 3759.5937 | 3919.3332 | 4392.5982 | 5930.781 | 5962 | 3759.5937 | 5962 | 4826.8881 | 45.63%
CE340-CE300 | 15930.2538 | 14487.6399 | 14625.3969 | 14756.6878 | 15760.481 | 15279 | 14487.6399 | 15930.2538 | 15139.9099 | 9.529%
CE330-CE340 | 2234.1221 | 1444.6899 | 1553.1369 | 1610.0247 | 2767.749 | 1840 | 1444.6899 | 2767.749 | 1908.2871 | 69.33%
CE350-CE300 | -4747.9518 | -5434.6602 | -5529.0384 | -4820.6365 | -4263.749 | -4446 | -5529.0384 | -4263.749 | -4873.6727 | 25.96%
CE360-CE300 | 4232.1084 | 3400.8393 | 3426.9252 | 3895.2567 | 4459.339 | 4403 | 3400.8393 | 4459.339 | 3969.5781 | 26.67%
CE400-CE300 | 3075.3436 | 2011.8384 | 2100.9408 | 2660.1023 |  | 2650 | 2011.8384 | 3075.3436 | 2499.645 | 42.55%
CE410-CE300 | -768.9108 | -2365.6101 | -2303.4729 |  |  | -2477 | -2477 | -768.9108 | -1978.7484 | 86.32%
CE420-CE300 | -1545.6363 | -1541.706 | -1217.2443 | -1240.4535 |  | -1212 | -1545.6363 | -1212 | -1351.408 | 24.69%
CE430-CE300 | -1872.1533 | -1577.1711 | -1721.9625 | -1663.2215 |  | -2010 | -2010 | -1577.1711 | -1768.9017 | 24.47%
CE440-CE300 | -929.828 | -699.0435 | -798.1113 | -708.8605 |  | -823 | -929.828 | -699.0435 | -791.7687 | 29.15%
CE500-CE300 | -5451.8128 | -3140.5665 | -3140.8596 | -3986.0493 | -4304.002 | -4983 | -5451.8128 | -3140.5665 | -4167.715 | 55.46%
CE510-CE500 | 17484.6814 | 17615.0169 | 17615.0169 | 17347.6038 | 17488.438 | 17340 | 17340 | 17615.0169 | 17481.7928 | 1.573%
CE525-CE520 | 2.0047 | -288.1173 | -288.1173 | -57.8538 | -8.624 | -42 | -288.1173 | 2.0047 | -113.7846 | 255%
CE530-CE500 | -18313.3062 | -18285.3366 | -18285.6297 | -18079.9419 | -18229.955 | -18084 | -18313.3062 | -18079.9419 | -18213.0282 | 1.281%
CE545-CE540 | -0.97976 | -81.4818 | -81.4818 | -8.5582 | -3.086 | -2 | -81.4818 | -0.97976 | -29.5979 | 272%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-20. Delta Various Annual Means (COP2, IDB)
COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0.16552 | 0.1798 | 0.18013 | 0.15538 | 0.17086 | 0.15 | 0.15 | 0.18013 | 0.16695 | 18.05%
CE320-CE300 | 0.17083 | 0.22029 | 0.21969 | 0.16788 | 0.17958 | 0.16 | 0.16 | 0.22029 | 0.18638 | 32.35%
CE330-CE300 | 0.24166 | 0.25649 | 0.29907 | 0.25338 | 0.2709 | 0.23 | 0.23 | 0.29907 | 0.25859 | 26.71%
CE330-CE320 | 0.070831 | 0.036201 | 0.079382 | 0.085508 | 0.091321 | 0.07 | 0.036201 | 0.091321 | 0.072207 | 76.34%
CE340-CE300 | 0.20521 | 0.23966 | 0.25826 | 0.21034 | 0.22316 | 0.19 | 0.19 | 0.25826 | 0.2211 | 30.87%
CE330-CE340 | 0.036452 | 0.016833 | 0.040815 | 0.043047 | 0.047744 | 0.04 | 0.016833 | 0.047744 | 0.037482 | 82.47%
CE350-CE300 | -0.00011501 | 0.003096 | -0.0019178 | 0.0063283 | 0.0025325 | 0 | -0.0019178 | 0.0063283 | 0.001654 | 498.6%
CE360-CE300 | 0.41996 | 0.46293 | 0.46845 | 0.4406 | 0.44031 | 0.43 | 0.41996 | 0.46845 | 0.44371 | 10.93%
CE400-CE300 | 0.0012106 | 0.013724 | 0.014548 | 0.0089602 |  | 0.03 | 0.0012106 | 0.03 | 0.013688 | 210.3%
CE410-CE300 | -0.0095511 | -0.025269 | -0.026661 |  |  | -0.02 | -0.026661 | -0.0095511 | -0.02037 | 84%
CE420-CE300 | -0.023 | -0.022394 | -0.019831 | -0.02108 |  | -0.02 | -0.023 | -0.019831 | -0.021261 | 14.9%
CE430-CE300 | -0.02827 | -0.024649 | -0.025889 | -0.026368 |  | -0.02 | -0.02827 | -0.02 | -0.025035 | 33.03%
CE440-CE300 | -0.017725 | -0.015393 | -0.015474 | -0.015876 |  | -0.01 | -0.017725 | -0.01 | -0.014894 | 51.87%
CE500-CE300 | -0.045013 | -0.010183 | -0.010822 | -0.024005 | -0.034365 | -0.03 | -0.045013 | -0.010183 | -0.025732 | 135.4%
CE510-CE500 | 0.40948 | 0.41598 | 0.41577 | 0.40797 | 0.39713 | 0.41 | 0.39713 | 0.41598 | 0.40939 | 4.606%
CE525-CE520 | 0.58247 | 0.57414 | 0.57204 | 0.50377 | 0.60629 | 0.49 | 0.49 | 0.60629 | 0.55478 | 20.96%
CE530-CE500 | -0.24223 | -0.25849 | -0.25718 | -0.21398 | -0.27645 | -0.22 | -0.27645 | -0.21398 | -0.24472 | 25.53%
CE545-CE540 | 0.5601 | 0.55853 | 0.56036 | 0.33359 | 0.54604 | 0.51 | 0.33359 | 0.56036 | 0.51144 | 44.34%
IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0.1313 | 0.055556 | 0 | 0.0013565 | 0.0080616 | 0.02 | 0 | 0.1313 | 0.036045 | 364.3%
CE320-CE300 | 0.27622 | 0.33333 | 0.33333 | 0.16367 | 0.24571 | 0.54 | 0.16367 | 0.54 | 0.31538 | 119.3%
CE330-CE300 | 0.25545 | 0.22222 | 0.22222 | 0.18266 | 0.21382 | 0.19 | 0.18266 | 0.25545 | 0.2144 | 33.95%
CE330-CE320 | -0.02077 | -0.11111 | -0.11111 | 0.018995 | -0.031885 | -0.35 | -0.35 | 0.018995 | -0.10098 | 365.4%
CE340-CE300 | 0.25135 | 0.22222 | 0.22222 | 0.20752 | 0.22722 | 0.22 | 0.20752 | 0.25135 | 0.22509 | 19.47%
CE330-CE340 | 0.0041016 | 0 | 0 | -0.024858 | -0.013394 | -0.03 | -0.03 | 0.0041016 | -0.010692 | 319%
CE350-CE300 | 2.0352 | 2.1111 | 2.1111 | 2.1509 | 2.187 | 2.16 | 2.0352 | 2.187 | 2.1259 | 7.139%
CE360-CE300 | 1.7407 | 1.5556 | 1.5 | 1.2324 | 1.3992 | 1.38 | 1.2324 | 1.7407 | 1.468 | 34.62%
CE400-CE300 | 0.50202 | 0 | 0 | 0.0012363 |  | 0 | 0 | 0.50202 | 0.10065 | 498.8%
CE410-CE300 | 0.49787 | 0 | 0 |  |  | 0 | 0 | 0.49787 | 0.12447 | 400%
CE420-CE300 | 0.3019 | 0 | 0 | -9.3106e-05 |  | 0 | -9.3106e-05 | 0.3019 | 0.060361 | 500.3%
CE430-CE300 | 0.36731 | 0 | 0 | -0.00010336 |  | 0 | -0.00010336 | 0.36731 | 0.073441 | 500.3%
CE440-CE300 | 0.2875 | 0 | 0 | -5.3781e-05 |  | 0 | -5.3781e-05 | 0.2875 | 0.057489 | 500.2%
CE500-CE300 | -3.3901 | -3.3889 | -3.5 | -3.7113 | -2.9838 | -1.13 | -3.7113 | -1.13 | -3.0173 | 85.55%
CE510-CE500 | 1.2445 | 0.11111 | 0.11111 | -0.022745 | 0 | 0 | -0.022745 | 1.2445 | 0.24067 | 526.6%
CE525-CE520 | 13.3272 | 13.6111 | 13.5556 | 13.5272 | 13.6289 | 15.8 | 13.3272 | 15.8 | 13.9083 | 17.78%
CE530-CE500 | -0.20888 | -0.055556 | 0 | 0.20651 | 0 | 0 | -0.20888 | 0.20651 | -0.0096546 | 4303%
CE545-CE540 | 13.3159 | 13.5556 | 13.5556 | 13.5189 | 13.576 | 15.71 | 13.3159 | 15.71 | 13.872 | 17.26%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-21. Delta Various Annual Means (Zone Humidity, Relative Humidity)
Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0.0020018 | 0.0021 | 0.0021 | 0.0019746 | 0.0019998 | 0.0019 | 0.0019 | 0.0021 | 0.0020127 | 9.937%
CE320-CE300 | 0.00091896 | 0.0009 | 0.0009 | 0.00082797 | 0.00087438 | 0.0007 | 0.0007 | 0.00091896 | 0.00085355 | 25.65%
CE330-CE300 | 0.00067186 | 0.0007 | 0.0007 | 0.0006823 | 0.00063678 | 0.0007 | 0.00063678 | 0.0007 | 0.00068182 | 9.272%
CE330-CE320 | -0.00024709 | -0.0002 | -0.0002 | -0.00014568 | -0.00023759 | 0 | -0.00024709 | 0 | -0.00017173 | 143.9%
CE340-CE300 | 0.00072232 | 0.0007 | 0.0007 | 0.00069759 | 0.00069351 | 0.0007 | 0.00069351 | 0.00072232 | 0.00070224 | 4.103%
CE330-CE340 | -5.0461e-05 | 0 | 0 | -1.5289e-05 | -5.6729e-05 | 0 | -5.6729e-05 | 0 | -2.0413e-05 | 277.9%
CE350-CE300 | 0.00063685 | 0.0008 | 0.0008 | 0.00063956 | 0.00058373 | 0.00057 | 0.00057 | 0.0008 | 0.00067169 | 34.24%
CE360-CE300 | -0.0005696 | -0.0005 | -0.0005 | -0.00052024 | -0.00062237 | -0.00062 | -0.00062237 | -0.0005 | -0.00055537 | 22.03%
CE400-CE300 | 0.00073206 | 0.0008 | 0.0008 | 0.00080072 |  | 0.0008 | 0.00073206 | 0.00080072 | 0.00078656 | 8.729%
CE410-CE300 | 0.00067139 | 0.0003 | 0.0003 |  |  | 0.0003 | 0.0003 | 0.00067139 | 0.00039285 | 94.54%
CE420-CE300 | 0.00019481 | 0.0002 | 0.0002 | 0.00016242 |  | 0.0001 | 0.0001 | 0.0002 | 0.00017145 | 58.33%
CE430-CE300 | 0.00024119 | 0.0002 | 0.0002 | 0.00020337 |  | 0.0002 | 0.0002 | 0.00024119 | 0.00020891 | 19.72%
CE440-CE300 | 8.8738e-05 | 0.0001 | 0.0001 | 4.8002e-05 |  | 0 | 0 | 0.0001 | 6.7348e-05 | 148.5%
CE500-CE300 | 0.00070622 |  |  | 8.6686e-05 | 0.0010435 | 0.0015 | 8.6686e-05 | 0.0015 | 0.00083409 | 169.4%
CE510-CE500 | 0.00037457 |  |  | 7.3411e-06 | -8.8998e-07 | 0 | -8.8998e-07 | 0.00037457 | 9.5255e-05 | 394.2%
CE525-CE520 | 0.0070203 |  |  | 0.0077564 | 0.0069569 | 0.00747 | 0.0069569 | 0.0077564 | 0.0073009 | 10.95%
CE530-CE500 | -0.0035488 |  |  | -0.0026606 | -0.0044208 | -0.00403 | -0.0044208 | -0.0026606 | -0.003665 | 48.02%
CE545-CE540 | 0.0017664 |  |  | 0.0023868 | 0.0028945 | 0.00259 | 0.0017664 | 0.0028945 | 0.0024094 | 46.82%
Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 9.7158 | 10.25 | 10.25 | 9.9598 | 10.0148 | 9.87 | 9.7158 | 10.25 | 10.0101 | 5.336%
CE320-CE300 | 3.3904 | 2.95 | 2.97 | 3.2494 | 3.2773 | 2.01 | 2.01 | 3.3904 | 2.9745 | 46.41%
CE330-CE300 | 2.2296 | 2.32 | 2.37 | 2.5851 | 2.2587 | 2.77 | 2.2296 | 2.77 | 2.4222 | 22.31%
CE330-CE320 | -1.1608 | -0.63 | -0.6 | -0.66425 | -1.0186 | 0.76 | -1.1608 | 0.76 | -0.55228 | 347.8%
CE340-CE300 | 2.4702 | 2.43 | 2.45 | 2.5566 | 2.4705 | 2.85 | 2.43 | 2.85 | 2.5379 | 16.55%
CE330-CE340 | -0.24056 | -0.11 | -0.08 | 0.028551 | -0.21187 | -0.08 | -0.24056 | 0.028551 | -0.11565 | 232.7%
CE350-CE300 | -3.1309 | -2.81 | -2.73 | -3.4182 | -3.5099 | -3.37 | -3.5099 | -2.73 | -3.1615 | 24.67%
CE360-CE300 | -7.5814 | -6.77 | -6.79 | -6.2219 | -6.9551 | -6.72 | -7.5814 | -6.2219 | -6.8397 | 19.88%
CE400-CE300 | 2.156 | 3.95 | 3.97 | 3.9572 |  | 4.08 | 2.156 | 4.08 | 3.6226 | 53.11%
CE410-CE300 | 1.8822 | 1.39 | 1.35 |  |  | 1.82 | 1.35 | 1.8822 | 1.6106 | 33.05%
CE420-CE300 | 0.16451 | 0.88 | 0.69 | 0.80676 |  | 0.83 | 0.16451 | 0.88 | 0.67425 | 106.1%
CE430-CE300 | 0.20708 | 0.91 | 1.02 | 1.0089 |  | 1.24 | 0.20708 | 1.24 | 0.87719 | 117.8%
CE440-CE300 | -0.28509 | 0.2 | 0.29 | 0.23749 |  | 0.3 | -0.28509 | 0.3 | 0.14848 | 394.1%
CE500-CE300 | 17.9113 |  |  | 10.6062 | 18.1158 | 15.8 | 10.6062 | 18.1158 | 15.6083 | 48.11%
CE510-CE500 | -2.3476 |  |  | 0.11417 | -0.010621 | 0.11 | -2.3476 | 0.11417 | -0.5335 | 461.4%
CE525-CE520 | -8.4071 |  |  | -6.4105 | -10.0881 | -14.8 | -14.8 | -6.4105 | -9.9264 | 84.52%
CE530-CE500 | -19.7962 |  |  | -10.2243 | -24.4903 | -24.13 | -24.4903 | -10.2243 | -19.6602 | 72.56%
CE545-CE540 | -11.8961 |  |  | -7.6766 | -3.1763 | -14.62 | -14.62 | -3.1763 | -9.3422 | 122.5%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-22. Delta Hourly Integrated Maximum Total Consumptions
Total Consumption (Wh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 968.3645 | 1019 | 993 | 640.9591 | 721 | 614 | 614 | 1019 | 826.0539 | 49.03%
CE320-CE300 | 1402.1615 | 1352 | 1379 | 1054.567 | 1172 | 1327 | 1054.567 | 1402.1615 | 1281.1214 | 27.13%
CE330-CE300 | 1720.664 | 1648 | 1805 | 1414.2502 | 1535 | 1787 | 1414.2502 | 1805 | 1651.6524 | 23.66%
CE330-CE320 | 318.5024 | 296 | 426 | 359.6832 | 363 | 460 | 296 | 460 | 370.5309 | 44.26%
CE340-CE300 | 1554.8648 | 1594 | 1588 | 1234.3106 | 1345 | 1553 | 1234.3106 | 1594 | 1478.1959 | 24.33%
CE330-CE340 | 165.7992 | 54 | 217 | 179.9396 | 190 | 234 | 54 | 234 | 173.4565 | 103.8%
CE350-CE300 | 0.85194 | 90 | 0 | 0.0021837 | 0 | -2 | -2 | 90 | 14.809 | 621.2%
CE360-CE300 | 1143.4651 | 1172 | 1124 | 844.4186 | 931 | 1214 | 844.4186 | 1214 | 1071.4806 | 34.49%
CE400-CE300 | 1.8307 | 0 | 75 | -1.7556e-06 |  | -29 | -29 | 75 | 9.5661 | 1087%
CE410-CE300 | 1.8307 | 0 | 0 |  |  | 1 | 0 | 1.8307 | 0.70767 | 258.7%
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | ----
CE430-CE300 | 0 | 0 | 0 | -1.0004e-10 |  | 0 | -1.0004e-10 | 0 | -2.0009e-11 | 500%
CE440-CE300 | 0 | 0 | 0 | 0 |  | -87 | -87 | 0 | -17.4 | 500%
CE500-CE300 | -1459.5539 | -1133 | -1177 | -1501.1724 | -1755 | -1274 | -1755 | -1133 | -1383.2877 | 44.97%
CE510-CE500 | 1038.4136 | 1159 | 1162 | 1011.1162 | 1009 | 1070 | 1009 | 1162 | 1074.9216 | 14.23%
CE525-CE520 | -1668.6417 | -1451 | -1483 | -1530.9547 | -1625 | -1099 | -1668.6417 | -1099 | -1476.2661 | 38.59%
CE530-CE500 | -2138.1546 | -2372 | -2370 | -2227.6394 | -2185 | -2185 | -2372 | -2138.1546 | -2246.299 | 10.41%
CE545-CE540 | -1494.1291 | -1593 | -1593 | -914.6465 | -1495 | -1514 | -1593 | -914.6465 | -1433.9626 | 47.31%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-23. Delta Hourly Integrated Maximum Coil Loads ( Total, Sensible)
Sensible + Latent Coil Load (Wh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 5153.95 | 5349 | 5578 | 4393.2239 | 4759 | 4919 | 4393.2239 | 5578 | 5025.3623 | 23.58%
CE320-CE300 | 8143.55 | 22412 | 22368 | 7031.9273 | 7402 | 7848 | 7031.9273 | 22412 | 12534.2462 | 122.7%
CE330-CE300 | 11317.95 | 12227 | 33117 | 10711.8252 | 11476 | 10343 | 10343 | 33117 | 14865.4625 | 153.2%
CE330-CE320 | 3174.4 | -10185 | 10749 | 3679.898 | 4074 | 2495 | -10185 | 10749 | 2331.2163 | 898%
CE340-CE300 | 9477.65 | 19418 | 28094 | 8595.018 | 8864 | 9060 | 8595.018 | 28094 | 13918.1113 | 140.1%
CE330-CE340 | 1840.3 | -7191 | 5023 | 2116.8072 | 2612 | 1283 | -7191 | 5023 | 947.3512 | 1289%
CE350-CE300 | -82.32 | 0 | -1 | 0.0093743 | 0 | 5 | -82.32 | 5 | -13.0518 | 669%
CE360-CE300 | 6683.11 | 9212 | 9564 | 5726.4726 | 5820 | 6379 | 5726.4726 | 9564 | 7230.7638 | 53.07%
CE400-CE300 | 9004.55 | 9142 | 18383 | 7994.8866 |  | 8702 | 7994.8866 | 18383 | 10645.2873 | 97.58%
CE410-CE300 | -82.32 | 0 | 0 |  |  | 1 | -82.32 | 1 | -20.33 | 409.8%
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | ----
CE430-CE300 | 0 | 0 | 0 | -5.5297e-10 |  | 0 | -5.5297e-10 | 0 | -1.1059e-10 | 500%
CE440-CE300 | 0 | 0 | 0 | -2.7649e-10 |  | -295 | -295 | 0 | -59 | 500%
CE500-CE300 | -4688.54 | -3694 | -3749 | -5086.83 | -5935 | -4517 | -5935 | -3694 | -4611.7283 | 48.59%
CE510-CE500 | 3107.54 | 3481 | 3482 | 3531.3254 | 3381 | 3542 | 3107.54 | 3542 | 3420.8109 | 12.7%
CE525-CE520 | 410.17 | -412 | -412 | -76.1817 | 8 | -881 | -881 | 410.17 | -227.1686 | 568.4%
CE530-CE500 | -7651.41 | -8131 | -8131 | -8007.6599 | -7791 | -7929 | -8131 | -7651.41 | -7940.1783 | 6.04%
CE545-CE540 | 500.2 | -291 | -292 | -186.6119 | -30 | -302 | -302 | 500.2 | -100.2353 | 800.3%
Sensible Coil Load (Wh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | -183.1 | -123 | -86 | -254.3484 | -379 | -259 | -379 | -86 | -214.0747 | 136.9%
CE320-CE300 | 8038.2 | 7916 | 7867 | 8441.2775 | 7677 | 8059 | 7677 | 8441.2775 | 7999.7462 | 9.554%
CE330-CE300 | 9948.7 | 10207 | 11285 | 11233.9719 | 10540 | 10513 | 9948.7 | 11285 | 10621.2787 | 12.58%
CE330-CE320 | 1910.5 | 2291 | 3418 | 2792.6945 | 2863 | 2454 | 1910.5 | 3418 | 2621.5324 | 57.5%
CE340-CE300 | 9551.5 | 8883 | 8881 | 9356.9768 | 9483 | 9272 | 8881 | 9551.5 | 9237.9128 | 7.258%
CE330-CE340 | 397.2 | 1324 | 2404 | 1876.9952 | 1057 | 1241 | 397.2 | 2404 | 1383.3659 | 145.1%
CE350-CE300 | 0.1 | 0 | 0 | -0.00037974 | 0 | -32 | -32 | 0.1 | -5.3167 | 603.8%
CE360-CE300 | 8783.3 | 8908 | 8860 | 9090.1056 | 8524 | 9271 | 8524 | 9271 | 8906.0676 | 8.388%
CE400-CE300 | 0.1 | 0 | 0 | -7.3683e-06 |  | -31 | -31 | 0.1 | -6.18 | 503.2%
CE410-CE300 | -11.7 | 0 | 0 |  |  | -15 | -15 | 0 | -6.675 | 224.7%
CE420-CE300 | 0 | 0 | 0 | -2.9104e-11 |  | -15 | -15 | 0 | -3 | 500%
CE430-CE300 | 0 | 0 | 0 | -4.1473e-10 |  | -15 | -15 | 0 | -3 | 500%
CE440-CE300 | 0 | 0 | 0 | -1.6371e-10 |  | -33 | -33 | 0 | -6.6 | 500%
CE500-CE300 | -3728.2 | -3194 | -3197 | -3681.5174 | -4681 | -3090 | -4681 | -3090 | -3595.2862 | 44.25%
CE510-CE500 | 2180 | 2504 | 2505 | 2441.0216 | 2345 | 2451 | 2180 | 2505 | 2404.3369 | 13.52%
CE525-CE520 | 286.8 | -309 | -304 | -335.6215 | -210 | -717 | -717 | 286.8 | -264.8036 | 379.1%
CE530-CE500 | 284.9 | -433 | -433 | -210.5244 | 0 | -192 | -433 | 284.9 | -163.9374 | 437.9%
CE545-CE540 | 500.2 | -291 | -292 | -186.6119 | -35 | -302 | -302 | 500.2 | -101.0687 | 793.7%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-24. Delta Hourly Integrated Maximum Coil Loads ( Latent)
Latent Coil Load (Wh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 6271.3 | 5835 | 5876 | 6040.0162 | 5737 | 5685 | 5685 | 6271.3 | 5907.386 | 9.925%
CE320-CE300 | 13511.6 | 22193 | 22109 | 11960.6494 | 11322 | 11537 | 11322 | 22193 | 15438.8749 | 70.41%
CE330-CE300 | 18189.5 | 17637 | 31415 | 16899.4932 | 17809 | 17096 | 16899.4932 | 31415 | 19840.9989 | 73.16%
CE330-CE320 | 4677.9 | -4556 | 9306 | 4938.8437 | 6487 | 5559 | -4556 | 9306 | 4402.124 | 314.9%
CE340-CE300 | 15212.6 | 21147 | 26617 | 13676.4198 | 13850 | 13402 | 13402 | 26617 | 17317.5033 | 76.31%
CE330-CE340 | 2976.9 | -3510 | 4798 | 3223.0734 | 3959 | 3694 | -3510 | 4798 | 2523.4956 | 329.2%
CE350-CE300 | 115.56 | -1 | -1 | 0.53144 | 380 | 1211 | -1 | 1211 | 284.1819 | 426.5%
CE360-CE300 | -360.54 | 722 | 942 | -1714.5041 | -1516 | -1458 | -1714.5041 | 942 | -564.174 | 470.9%
CE400-CE300 | 17439.6 | 16274 | 23002 | 16082.4601 |  | 16253 | 16082.4601 | 23002 | 17810.212 | 38.85%
CE410-CE300 | 1503.2 | 0 | -3 |  |  | -15 | -15 | 1503.2 | 371.3 | 408.9%
CE420-CE300 | 115.34 | 0 | 0 | -5.6389e-11 |  | 2 | -5.6389e-11 | 115.34 | 23.468 | 491.5%
CE430-CE300 | 0 | 1801 | 1707 | 838.9522 |  | 2 | 0 | 1801 | 869.7904 | 207.1%
CE440-CE300 | 0 | 0 | -3 | -2.9104e-11 |  | -253 | -253 | 0 | -51.2 | 494.1%
CE500-CE300 | -1670.24 | -1571 | -1661 | -2396.1014 | -2570 | -2630 | -2630 | -1571 | -2083.0569 | 50.84%
CE510-CE500 | 927.1 | 990 | 990 | 1116.0715 | 1045 | 1112 | 927.1 | 1116.0715 | 1030.0286 | 18.35%
CE525-CE520 | 123.37 | -122 | -122 | 248.8578 | 212 | -144 | -144 | 248.8578 | 32.7046 | 1201%
CE530-CE500 | -7965.46 | -7733 | -7733 | -7837.6616 | -7626 | -7726.1 | -7965.46 | -7626 | -7770.2036 | 4.369%
CE545-CE540 | -627.186 | 0 | 0 | -1654.9514 | -841 | -1181 | -1654.9514 | 0 | -717.3562 | 230.7%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-25. Delta Hourly Integrated Maximum and Minimum COP2
Maximum COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | -0.025037 | 0.272 | 0.271 | 0.2477 | 0.25703 | 0.24 | -0.025037 | 0.272 | 0.21045 | 141.1%
CE320-CE300 | 0 | 1.274 | 1.11 | 0.014298 | 0.072694 | 0.5 | 0 | 1.274 | 0.49517 | 257.3%
CE330-CE300 | 0 | 0.24 | 1.738 | 0.14626 | 0.25134 | 0.17 | 0 | 1.738 | 0.42427 | 409.6%
CE330-CE320 | 0 | -1.034 | 0.628 | 0.13196 | 0.17864 | -0.33 | -1.034 | 0.628 | -0.070899 | 2344%
CE340-CE300 | 0 | 0.752 | 1.482 | 0.061376 | 0.14655 | 0.07 | 0 | 1.482 | 0.41865 | 354%
CE330-CE340 | 0 | -0.512 | 0.256 | 0.084885 | 0.10479 | 0.1 | -0.512 | 0.256 | 0.0056117 | 13686%
CE350-CE300 | 0 | 0.02 | 0.006 | 0.63002 | 0.061488 | 0 | 0 | 0.63002 | 0.11959 | 526.8%
CE360-CE300 | 0.23263 | 0.559 | 0.57 | 0.53014 | 0.5614 | 0.56 | 0.23263 | 0.57 | 0.5022 | 67.18%
CE400-CE300 | -0.091398 | 0.219 | 0.919 | 0.14625 |  | 0.17 | -0.091398 | 0.919 | 0.27257 | 370.7%
CE410-CE300 | -0.28043 | 0.034 | -0.002 |  |  | -0.04 | -0.28043 | 0.034 | -0.072107 | 436.1%
CE420-CE300 | -0.38705 | -0.062 | -0.098 | -0.10384 |  | 0.06 | -0.38705 | 0.06 | -0.11818 | 378.3%
CE430-CE300 | -0.38705 | -0.064 | -0.098 | -0.13253 |  | 0.05 | -0.38705 | 0.05 | -0.12632 | 346%
CE440-CE300 | -0.28486 | -0.095 | -0.098 | -0.12338 |  | -0.07 | -0.28486 | -0.07 | -0.13425 | 160%
CE500-CE300 | 0.1068 | 3.498 | 1.444 | 0.27276 | 0.31401 | 0.26 | 0.1068 | 3.498 | 0.98259 | 345.1%
CE510-CE500 | 0.4174 | 0 | 0 | 0.48669 | 0.50496 | 0.39 | 0 | 0.50496 | 0.29984 | 168.4%
CE525-CE520 | 0.90402 | 1.429 | 1.379 | 0.76636 | 0.83633 | 0.56 | 0.56 | 1.429 | 0.97912 | 88.75%
CE530-CE500 | -0.26907 | -3.386 | -1.451 | -0.27296 | -0.34458 | -0.26 | -3.386 | -0.26 | -0.99727 | 313.5%
CE545-CE540 | 0.79448 | 0.819 | 0.973 | 0.47021 | 0.48982 | 0.48 | 0.47021 | 0.973 | 0.67108 | 74.92%
Minimum COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0.072169 | 0.052 | 0.05 | 0.11113 | 0.087015 | 0.06 | 0.05 | 0.11113 | 0.072052 | 84.84%
CE320-CE300 | 0.032137 | 0.003 | 0.004 | 0.059984 | 0.028893 | 0.02 | 0.003 | 0.059984 | 0.024669 | 231%
CE330-CE300 | 0.032137 | 0 | 0 | 0.062559 | 0.037696 | 0.03 | 0 | 0.062559 | 0.027065 | 231.1%
CE330-CE320 | 0 | -0.003 | -0.004 | 0.0025756 | 0.0088028 | 0.01 | -0.004 | 0.01 | 0.0023964 | 584.2%
CE340-CE300 | 0.032137 | 0 | 0 | 0.062559 | 0.037696 | 0.03 | 0 | 0.062559 | 0.027065 | 231.1%
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE350-CE300 | -0.0026372 | 0 | 0 | -4.2544e-07 | 0.00027963 | 0 | -0.0026372 | 0.00027963 | -0.000393 | 742.2%
CE360-CE300 | 0.032137 | 0.001 | 0 | 0.062561 | 0.037696 | 0.03 | 0 | 0.062561 | 0.027232 | 229.7%
CE400-CE300 | -0.011155 | -0.064 | -0.066 | -3.9918e-07 |  | 0 | -0.066 | 0 | -0.028231 | 233.8%
CE410-CE300 | -0.0072339 | 0 | 0 |  |  | 0 | -0.0072339 | 0 | -0.0018085 | 400%
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | ----
CE430-CE300 | -0.021929 | -0.064 | -0.066 | 0 |  | 0 | -0.066 | 0 | -0.030386 | 217.2%
CE440-CE300 | -0.010585 | -0.064 | -0.066 | -4.885e-15 |  | 0 | -0.066 | 0 | -0.028117 | 234.7%
CE500-CE300 | -0.10787 | -0.105 | -0.149 | -0.076073 | -0.11916 | -0.1 | -0.149 | -0.076073 | -0.10952 | 66.59%
CE510-CE500 | 0.20276 | 0.124 | 0 | 0.15983 | 0.21527 | 0.19 | 0 | 0.21527 | 0.14864 | 144.8%
CE525-CE520 | 0.46939 | 0.476 | 0.42 | 0.40795 | 0.56074 | 0.43 | 0.40795 | 0.56074 | 0.46068 | 33.17%
CE530-CE500 | -0.18393 | -0.198 | -0.154 | -0.1735 | -0.19318 | -0.19 | -0.198 | -0.154 | -0.1821 | 24.16%
CE545-CE540 | 0.4795 | 0.459 | 0.46 | 0.27714 | 0.54916 | 0.44 | 0.27714 | 0.54916 | 0.44413 | 61.25%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-26. Delta Hourly Integrated Maximum and Minimum IDB
Maximum IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0.8779 | 1.78 | 1.61 | 1.4722 | 1.57 | 1 | 0.8779 | 1.78 | 1.385 | 65.13%
CE320-CE300 | 6.1605 | 6.5 | 6.39 | 6.7065 | 7.27 | 5.46 | 5.46 | 7.27 | 6.4145 | 28.22%
CE330-CE300 | 6.0322 | 6.61 | 6.89 | 6.0662 | 6.85 | 5.11 | 5.11 | 6.89 | 6.2597 | 28.44%
CE330-CE320 | -0.1283 | 0.11 | 0.5 | -0.64028 | -0.42 | -0.35 | -0.64028 | 0.5 | -0.15476 | 736.8%
CE340-CE300 | 6.1067 | 6.5 | 6.45 | 6.4953 | 7.1 | 5.39 | 5.39 | 7.1 | 6.3403 | 26.97%
CE330-CE340 | -0.0745 | 0.11 | 0.44 | -0.4291 | -0.25 | -0.28 | -0.4291 | 0.44 | -0.0806 | 1078%
CE350-CE300 | 8.3842 | 9.83 | 9.83 | 9.9997 | 9.95 | 8.81 | 8.3842 | 9.9997 | 9.4673 | 17.06%
CE360-CE300 | 7.5586 | 7.67 | 7.45 | 7.5081 | 7.95 | 6.94 | 6.94 | 7.95 | 7.5128 | 13.44%
CE400-CE300 | 0.9149 | 2.45 | 3.72 | 1.9074 |  | -0.15 | -0.15 | 3.72 | 1.7685 | 218.8%
CE410-CE300 | 0.6257 | 0 | 0 |  |  | 0 | 0 | 0.6257 | 0.15643 | 400%
CE420-CE300 | 0 | 0 | 0 | -1.5401e-11 |  | 0.04 | -1.5401e-11 | 0.04 | 0.008 | 500%
CE430-CE300 | 0.9993 | 0 | 0 | 0.00056794 |  | 0.26 | 0 | 0.9993 | 0.25197 | 396.6%
CE440-CE300 | 0.8453 | 0 | 0 | 0.00049509 |  | 0.07 | 0 | 0.8453 | 0.18316 | 461.5%
CE500-CE300 | -0.3945 | 0 | 0 | -0.0026447 | -0.03 | -1.19 | -1.19 | 0 | -0.26952 | 441.5%
CE510-CE500 | 0.2949 | 0 | 0 | -2.2958e-08 | 0 | 0 | -2.2958e-08 | 0.2949 | 0.04915 | 600%
CE525-CE520 | 19.9568 | 18.95 | 19.12 | 19.999 | 19.02 | 16.38 | 16.38 | 19.999 | 18.9043 | 19.14%
CE530-CE500 | 0.3106 | -0.05 | -0.05 | 0.00043309 | 0 | 0 | -0.05 | 0.3106 | 0.035172 | 1025%
CE545-CE540 | 19.525 | 19.89 | 19.89 | 19.9995 | 19.95 | 20 | 19.525 | 20 | 19.8757 | 2.39%
Minimum IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0 | 0 | 0 | -0.00012889 | 0 | 0 | -0.00012889 | 0 | -2.1482e-05 | 600%
CE320-CE300 | 0 | 1.94 | 1.95 | -0.9638 | 0 | 0 | -0.9638 | 1.95 | 0.4877 | 597.5%
CE330-CE300 | 0 | 0 | 0 | -0.0015681 | 0 | 0 | -0.0015681 | 0 | -0.00026135 | 600%
CE330-CE320 | 0 | -1.94 | -1.95 | 0.96224 | 0 | 0 | -1.95 | 0.96224 | -0.48796 | 596.8%
CE340-CE300 | 0 | 0 | 0 | -0.0015681 | 0 | 0 | -0.0015681 | 0 | -0.00026135 | 600%
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE360-CE300 | 0 | 0 | 0 | 0.00017983 | 0 | 0 | 0 | 0.00017983 | 2.9972e-05 | 600%
CE400-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0 | -3.0198e-14 | 0 | -6.0396e-15 | 500%
CE410-CE300 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | ----
CE420-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0 | -3.0198e-14 | 0 | -6.0396e-15 | 500%
CE430-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0 | -3.0198e-14 | 0 | -6.0396e-15 | 500%
CE440-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0.01 | -3.0198e-14 | 0.01 | 0.002 | 500%
CE500-CE300 | 0.49703 | -0.72 | -0.89 | 0.22125 | 0.54 | 17.05 | -0.89 | 17.05 | 2.783 | 644.6%
CE510-CE500 | 0 | 0 | 0 | 1.2601e-08 | 0 | 0 | 0 | 1.2601e-08 | 2.1002e-09 | 600%
CE525-CE520 | 0.13889 | 0.06 | 0.05 | 0.17974 | 0.03 | 19.44 | 0.03 | 19.44 | 3.3164 | 585.3%
CE530-CE500 | -0.00551 | 0 | 0 | -0.00068516 | 0 | 0 | -0.00551 | 0 | -0.0010325 | 533.6%
CE545-CE540 | 0.22078 | 0.06 | 0.05 | 0.18049 | 0.03 | 18.06 | 0.03 | 18.06 | 3.1002 | 581.6%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-27. Delta Hourly Integrated Maximum and Minimum Zone Humidity Ratio
Maximum Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0.0024658 | 0.005 | 0.0052 | 0.0020112 | 0.001975 | 0.0023 | 0.001975 | 0.0052 | 0.0031587 | 102.1%
CE320-CE300 | 0.0047326 | 0.0039 | 0.0039 | 0.0041811 | 0.00409 | 0.0043 | 0.0039 | 0.0047326 | 0.004184 | 19.9%
CE330-CE300 | 0.0043671 | 0.004 | 0.004 | 0.0043074 | 0.003588 | 0.0043 | 0.003588 | 0.0043671 | 0.0040937 | 19.03%
CE330-CE320 | -0.0003655 | 0.0001 | 0.0001 | 0.00012627 | -0.000502 | 0 | -0.000502 | 0.00012627 | -9.0205e-05 | 696.5%
CE340-CE300 | 0.0045871 | 0.0039 | 0.0037 | 0.0041608 | 0.003815 | 0.0043 | 0.0037 | 0.0045871 | 0.0040771 | 21.76%
CE330-CE340 | -0.00022 | 0.0001 | 0.0003 | 0.00014662 | -0.000227 | 0 | -0.000227 | 0.0003 | 1.6603e-05 | 3174%
CE350-CE300 | 0.0034739 | 0.0061 | 0.0062 | 0.0035636 | 0.003022 | 0.0032 | 0.003022 | 0.0062 | 0.0042599 | 74.6%
CE360-CE300 | 0.0001491 | 0 | 0 | 0.00023399 | 0 | 0 | 0 | 0.00023399 | 6.3848e-05 | 366.5%
CE400-CE300 | 0.0036593 | 0.0032 | 0.0033 | 0.00325 |  | 0.0039 | 0.0032 | 0.0039 | 0.0034619 | 20.22%
CE410-CE300 | 0.0035512 | 0.0031 | 0.0032 |  |  | 0.0039 | 0.0031 | 0.0039 | 0.0034378 | 23.27%
CE420-CE300 | 0.0010125 | 0.0009 | 0.0004 | 0.00096639 |  | 0.0013 | 0.0004 | 0.0013 | 0.00091578 | 98.28%
CE430-CE300 | 0.0029463 | 0.0018 | 0.0019 | 0.0025083 |  | 0.0024 | 0.0018 | 0.0029463 | 0.0023109 | 49.6%
CE440-CE300 | 2.85e-05 | 0 | 0 | 1.3697e-12 |  | 0 | 0 | 2.85e-05 | 5.7e-06 | 500%
CE500-CE300 | -0.0015646 | -0.0019 | -0.0019 | -0.0019411 | -0.001744 | -0.0019 | -0.0019411 | -0.0015646 | -0.0018249 | 20.63%
CE510-CE500 | 0.0001517 | 0 | 0.0001 | 3.4061e-06 | 3e-06 | 0 | 0 | 0.0001517 | 4.3018e-05 | 352.6%
CE525-CE520 | 0.010392 | 0.0103 | 0.0102 | 0.011462 | 0.01006 | 0.0067 | 0.0067 | 0.011462 | 0.0098524 | 48.34%
CE530-CE500 | -0.0047305 | -0.0038 | -0.0037 | -0.0049096 | -0.006222 | -0.00473 | -0.006222 | -0.0037 | -0.004682 | 53.87%
CE545-CE540 | 0.0009051 | 0.0072 | 0.0059 | 1.8956e-13 | 0.003433 | 0.00129 | 1.8956e-13 | 0.0072 | 0.0031214 | 230.7%
Minimum Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 1e-08 | 0 | 0 | 1.5608e-05 | 5.1e-05 | -1e-05 | -1e-05 | 5.1e-05 | 9.4364e-06 | 646.4%
CE320-CE300 | 0 | 0 | 0 | 5.8672e-06 | 0 | 0 | 0 | 5.8672e-06 | 9.7787e-07 | 600%
CE330-CE300 | 0 | 0 | 0 | -1.7036e-08 | 0 | 0 | -1.7036e-08 | 0 | -2.8393e-09 | 600%
CE330-CE320 | 0 | 0 | 0 | -5.8842e-06 | 0 | 0 | -5.8842e-06 | 0 | -9.8071e-07 | 600%
CE340-CE300 | 0 | 0 | 0 | -1.7036e-08 | 0 | 0 | -1.7036e-08 | 0 | -2.8393e-09 | 600%
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE360-CE300 | 0 | 0 | 0 | -2.2318e-11 | 0 | 0 | -2.2318e-11 | 0 | -3.7197e-12 | 600%
CE400-CE300 | 0 | 0 | 0 | 2.2054e-12 |  | 0 | 0 | 2.2054e-12 | 4.4107e-13 | 500%
CE410-CE300 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | ----
CE420-CE300 | 0 | 0 | 0 | -1.2812e-12 |  | 0 | -1.2812e-12 | 0 | -2.5624e-13 | 500%
CE430-CE300 | 0 | 0 | 0 | 2.2054e-12 |  | 0 | 0 | 2.2054e-12 | 4.4107e-13 | 500%
CE440-CE300 | 0 | 0 | 0 | -1.7443e-12 |  | 0 | -1.7443e-12 | 0 | -3.4886e-13 | 500%
CE500-CE300 | 0.0049507 |  |  | 0.0050771 | 0.00494 | 0.00833 | 0.00494 | 0.00833 | 0.0058245 | 58.2%
CE510-CE500 | 0 |  |  | 6.179e-12 | 0 | 0.0002 | 0 | 0.0002 | 5e-05 | 400%
CE525-CE520 | 0.00073266 |  |  | 0.00052082 | 0.000384 | 0.00883 | 0.000384 | 0.00883 | 0.0026169 | 322.8%
CE530-CE500 | -0.00061959 |  |  | -0.00027005 | -0.001454 | -0.00367 | -0.00367 | -0.00027005 | -0.0015034 | 226.1%
CE545-CE540 | 0.0020983 |  |  | 0.002957 | 0.003432 | 0.0028 | 0.0020983 | 0.003432 | 0.0028218 | 47.26%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B16.5.2-28. Delta Hourly Integrated Maximum and Minimum Zone Relative Humidity
Maximum Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 8.9137 | 30.83 | 31.85 | 10.2766 | 9 | 10.75 | 8.9137 | 31.85 | 16.9367 | 135.4%
CE320-CE300 | 13.0466 | 14.06 | 14.82 | 14.5993 | 15 | 14.44 | 13.0466 | 15 | 14.3276 | 13.63%
CE330-CE300 | 7.8699 | 9.11 | 9.09 | 8.5081 | 8 | 11.26 | 7.8699 | 11.26 | 8.973 | 37.78%
CE330-CE320 | -5.1767 | -4.95 | -5.73 | -6.0911 | -7 | -3.18 | -7 | -3.18 | -5.3546 | 71.34%
CE340-CE300 | 11.1401 | 12.02 | 12.41 | 12.4287 | 12 | 12.81 | 11.1401 | 12.81 | 12.1348 | 13.76%
CE330-CE340 | -3.2702 | -2.91 | -3.32 | -3.9205 | -4 | -1.55 | -4 | -1.55 | -3.1618 | 77.49%
CE350-CE300 | 0 | 11.77 | 12.27 | 4.9738e-13 | 2 | 5.21 | 0 | 12.27 | 5.2083 | 235.6%
CE360-CE300 | 0 | 0 | 0 | -0.00016648 | 0 | 0 | -0.00016648 | 0 | -2.7747e-05 | 600%
CE400-CE300 | 14.9642 | 16.22 | 16.72 | 16.269 |  | 18.87 | 14.9642 | 18.87 | 16.6086 | 23.52%
CE410-CE300 | 14.4355 | 15.44 | 15.94 |  |  | 18.74 | 14.4355 | 18.74 | 16.1389 | 26.67%
CE420-CE300 | 2.0519 | 5.16 | 2.68 | 4.9167 |  | 6.41 | 2.0519 | 6.41 | 4.2437 | 102.7%
CE430-CE300 | 11.9195 | 9.08 | 9.58 | 12.3754 |  | 11.5 | 9.08 | 12.3754 | 10.891 | 30.26%
CE440-CE300 | -0.065 | 0 | 0 | 6.6574e-09 |  | 0.07 | -0.065 | 0.07 | 0.001 | 13500%
CE500-CE300 | 31.2108 |  |  | 31.6327 | 32 | -7.36 | -7.36 | 32 | 21.8709 | 180%
CE510-CE500 | 0 |  |  | 0 | 0 | -2.57 | -2.57 | 0 | -0.6425 | 400%
CE525-CE520 | 9.7701 |  |  | 6.1863 | 5 | -20.65 | -20.65 | 9.7701 | 0.076612 | 39706%
CE530-CE500 | -8.9555 |  |  | -3.8398 | -21 | -24.07 | -24.07 | -3.8398 | -14.4663 | 139.8%
CE545-CE540 | 29.6022 |  |  | 41.0554 | 50 | -15.82 | -15.82 | 50 | 26.2094 | 251.1%
Minimum Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 |  |  |  | (Max-Min) | Tested Prg
Case | TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | Mean | /Mean* | Org
CE310-CE300 | 0.0586 | 0 | 0 | 1.1 | 1 | 0.99 | 0 | 1.1 | 0.52476 | 209.6%
CE320-CE300 | 0 | 0 | 0 | 0.23921 | 0 | -2.02 | -2.02 | 0.23921 | -0.2968 | 761.2%
CE330-CE300 | 0 | 0 | 0 | 0.00010511 | 0 | 0 | 0 | 0.00010511 | 1.7518e-05 | 600%
CE330-CE320 | 0 | 0 | 0 | -0.23911 | 0 | 2.02 | -0.23911 | 2.02 | 0.29682 | 761.1%
CE340-CE300 | 0 | 0 | 0 | 0.00010511 | 0 | 0 | 0 | 0.00010511 | 1.7518e-05 | 600%
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ----
CE360-CE300 | 0 | 0 | 0 | -5.7187e-05 | 0 | 0 | -5.7187e-05 | 0 | -9.5312e-06 | 600%
CE400-CE300 | -0.1222 | 0 | 0 | -0.47678 |  | -0.37 | -0.47678 | 0 | -0.1938 | 246%
CE410-CE300 | -0.1221 | 0 | 0 |  |  | -0.36 | -0.36 | 0 | -0.12053 | 298.7%
CE420-CE300 | -0.1213 | 0 | 0 | -0.47665 |  | -0.35 | -0.47665 | 0 | -0.18959 | 251.4%
CE430-CE300 | -0.1234 | 0 | 0 | -0.47678 |  | -0.36 | -0.47678 | 0 | -0.19204 | 248.3%
CE440-CE300 | -0.1243 | 0 | 0 | -0.47678 |  | -0.4 | -0.47678 | 0 | -0.20022 | 238.1%
CE500-CE300 | 40.0742 |  |  | 40.7644 | 39 | 37.89 | 37.89 | 40.7644 | 39.4322 | 7.289%
CE510-CE500 | -1.3175 |  |  | 0.12165 | 0 | 0.32 | -1.3175 | 0.32 | -0.21896 | 747.8%
CE525-CE520 | -15.7395 |  |  | -13.8748 | -17 | -17.5 | -17.5 | -13.8748 | -16.0286 | 22.62%
CE530-CE500 | -23.812 |  |  | -21.139 | -26 | -19.15 | -26 | -19.15 | -22.5253 | 30.41%
CE545-CE540 | -19.3505 |  |  | -16.7748 | -12 | -19.6 | -19.6 | -12 | -16.9313 | 44.89%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## A
RESULTS5-3B.XLS | [5 empty] | INSTRUCTIONS
Output spreadsheet for HVAC BESTEST | [5 empty] | Import data so that Cell A1 of Sec5-3Bout.XLS is in A1 of Sheet "YD" (your data)
SEE CELL G1 FOR INSTRUCTIONS | [5 empty] | Check that the first value (Total consumption kWh for CE300) lands in YD!B62.
Data should land in "YD" cells as tabulated below. Your data will then appear in column H of Sheet A
DO NOT INSERT ROWS ON THIS SHEET! | [5 empty] | and in rightmost column of each table on sheets Q, R, S, T, Qdata, Rdata, Sdata, and Tdata.
Gives locations in participant spreadsheets | [5 empty] | Chart update of "your data" is not automated.
See RESULTS5-3B.DOC for spreadsheet navigation.
Address guide starts at row 56
Raw data presentation starts around row 137
Mean Data starts at row 137
June 28 hourly data starts at row 483
CE500,CE530 avg daily starts at row 826
Hourly Maxima consumption and loads start around row 1044
Deltas start at 1450
SHEET GUIDE:
A: Unformatted data compilation, all programs
B: TRNSYS results
C: DOE-2.2 results
D: DOE-2.1E ESTSC results
E: EnergyPlus results
F: CODYRUN results
G: HOT3000/ESP-r results
YD: Your data
I,J: Extra results data sheets
Q: Absolute sum, mean results, formatted for printout
R: Absolute Max, Min Results, formatted for printout
S: Hourly results, formatted for printout
T: Sensitivity results, formatted for printout
Qdata: Absolute sum, mean results, formatted for chart source data
Rdata: Absolute Max, Min Results, formatted for chart source data
Sdata: Hourly results, formatted for chart source data
Tdata: Sensitivity results, formatted for chart source data
Sheets after "Tdata" are Charts
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | CE300 Only, Maxima
C E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [15 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio |  | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
CE300 | B62 | C62 | D62 | E62 | F62 | G62 | H62 | I62 | J62 | K62 | L62 | M62 | N62 |  | CE300 | Q62 | R62 | S62 | T62 | U62 | V62 | W62 | X62 | Y62 | Z62 | AA62 | AB62 | AC62 | AD62 | AE62 | AF62 | AG62 | AH62
CE310 | B63 | C63 | D63 | E63 | F63 | G63 | H63 | I63 | J63 | K63 | L63 |  |  |  | CE310 | Q63 | R63 | S63 | T63 | U63 | V63 | W63 | X63 | Y63 | Z63 | AA63 | AB63
CE320 | B64 | C64 | D64 | E64 | F64 | G64 | H64 | I64 | J64 | K64 | L64 |  |  |  | CE320 | Q64 | R64 | S64 | T64 | U64 | V64 | W64 | X64 | Y64 | Z64 | AA64 | AB64
CE330 | B65 | C65 | D65 | E65 | F65 | G65 | H65 | I65 | J65 | K65 | L65 |  |  |  | CE330 | Q65 | R65 | S65 | T65 | U65 | V65 | W65 | X65 | Y65 | Z65 | AA65 | AB65
CE340 | B66 | C66 | D66 | E66 | F66 | G66 | H66 | I66 | J66 | K66 | L66 |  |  |  | CE340 | Q66 | R66 | S66 | T66 | U66 | V66 | W66 | X66 | Y66 | Z66 | AA66 | AB66
CE350 | B67 | C67 | D67 | E67 | F67 | G67 | H67 | I67 | J67 | K67 | L67 |  |  |  | CE350 | Q67 | R67 | S67 | T67 | U67 | V67 | W67 | X67 | Y67 | Z67 | AA67 | AB67
CE360 | B68 | C68 | D68 | E68 | F68 | G68 | H68 | I68 | J68 | K68 | L68 |  |  |  | CE360 | Q68 | R68 | S68 | T68 | U68 | V68 | W68 | X68 | Y68 | Z68 | AA68 | AB68
CE400 | B69 | C69 | D69 | E69 | F69 | G69 | H69 | I69 | J69 | K69 | L69 |  |  |  | CE400 | Q69 | R69 | S69 | T69 | U69 | V69 | W69 | X69 | Y69 | Z69 | AA69 | AB69
CE410 | B70 | C70 | D70 | E70 | F70 | G70 | H70 | I70 | J70 | K70 | L70 |  |  |  | CE410 | Q70 | R70 | S70 | T70 | U70 | V70 | W70 | X70 | Y70 | Z70 | AA70 | AB70
CE420 | B71 | C71 | D71 | E71 | F71 | G71 | H71 | I71 | J71 | K71 | L71 |  |  |  | CE420 | Q71 | R71 | S71 | T71 | U71 | V71 | W71 | X71 | Y71 | Z71 | AA71 | AB71
CE430 | B72 | C72 | D72 | E72 | F72 | G72 | H72 | I72 | J72 | K72 | L72 |  |  |  | CE430 | Q72 | R72 | S72 | T72 | U72 | V72 | W72 | X72 | Y72 | Z72 | AA72 | AB72
CE440 | B73 | C73 | D73 | E73 | F73 | G73 | H73 | I73 | J73 | K73 | L73 |  |  |  | CE440 | Q73 | R73 | S73 | T73 | U73 | V73 | W73 | X73 | Y73 | Z73 | AA73 | AB73
CE500 | B74 | C74 | D74 | E74 | F74 | G74 | H74 | I74 | J74 | K74 | L74 |  |  |  | CE500 | Q74 | R74 | S74 | T74 | U74 | V74 | W74 | X74 | Y74 | Z74 | AA74 | AB74
CE500 May-Sep | B75 | C75 | D75 | E75 | F75 | G75 | H75 | I75 | J75 | K75 | L75 |  |  |  | CE510 | Q75 | R75 | S75 | T75 | U75 | V75 | W75 | X75 | Y75 | Z75 | AA75 | AB75
CE510 May-Sep | B76 | C76 | D76 | E76 | F76 | G76 | H76 | I76 | J76 | K76 | L76 |  |  |  | CE520 | Q76 | R76 | S76 | T76 | U76 | V76 | W76 | X76 | Y76 | Z76 | AA76 | AB76
CE520 | B77 | C77 | D77 | E77 | F77 | G77 | H77 | I77 | J77 | K77 | L77 |  |  |  | CE522 | Q77 | R77 | S77 | T77 | U77 | V77 | W77 | X77 | Y77 | Z77 | AA77 | AB77
CE522 | B78 | C78 | D78 | E78 | F78 | G78 | H78 | I78 | J78 | K78 | L78 |  |  |  | CE525 | Q78 | R78 | S78 | T78 | U78 | V78 | W78 | X78 | Y78 | Z78 | AA78 | AB78
CE525 | B79 | C79 | D79 | E79 | F79 | G79 | H79 | I79 | J79 | K79 | L79 |  |  |  | CE530 | Q79 | R79 | S79 | T79 | U79 | V79 | W79 | X79 | Y79 | Z79 | AA79 | AB79
CE530 | B80 | C80 | D80 | E80 | F80 | G80 | H80 | I80 | J80 | K80 | L80 |  |  |  | CE540 | Q80 | R80 | S80 | T80 | U80 | V80 | W80 | X80 | Y80 | Z80 | AA80 | AB80
CE540 | B81 | C81 | D81 | E81 | F81 | G81 | H81 | I81 | J81 | K81 | L81 |  |  |  | CE545 | Q81 | R81 | S81 | T81 | U81 | V81 | W81 | X81 | Y81 | Z81 | AA81 | AB81
CE545 | B82 | C82 | D82 | E82 | F82 | G82 | H82 | I82 | J82 | K82 | L82
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e C E 3 0 0 | [11 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | B89 | C89 | D89 | E89 | F89 | G89 | H89 | I89 | J89 | K89 | L89 |  |  |  | CE300 | Q89 | R89 | S89 | T89 | U89 | V89 | W89 | X89 | Y89 | Z89 | AA89 | AB89 | AC89 | AD89 | AE89 | AF89 | AG89 | AH89 | AI89 | AJ89 | AK89 | AL89 | AM89 | AN89
2 | B90 | C90 | D90 | E90 | F90 | G90 | H90 | I90 | J90 | K90 | L90 |  |  |  | CE310 | Q90 | R90 | S90 | T90 | U90 | V90 | W90 | X90 | Y90 | Z90 | AA90 | AB90 | AC90 | AD90 | AE90 | AF90 | AG90 | AH90 | AI90 | AJ90 | AK90 | AL90 | AM90 | AN90
3 | B91 | C91 | D91 | E91 | F91 | G91 | H91 | I91 | J91 | K91 | L91 |  |  |  | CE320 | Q91 | R91 | S91 | T91 | U91 | V91 | W91 | X91 | Y91 | Z91 | AA91 | AB91 | AC91 | AD91 | AE91 | AF91 | AG91 | AH91 | AI91 | AJ91 | AK91 | AL91 | AM91 | AN91
4 | B92 | C92 | D92 | E92 | F92 | G92 | H92 | I92 | J92 | K92 | L92 |  |  |  | CE330 | Q92 | R92 | S92 | T92 | U92 | V92 | W92 | X92 | Y92 | Z92 | AA92 | AB92 | AC92 | AD92 | AE92 | AF92 | AG92 | AH92 | AI92 | AJ92 | AK92 | AL92 | AM92 | AN92
5 | B93 | C93 | D93 | E93 | F93 | G93 | H93 | I93 | J93 | K93 | L93 |  |  |  | CE340 | Q93 | R93 | S93 | T93 | U93 | V93 | W93 | X93 | Y93 | Z93 | AA93 | AB93 | AC93 | AD93 | AE93 | AF93 | AG93 | AH93 | AI93 | AJ93 | AK93 | AL93 | AM93 | AN93
6 | B94 | C94 | D94 | E94 | F94 | G94 | H94 | I94 | J94 | K94 | L94 |  |  |  | CE350 | Q94 | R94 | S94 | T94 | U94 | V94 | W94 | X94 | Y94 | Z94 | AA94 | AB94 | AC94 | AD94 | AE94 | AF94 | AG94 | AH94 | AI94 | AJ94 | AK94 | AL94 | AM94 | AN94
7 | B95 | C95 | D95 | E95 | F95 | G95 | H95 | I95 | J95 | K95 | L95 |  |  |  | CE360 | Q95 | R95 | S95 | T95 | U95 | V95 | W95 | X95 | Y95 | Z95 | AA95 | AB95 | AC95 | AD95 | AE95 | AF95 | AG95 | AH95 | AI95 | AJ95 | AK95 | AL95 | AM95 | AN95
8 | B96 | C96 | D96 | E96 | F96 | G96 | H96 | I96 | J96 | K96 | L96 |  |  |  | CE400 | Q96 | R96 | S96 | T96 | U96 | V96 | W96 | X96 | Y96 | Z96 | AA96 | AB96 | AC96 | AD96 | AE96 | AF96 | AG96 | AH96 | AI96 | AJ96 | AK96 | AL96 | AM96 | AN96
9 | B97 | C97 | D97 | E97 | F97 | G97 | H97 | I97 | J97 | K97 | L97 |  |  |  | CE410 | Q97 | R97 | S97 | T97 | U97 | V97 | W97 | X97 | Y97 | Z97 | AA97 | AB97 | AC97 | AD97 | AE97 | AF97 | AG97 | AH97 | AI97 | AJ97 | AK97 | AL97 | AM97 | AN97
10 | B98 | C98 | D98 | E98 | F98 | G98 | H98 | I98 | J98 | K98 | L98 |  |  |  | CE420 | Q98 | R98 | S98 | T98 | U98 | V98 | W98 | X98 | Y98 | Z98 | AA98 | AB98 | AC98 | AD98 | AE98 | AF98 | AG98 | AH98 | AI98 | AJ98 | AK98 | AL98 | AM98 | AN98
11 | B99 | C99 | D99 | E99 | F99 | G99 | H99 | I99 | J99 | K99 | L99 |  |  |  | CE430 | Q99 | R99 | S99 | T99 | U99 | V99 | W99 | X99 | Y99 | Z99 | AA99 | AB99 | AC99 | AD99 | AE99 | AF99 | AG99 | AH99 | AI99 | AJ99 | AK99 | AL99 | AM99 | AN99
12 | B100 | C100 | D100 | E100 | F100 | G100 | H100 | I100 | J100 | K100 | L100 |  |  |  | CE440 | Q100 | R100 | S100 | T100 | U100 | V100 | W100 | X100 | Y100 | Z100 | AA100 | AB100 | AC100 | AD100 | AE100 | AF100 | AG100 | AH100 | AI100 | AJ100 | AK100 | AL100 | AM100 | AN100
13 | B101 | C101 | D101 | E101 | F101 | G101 | H101 | I101 | J101 | K101 | L101 |  |  |  | CE500 | Q101 | R101 | S101 | T101 | U101 | V101 | W101 | X101 | Y101 | Z101 | AA101 | AB101 | AC101 | AD101 | AE101 | AF101 | AG101 | AH101 | AI101 | AJ101 | AK101 | AL101 | AM101 | AN101
14 | B102 | C102 | D102 | E102 | F102 | G102 | H102 | I102 | J102 | K102 | L102 |  |  |  | CE510 | Q102 | R102 | S102 | T102 | U102 | V102 | W102 | X102 | Y102 | Z102 | AA102 | AB102 | AC102 | AD102 | AE102 | AF102 | AG102 | AH102 | AI102 | AJ102 | AK102 | AL102 | AM102 | AN102
15 | B103 | C103 | D103 | E103 | F103 | G103 | H103 | I103 | J103 | K103 | L103 |  |  |  | CE520 | Q103 | R103 | S103 | T103 | U103 | V103 | W103 | X103 | Y103 | Z103 | AA103 | AB103 | AC103 | AD103 | AE103 | AF103 | AG103 | AH103 | AI103 | AJ103 | AK103 | AL103 | AM103 | AN103
16 | B104 | C104 | D104 | E104 | F104 | G104 | H104 | I104 | J104 | K104 | L104 |  |  |  | CE522 | Q104 | R104 | S104 | T104 | U104 | V104 | W104 | X104 | Y104 | Z104 | AA104 | AB104 | AC104 | AD104 | AE104 | AF104 | AG104 | AH104 | AI104 | AJ104 | AK104 | AL104 | AM104 | AN104
17 | B105 | C105 | D105 | E105 | F105 | G105 | H105 | I105 | J105 | K105 | L105 |  |  |  | CE525 | Q105 | R105 | S105 | T105 | U105 | V105 | W105 | X105 | Y105 | Z105 | AA105 | AB105 | AC105 | AD105 | AE105 | AF105 | AG105 | AH105 | AI105 | AJ105 | AK105 | AL105 | AM105 | AN105
18 | B106 | C106 | D106 | E106 | F106 | G106 | H106 | I106 | J106 | K106 | L106 |  |  |  | CE530 | Q106 | R106 | S106 | T106 | U106 | V106 | W106 | X106 | Y106 | Z106 | AA106 | AB106 | AC106 | AD106 | AE106 | AF106 | AG106 | AH106 | AI106 | AJ106 | AK106 | AL106 | AM106 | AN106
19 | B107 | C107 | D107 | E107 | F107 | G107 | H107 | I107 | J107 | K107 | L107 |  |  |  | CE540 | Q107 | R107 | S107 | T107 | U107 | V107 | W107 | X107 | Y107 | Z107 | AA107 | AB107 | AC107 | AD107 | AE107 | AF107 | AG107 | AH107 | AI107 | AJ107 | AK107 | AL107 | AM107 | AN107
20 | B108 | C108 | D108 | E108 | F108 | G108 | H108 | I108 | J108 | K108 | L108 |  |  |  | CE545 | Q108 | R108 | S108 | T108 | U108 | V108 | W108 | X108 | Y108 | Z108 | AA108 | AB108 | AC108 | AD108 | AE108 | AF108 | AG108 | AH108 | AI108 | AJ108 | AK108 | AL108 | AM108 | AN108
21 | B109 | C109 | D109 | E109 | F109 | G109 | H109 | I109 | J109 | K109 | L109
22 | B110 | C110 | D110 | E110 | F110 | G110 | H110 | I110 | J110 | K110 | L110
23 | B111 | C111 | D111 | E111 | F111 | G111 | H111 | I111 | J111 | K111 | L111
24 | B112 | C112 | D112 | E112 | F112 | G112 | H112 | I112 | J112 | K112 | L112
C a s e C E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | B120 | C120 | D120 | E120 | F120 | G120 | H120 | I120 | J120 | K120 | L120
June 25 | B121 | C121 | D121 | E121 | F121 | G121 | H121 | I121 | J121 | K121 | L121
C a s e C E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | B129 | C129 | D129 | E129 | F129 | G129 | H129 | I129 | J129 | K129 | L129
June 25 | B130 | C130 | D130 | E130 | F130 | G130 | H130 | I130 | J130 | K130 | L130
Energy Consumption, Total (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 35633.7773 | 34750 | 34755 | 34745.6375 | 34976.411 | 35070
CE310 | 39973.3798 | 39379 | 39384 | 39290.3641 | 39519.569 | 39608
CE320 | 40059.657 | 38745 | 38792 | 39079.1002 | 39400.815 | 39457
CE330 | 40963.3004 | 39708 | 39438 | 40143.3736 | 40535.137 | 40330
CE340 | 40619.2951 | 39358 | 39265 | 39783.0185 | 40065.261 | 39947
CE350 | 32236.9795 | 30547 | 30548 | 31145.1136 | 31586.592 | 31742
CE360 | 55298.7917 | 54064 | 54016 | 54704.711 | 54843.258 | 55068
CE400 | 32045.1536 | 30846 | 30876 | 31012.681 |  | 31413
CE410 | 32078.4319 | 31668 | 31699 |  |  | 31503
CE420 | 33387.0076 | 32530 | 32910 | 32735.5046 |  | 33208
CE430 | 32538.0313 | 31932 | 31811 | 31772.397 |  | 31818
CE440 | 33691.321 | 33032 | 32973 | 33031.6453 |  | 33248
CE500 | 22337.887 | 22817 | 22822 | 23034.6081 | 22322.953 | 23138
CE500 May-Sep | 17390.8511 | 17872 | 17870 | 17996.1112 | 17434.537 | 18051
CE510 May-Sep | 34608.7754 | 35971 | 35970 | 35732.4838 | 34848.637 | 35845
CE520 | 24986.582 | 25389 | 25390 | 25017.1776 | 25131.07 | 25781
CE522 | 23544.1607 | 24293 | 24307 | 24077.7247 | 23619.744 | 24360
CE525 | 20320.874 | 20408 | 20421 | 20701.5603 | 20241.713 | 21323
CE530 | 17281.271 | 17540 | 17537 | 17741.9432 | 17442.468 | 17875
CE540 | 19430.3785 | 19878 | 19874 | 19061.1125 | 19536.572 | 20164
CE545 | 15687.0796 | 15802 | 15791 | 16635.7259 | 15791.081 | 16339
Energy Consumption, Compressor (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 22353.5343 | 21569 | 21573 | 23883.5456 | 21770.001 | 21876
CE310 | 26339.6254 | 25813 | 25817 | 28428.2722 | 25936.821 | 26053
CE320 | 26433.1374 | 25250 | 25294 | 28217.0083 | 25846.026 | 25912
CE330 | 27299.7321 | 26172 | 25925 | 29281.2817 | 26927.733 | 26775
CE340 | 26962.9373 | 25829 | 25745 | 28920.9266 | 26472.79 | 26400
CE350 | 19316.8404 | 17802 | 17801 | 20283.0217 | 18738.055 | 18891
CE360 | 40105.8399 | 38999 | 38955 | 43842.619 | 39697.162 | 39941
CE400 | 19178.9487 | 18106 | 18131 | 20150.589 |  | 18629
CE410 | 19204.4944 | 18823 | 18850 |  |  | 18685
CE420 | 20358.5854 | 19596 | 19934 | 21873.4127 |  | 20214
CE430 | 19598.6211 | 19059 | 18951 | 20910.3051 |  | 18966
CE440 | 20629.1333 | 20042 | 19989 | 22169.5533 |  | 20249
CE500 | 17854.2956 | 18473 | 18478 | 20406.2816 | 17857.852 | 18522
CE500 May-Sep | 13942.1479 | 14508 | 14506 | 15967.1478 | 13988.512 | 14491
CE510 May-Sep | 27747.879 | 28811 | 28810 | 31669.1814 | 27901.957 | 28721
CE520 | 19521.2767 | 20121 | 20126 | 21998.5084 | 19654.972 | 20185
CE522 | 18620.3108 | 19407 | 19418 | 21235.1683 | 18689.799 | 19281
CE525 | 16557.8748 | 16880 | 16893 | 18521.6644 | 16506.802 | 17443
CE530 | 13656.9951 | 14127 | 14124 | 15651.7258 | 13855.928 | 14172
CE540 | 15020.7433 | 15680 | 15677 | 16751.8668 | 15163.82 | 15664
CE545 | 12621.8685 | 12967 | 12957 | 14764.8235 | 12750.623 | 13215
Energy Consumption, Condenser Fan (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 2400.3229 | 2301 | 2302 |  | 2326.49 | 2323
CE310 | 2753.8345 | 2686 | 2687 |  | 2702.828 | 2691
CE320 | 2746.5996 | 2615 | 2618 |  | 2674.869 | 2681
CE330 | 2783.6483 | 2656 | 2633 |  | 2727.484 | 2693
CE340 | 2776.4378 | 2649 | 2640 |  | 2712.551 | 2684
CE350 | 2040.2191 | 1865 | 1867 |  | 1968.617 | 1970
CE360 | 4313.0318 | 4185 | 4181 |  | 4266.176 | 4272
CE400 | 1986.2848 | 1860 | 1865 |  |  | 1902
CE410 | 1994.0175 | 1965 | 1969 |  |  | 1936
CE420 | 2148.5022 | 2054 | 2096 |  |  | 2115
CE430 | 2059.4903 | 1993 | 1980 |  |  | 1970
CE440 | 2182.2678 | 2110 | 2104 |  |  | 2120
CE500 | 1919.7698 | 1975 | 1975 |  | 1911.869 | 1976
CE500 May-Sep | 1476.6547 | 1527 | 1527 |  | 1475.528 | 1524
CE510 May-Sep | 2937.6766 | 3061 | 3061 |  | 2974.4 | 3050
CE520 | 2340.1169 | 2394 | 2393 |  | 2344.827 | 2396
CE522 | 2108.2783 | 2182 | 2182 |  | 2110.833 | 2174
CE525 | 1611.2289 | 1642 | 1643 |  | 1599.203 | 1663
CE530 | 1551.8309 | 1580 | 1580 |  | 1535.684 | 1585
CE540 | 1888.1035 | 1940 | 1939 |  | 1872.336 | 1926
CE545 | 1312.4522 | 1334 | 1333 |  | 1301.791 | 1337
Energy Consumption, ID Fan (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
CE310 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
CE320 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
CE330 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
CE340 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
CE350 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
CE360 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
CE400 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880
CE410 | 10879.92 | 10880 | 10880 |  |  | 10880
CE420 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880
CE430 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880
CE440 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880
CE500 | 2563.8216 | 2369 | 2369 | 2628.3265 | 2553.232 | 2639
CE500 May-Sep | 1972.0485 | 1837 | 1837 | 2028.9634 | 1970.497 | 2035
CE510 May-Sep | 3923.2198 | 4099 | 4099 | 4063.3025 | 3972.28 | 4073
CE520 | 3125.1884 | 2874 | 2871 | 3018.6693 | 3131.271 | 3200
CE522 | 2815.5716 | 2704 | 2707 | 2842.5564 | 2819.112 | 2904
CE525 | 2151.7702 | 1886 | 1885 | 2179.8959 | 2135.708 | 2221
CE530 | 2072.4451 | 1833 | 1833 | 2090.2174 | 2050.856 | 2117
CE540 | 2521.5317 | 2258 | 2258 | 2309.2457 | 2500.416 | 2573
CE545 | 1752.7588 | 1501 | 1501 | 1870.9023 | 1738.667 | 1786
Coil Load, total (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 80426.8675 | 77283.4356 | 77291.9355 | 77317.9497 | 77744.589 | 78257
CE310 | 99342.1316 | 97394.7852 | 97412.0781 | 96447.5904 | 97295.866 | 97261
CE320 | 99791.678 | 96356.3319 | 96493.2096 | 96083.5597 | 97141.307 | 96957
CE330 | 105012.8715 | 100729.9701 | 100993.467 | 102211.3604 | 103712.915 | 102008
CE340 | 102727.9789 | 99027.6453 | 99223.143 | 99708.5156 | 100676.21 | 99753
CE350 | 69387.9976 | 63736.3536 | 63634.6479 | 65790.3681 | 66860.163 | 67389
CE360 | 162974.0626 | 159807.2061 | 159853.809 | 161248.445 | 161200.179 | 162168
CE400 | 68792.8221 | 64917.5466 | 65025.1143 | 65413.8414 |  | 66898
CE410 | 68672.8538 | 66779.6109 | 66843.5067 |  |  | 66175
CE420 | 72609.3074 | 69610.9569 | 70882.1316 | 70349.4668 |  | 71803
CE430 | 69756.312 | 67640.7387 | 67219.2609 | 67141.3524 |  | 67200
CE440 | 73711.3635 | 71380.1085 | 71181.0936 | 71417.307 |  | 72029
CE500 | 63357.1063 | 65995.8615 | 65992.3443 | 65571.1832 | 63105.366 | 65614
CE500 May-Sep | 48443.4308 | 50692.8174 | 50690.4726 | 50354.2901 | 48439.57 | 50357
CE510 May-Sep | 108974.3099 | 114017.9517 | 114015.3138 | 112792.6463 | 108979.013 | 112781
CE520 | 63421.5444 | 66571.2168 | 66565.3548 | 66087.7865 | 63212.102 | 66146
CE522 | 63389.2228 | 66373.0812 | 66371.9088 | 65850.6755 | 63157.03 | 65900
CE525 | 63292.9454 | 65399.1099 | 65395.0065 | 64973.3114 | 63001.558 | 65155
CE530 | 45045.848 | 46634.2617 | 46630.7445 | 46944.3571 | 44875.414 | 47002
CE540 | 45112.827 | 47129.8938 | 47126.0835 | 47296.6053 | 44979.842 | 47462
CE545 | 44981.3517 | 46239.7491 | 46235.9388 | 46611.8912 | 44775.11 | 46668
Coil Load, Sensible (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 56661.7484 | 55796.8608 | 55804.7745 | 55251.9574 | 55209.465 | 55191
CE310 | 56256.3775 | 56300.9928 | 56312.7168 | 55225.158 | 55185.072 | 55083
CE320 | 62859.2053 | 62697.021 | 62746.848 | 62043.4531 | 62008.804 | 62734
CE330 | 63083.3765 | 63311.0655 | 63327.7722 | 63778.6556 | 62649.459 | 61822
CE340 | 63032.6061 | 63053.4306 | 63110.5851 | 62885.8356 | 62380.56 | 61406
CE350 | 50370.8304 | 47684.439 | 47676.5253 | 48545.0123 | 48588.802 | 48768
CE360 | 134976.8351 | 134919.792 | 134939.7228 | 135287.1959 | 134205.707 | 134697
CE400 | 41952.3595 | 41419.1334 | 41437.0125 | 40687.7468 |  | 41181
CE410 | 45676.6456 | 47658.6462 | 47659.8186 |  |  | 45585
CE420 | 50389.8247 | 49666.0881 | 50612.2149 | 49523.9279 |  | 49984
CE430 | 47863.3462 | 47731.335 | 47454.0624 | 46738.5816 |  | 46143
CE440 | 50876.0725 | 50592.5772 | 50492.0439 | 50060.1752 |  | 49785
CE500 | 45043.8 | 47649.8532 | 47646.0429 | 47491.2402 | 44874.225 | 47530
CE500 May-Sep | 34443.2344 | 36595.5867 | 36593.2419 | 36475.5877 | 34448.151 | 36480
CE510 May-Sep | 77489.4321 | 82305.7041 | 82303.0662 | 81566.3401 | 77498.985 | 81563
CE520 | 45109.6141 | 48101.5203 | 48095.6583 | 47986.359 | 44976.724 | 48059
CE522 | 45076.0312 | 47962.2978 | 47961.4185 | 47757.6997 | 44924.113 | 47795
CE525 | 44979.0103 | 47217.5307 | 47213.4273 | 46929.7377 | 44775.105 | 47110
CE530 | 45045.848 | 46573.59 | 46570.0728 | 46944.356 | 44874.225 | 47002
CE540 | 45111.8473 | 47022.9123 | 47019.102 | 47288.0472 | 44976.747 | 47460
CE545 | 44981.3517 | 46214.2494 | 46210.4391 | 46611.8912 | 44775.105 | 46668
Coil Load, Latent (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 23765.119 | 21486.5748 | 21487.161 | 22065.9923 | 22535.143 | 23067
CE310 | 43085.7541 | 41093.7924 | 41099.3613 | 41222.4325 | 42110.836 | 42178
CE320 | 36932.4726 | 33659.3109 | 33746.3616 | 34040.1066 | 35132.592 | 34224
CE330 | 41929.495 | 37418.9046 | 37665.6948 | 38432.7048 | 41063.373 | 40186
CE340 | 39695.3729 | 35974.2147 | 36112.5579 | 36822.6801 | 38295.624 | 38346
CE350 | 19017.1672 | 16051.9146 | 15958.1226 | 17245.3558 | 18271.394 | 18621
CE360 | 27997.2274 | 24887.4141 | 24914.0862 | 25961.249 | 26994.482 | 27470
CE400 | 26840.4626 | 23498.4132 | 23588.1018 | 24726.0946 |  | 25717
CE410 | 22996.2083 | 19120.9647 | 19183.6881 |  |  | 20590
CE420 | 22219.4827 | 19944.8688 | 20269.9167 | 20825.5388 |  | 21855
CE430 | 21892.9657 | 19909.4037 | 19765.1985 | 20402.7708 |  | 21057
CE440 | 22835.291 | 20787.5313 | 20689.0497 | 21357.1318 |  | 22244
CE500 | 18313.3062 | 18346.0083 | 18346.3014 | 18079.943 | 18231.141 | 18084
CE500 May-Sep | 14000.1964 | 14097.2307 | 14097.2307 | 13878.7023 | 13991.418 | 13877
CE510 May-Sep | 31484.8778 | 31712.2476 | 31712.2476 | 31226.3062 | 31479.856 | 31217
CE520 | 18311.9303 | 18469.6965 | 18469.6965 | 18101.4275 | 18235.133 | 18087
CE522 | 18313.1916 | 18410.7834 | 18410.4903 | 18092.9758 | 18233.151 | 18104
CE525 | 18313.9351 | 18181.5792 | 18181.5792 | 18043.5737 | 18226.509 | 18045
CE530 | 0 | 60.6717 | 60.6717 | 0.0011462 | 1.186 | 0
CE540 | 0.97976 | 106.9815 | 106.9815 | 8.5582 | 3.09 | 2
CE545 | 0 | 25.4997 | 25.4997 | 3.4549e-12 | 0.004 | 0
Mean COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 3.2491 | 3.2377 | 3.2374 | 3.2373 | 3.2264 | 3.23
CE310 | 3.4146 | 3.4175 | 3.4175 | 3.3927 | 3.3972 | 3.38
CE320 | 3.4199 | 3.458 | 3.4571 | 3.4052 | 3.406 | 3.39
CE330 | 3.4907 | 3.4942 | 3.5364 | 3.4907 | 3.4973 | 3.46
CE340 | 3.4543 | 3.4773 | 3.4956 | 3.4476 | 3.4495 | 3.42
CE350 | 3.2489 | 3.2408 | 3.2354 | 3.2436 | 3.2289 | 3.23
CE360 | 3.669 | 3.7006 | 3.7058 | 3.6779 | 3.6667 | 3.66
CE400 | 3.2503 | 3.2514 | 3.2519 | 3.2462 |  | 3.26
CE410 | 3.2395 | 3.2124 | 3.2107 |  |  | 3.21
CE420 | 3.2261 | 3.2153 | 3.2175 | 3.2162 |  | 3.21
CE430 | 3.2208 | 3.213 | 3.2115 | 3.2109 |  | 3.21
CE440 | 3.2313 | 3.2223 | 3.2219 | 3.2214 |  | 3.22
CE500 | 3.2041 | 3.2275 | 3.2265 | 3.2133 | 3.192 | 3.2
CE500 May-Sep | 3.1418 | 3.1614 | 3.1616 | 3.1536 | 3.1324 | 3.14
CE510 May-Sep | 3.5513 | 3.5774 | 3.5774 | 3.5616 | 3.5295 | 3.55
CE520 | 2.9011 | 2.9567 | 2.956 | 3.0042 | 2.8733 | 2.92
CE522 | 3.0581 | 3.0744 | 3.0728 | 3.101 | 3.0363 | 3.07
CE525 | 3.4835 | 3.5309 | 3.528 | 3.508 | 3.4796 | 3.41
CE530 | 2.9618 | 2.969 | 2.9694 | 2.9993 | 2.9156 | 2.98
CE540 | 2.668 | 2.6748 | 2.6752 | 2.8234 | 2.6403 | 2.69
CE545 | 3.2281 | 3.2333 | 3.2355 | 3.157 | 3.1863 | 3.2
Mean IDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 23.6243 | 24.0556 | 24.0556 | 24.0907 | 24.0816 | 23.99
CE310 | 23.7556 | 24.1111 | 24.0556 | 24.0921 | 24.0897 | 24.01
CE320 | 23.9005 | 24.3889 | 24.3889 | 24.2544 | 24.3274 | 24.53
CE330 | 23.8797 | 24.2778 | 24.2778 | 24.2734 | 24.2955 | 24.18
CE340 | 23.8756 | 24.2778 | 24.2778 | 24.2983 | 24.3089 | 24.21
CE350 | 25.6595 | 26.1667 | 26.1667 | 26.2416 | 26.2686 | 26.15
CE360 | 25.3649 | 25.6111 | 25.5556 | 25.3232 | 25.4809 | 25.37
CE400 | 24.1263 | 24.0556 | 24.0556 | 24.092 |  | 23.99
CE410 | 24.1221 | 24.0556 | 24.0556 |  |  | 23.99
CE420 | 23.9262 | 24.0556 | 24.0556 | 24.0906 |  | 23.99
CE430 | 23.9916 | 24.0556 | 24.0556 | 24.0906 |  | 23.99
CE440 | 23.9118 | 24.0556 | 24.0556 | 24.0907 |  | 23.99
CE500 | 20.2342 | 20.6667 | 20.5556 | 20.3795 | 21.0978 | 22.86
CE500 May-Sep | 24.5723 | 25 | 25 | 24.9823 | 25 | 25
CE510 May-Sep | 25.8168 | 25.1111 | 25.1111 | 24.9596 | 25 | 25
CE520 | 13.5171 | 13.7778 | 13.7222 | 13.5769 | 14.1421 | 14.89
CE522 | 16.9456 | 17.2778 | 17.2222 | 16.9966 | 17.729 | 18.7
CE525 | 26.8443 | 27.3889 | 27.2778 | 27.1041 | 27.7709 | 30.69
CE530 | 20.0253 | 20.6111 | 20.5556 | 20.586 | 21.0978 | 22.86
CE540 | 13.2893 | 13.7778 | 13.7222 | 13.7934 | 14.1406 | 14.98
CE545 | 26.6052 | 27.3333 | 27.2778 | 27.3123 | 27.7166 | 30.69
Mean Humidity Ratio
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 0.0090691 | 0.0092 | 0.0092 | 0.0092861 | 0.0091748 | 0.0092
CE310 | 0.011071 | 0.0113 | 0.0113 | 0.011261 | 0.011175 | 0.0111
CE320 | 0.009988 | 0.0101 | 0.0101 | 0.010114 | 0.010049 | 0.0099
CE330 | 0.0097409 | 0.0099 | 0.0099 | 0.0099684 | 0.0098116 | 0.0099
CE340 | 0.0097914 | 0.0099 | 0.0099 | 0.0099837 | 0.0098683 | 0.0099
CE350 | 0.0097059 | 0.01 | 0.01 | 0.0099257 | 0.0097585 | 0.00977
CE360 | 0.0084995 | 0.0087 | 0.0087 | 0.0087659 | 0.0085524 | 0.00858
CE400 | 0.0098011 | 0.01 | 0.01 | 0.010087 |  | 0.01
CE410 | 0.0097405 | 0.0095 | 0.0095 |  |  | 0.0095
CE420 | 0.0092639 | 0.0094 | 0.0094 | 0.0094486 |  | 0.0093
CE430 | 0.0093103 | 0.0094 | 0.0094 | 0.0094895 |  | 0.0094
CE440 | 0.0091578 | 0.0093 | 0.0093 | 0.0093341 |  | 0.0092
CE500 | 0.0097753 |  |  | 0.0093728 | 0.010218 | 0.0107
CE500 May-Sep | 0.011021 | 0.0114 | 0.0114 | 0.011322 | 0.011329 | 0.0109
CE510 May-Sep | 0.011395 | 0.0114 | 0.0114 | 0.011329 | 0.011328 | 0.0109
CE520 | 0.0066924 |  |  | 0.0060452 | 0.0070234 | 0.00763
CE522 | 0.0081904 |  |  | 0.0076074 | 0.0085797 | 0.00901
CE525 | 0.013713 |  |  | 0.013802 | 0.01398 | 0.0151
CE530 | 0.0062265 |  |  | 0.0067122 | 0.0057975 | 0.00667
CE540 | 0.0044601 |  |  | 0.0043466 | 0.0038546 | 0.00463
CE545 | 0.0062265 |  |  | 0.0067334 | 0.006749 | 0.00722
Mean Relative Humidity
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE300 | 48.6149 | 48.26 | 48.28 | 48.5913 | 47.8261 | 47.93
CE310 | 58.3307 | 58.51 | 58.53 | 58.5512 | 57.841 | 57.8
CE320 | 52.0053 | 51.21 | 51.25 | 51.8407 | 51.1034 | 49.94
CE330 | 50.8445 | 50.58 | 50.65 | 51.1765 | 50.0848 | 50.7
CE340 | 51.085 | 50.69 | 50.73 | 51.1479 | 50.2967 | 50.78
CE350 | 45.484 | 45.45 | 45.55 | 45.1731 | 44.3162 | 44.56
CE360 | 41.0335 | 41.49 | 41.49 | 42.3695 | 40.871 | 41.21
CE400 | 50.7709 | 52.21 | 52.25 | 52.5485 |  | 52.01
CE410 | 50.4971 | 49.65 | 49.63 |  |  | 49.75
CE420 | 48.7794 | 49.14 | 48.97 | 49.3981 |  | 48.76
CE430 | 48.8219 | 49.17 | 49.3 | 49.6002 |  | 49.17
CE440 | 48.3298 | 48.46 | 48.57 | 48.8288 |  | 48.23
CE500 | 66.5261 |  |  | 59.1976 | 65.9419 | 63.73
CE500 May-Sep | 57.0476 | 57.47 | 57.47 | 57.3219 | 57.0722 | 55.13
CE510 May-Sep | 54.7001 | 57.36 | 57.36 | 57.4361 | 57.0615 | 55.24
CE520 | 69.8745 |  |  | 61.4049 | 70.2268 | 72.17
CE522 | 68.6774 |  |  | 60.7524 | 68.2314 | 68.11
CE525 | 61.4674 |  |  | 54.9944 | 60.1387 | 57.37
CE530 | 46.7299 |  |  | 48.9733 | 41.4516 | 39.6
CE540 | 48.521 |  |  | 46.3072 | 40.0509 | 43.82
CE545 | 36.6249 |  |  | 38.6306 | 36.8747 | 29.2
Weather Data Comparison, Annual Means CE300 only
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
ODB | 19.9145 | 19.8889 | 19.8889 | 19.9141 | 19.9145 | 19.91
OHR | 0.011643 | 0.0116 | 0.0116 | 0.011593 | 0.011649 | 0.0116
JUNE 28 HOURLY OUTPUT
Energy Consumption, Compressor (kWh,e)
Hour | TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 2055.7697 | 1897 | 1894 | 2118.6889 | 1886 | 1942.81
2 | 2053.6706 | 1941 | 1941 | 2131.2588 | 1964 | 1950.53
3 | 2054.4923 | 1897 | 1894 | 2112.6225 | 1881 | 1902.33
4 | 1830.0824 | 1891 | 1890 | 2074.7396 | 1878 | 1845.43
5 | 2029.3426 | 1697 | 1694 | 1997.2205 | 1756 | 1914.46
6 | 1839.4317 | 2126 | 2133 | 2141.5966 | 2075 | 2506.57
7 | 2667.2444 | 3198 | 3223 | 2869.5781 | 3035 | 3170.95
8 | 3552.7185 | 3135 | 3145 | 3498.5394 | 3303 | 3433.96
9 | 4364.7758 | 4528 | 4526 | 4681.7762 | 4483 | 4489.15
10 | 4441.0633 | 4651 | 4655 | 4947.6011 | 4594 | 4853.28
11 | 4999.595 | 5434 | 5456 | 5406.6429 | 5238 | 5164.22
12 | 5316.7711 | 5019 | 5015 | 5632.385 | 5066 | 5004.96
13 | 6188.5477 | 6040 | 6036 | 7132.8035 | 6442 | 6454.59
14 | 6210.9293 | 6420 | 6429 | 6983.3064 | 6523 | 6503.4
15 | 7922.4534 | 7671 | 7683 | 8572.0438 | 8000 | 8040.55
16 | 7964.823 | 8190 | 8222 | 8732.6963 | 8169 | 8133.59
17 | 5420.7775 | 5715 | 5696 | 5718.3243 | 5306 | 5211.79
18 | 5409.9868 | 5536 | 5531 | 5880.5828 | 5381 | 5122.29
19 | 5260.0345 | 4711 | 4689 | 5555.1112 | 4791 | 4831.72
20 | 4880.3429 | 4859 | 4855 | 5259.2137 | 4809 | 4874.85
21 | 3938.7143 | 3913 | 3918 | 4325.7083 | 3939 | 3935.62
22 | 3923.9563 | 3825 | 3823 | 4278.8801 | 3852 | 3844.33
23 | 4122.5716 | 3750 | 3748 | 4172.5901 | 3752 | 3807.46
24 | 3877.3845 | 3880 | 3880 | 4151.9737 | 3794 | 3664.17
Energy Consumption, Condenser Fan (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 256.5326 | 237 | 237 |  | 237 | 240.938
2 | 256.5271 | 240 | 241 |  | 244 | 241.104
3 | 256.5356 | 237 | 237 |  | 236 | 236.85
4 | 229.5857 | 237 | 236 |  | 236 | 231.118
5 | 256.394 | 215 | 215 |  | 224 | 238.687
6 | 229.5597 | 259 | 259 |  | 253 | 292.588
7 | 308.5446 | 352 | 353 |  | 334 | 342.969
8 | 384.0455 | 332 | 335 |  | 352 | 360.598
9 | 458.1014 | 469 | 467 |  | 463 | 460.788
10 | 457.9932 | 479 | 478 |  | 472 | 489.455
11 | 506.3045 | 537 | 536 |  | 516 | 508.218
12 | 529.3648 | 498 | 498 |  | 504 | 496.504
13 | 616.6094 | 597 | 600 |  | 642 | 639.274
14 | 616.1242 | 633 | 635 |  | 645 | 639.953
15 | 781.0016 | 751 | 754 |  | 785 | 784.905
16 | 781.0124 | 800 | 803 |  | 799 | 793.61
17 | 529.4985 | 561 | 556 |  | 519 | 509.581
18 | 529.3784 | 544 | 541 |  | 528 | 506.956
19 | 529.2289 | 481 | 479 |  | 492 | 492.97
20 | 506.2207 | 504 | 503 |  | 498 | 501.239
21 | 409.0843 | 405 | 406 |  | 408 | 405.543
22 | 409.5326 | 399 | 399 |  | 402 | 398.939
23 | 433.8551 | 395 | 394 |  | 395 | 397.275
24 | 409.5808 | 407 | 407 |  | 399 | 385.64
Coil Load, Total (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 8131.73 | 7552.3077 | 7544.9802 | 7471.7175 | 7472 | 7667.56
2 | 8115.8 | 7630.2723 | 7627.0482 | 7494.4102 | 7707 | 7674.46
3 | 8127.89 | 7550.256 | 7546.1526 | 7446.5844 | 7445 | 7527.94
4 | 7224.15 | 7533.8424 | 7528.2735 | 7331.9994 | 7432 | 7317.22
5 | 8104.85 | 6797.8683 | 6753.024 | 7091.0224 | 7000 | 7514.35
6 | 7130.87 | 8136.1629 | 8185.1106 | 7425.0625 | 7915 | 9222.93
7 | 9711.38 | 11075.9559 | 11232.7644 | 9216 | 10450 | 10769.5
8 | 12121.31 | 10290.741 | 10271.6895 | 10609.4108 | 10813 | 11186.4
9 | 14555.62 | 14785.7226 | 14844.0495 | 14032.3459 | 14631 | 14744.4
10 | 14639.38 | 15339.9747 | 15392.7327 | 14777.6894 | 15099 | 15882.1
11 | 16374.09 | 17455.2774 | 17605.0515 | 15905.4096 | 16722 | 16614.5
12 | 17248.4 | 16215.1713 | 16187.6199 | 16521.8755 | 16258 | 16029.6
13 | 20498.21 | 19722.9921 | 19620.9933 | 21588.4217 | 21090 | 21179.7
14 | 20234.06 | 20808.3414 | 20819.1861 | 20677.8576 | 21067 | 21055.4
15 | 26687.28 | 25387.1496 | 25392.7185 | 26132.9897 | 26636 | 27069.8
16 | 26722.68 | 27581.0031 | 27721.1049 | 26664.6248 | 27416 | 27623.3
17 | 17231.33 | 18204.7341 | 18244.5957 | 16344.6134 | 16702 | 16551
18 | 17505.88 | 17933.3235 | 17977.8747 | 17193.4049 | 17312 | 16829.6
19 | 17661.69 | 16012.053 | 15914.4507 | 16877.6217 | 16232 | 16635.3
20 | 16989.81 | 17082.1611 | 17120.2641 | 16536.4933 | 16867 | 17131.1
21 | 13539.94 | 13435.4109 | 13445.0832 | 13445.4149 | 13484 | 13524.8
22 | 13564.54 | 13280.361 | 13285.0506 | 13386.5014 | 13322 | 13355.8
23 | 14531.34 | 13191.8448 | 13192.1379 | 13190.5663 | 13139 | 13343.3
24 | 13691.76 | 13724.4075 | 13754.3037 | 13196.202 | 13323 | 12972.7
Coil Load, Sensible (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 6189.34 | 5889.2583 | 5886.9135 | 5810.748 | 5788 | 5870.06
2 | 6201.56 | 6069.8079 | 6067.17 | 5853.1492 | 5961 | 5871.7
3 | 6194.38 | 5881.3446 | 5878.1205 | 5809.4072 | 5788 | 5782.88
4 | 5548.55 | 5878.1205 | 5873.4309 | 5743.5733 | 5788 | 5683.06
5 | 6318.9 | 5675.2953 | 5671.7781 | 5614.133 | 5580 | 5955.01
6 | 5686.24 | 6438.5277 | 6438.5277 | 6015.0762 | 6341 | 7311.79
7 | 7596.88 | 8342.2122 | 8347.7811 | 7532.4754 | 8277 | 8646.87
8 | 9558.23 | 9069.9795 | 9069.1002 | 8756.6552 | 9038 | 9298.63
9 | 11757.9 | 11872.6017 | 11875.2396 | 11767.1681 | 11971 | 11923.2
10 | 11506.4 | 12039.0825 | 12041.1342 | 11996.3298 | 11971 | 12287.1
11 | 12342.2 | 12811.9872 | 12817.5561 | 12488.0938 | 12731 | 12561.8
12 | 12810 | 12612.093 | 12610.9206 | 12670.959 | 12559 | 12561.3
13 | 16816.1 | 17139.0225 | 17135.2122 | 17401.2828 | 17422 | 17430.7
14 | 17283.5 | 17638.1718 | 17639.0511 | 17591.92 | 17629 | 17608.6
15 | 22882.4 | 22196.463 | 22196.7561 | 22480.6555 | 22491 | 22350.4
16 | 22284.7 | 22527.9591 | 22533.2349 | 22557.3408 | 22491 | 22292
17 | 13048.3 | 13599.2538 | 13600.1331 | 13061.4841 | 12939 | 12739.1
18 | 12720.6 | 12829.8663 | 12831.6249 | 12869.5918 | 12729 | 12180.9
19 | 12490.8 | 11875.5327 | 11871.1362 | 12169.8539 | 11761 | 11540.7
20 | 11655.3 | 11532.3126 | 11534.0712 | 11555.6363 | 11381 | 11359.2
21 | 8882.19 | 9302.4078 | 9302.7009 | 9062.7383 | 9036 | 8931.39
22 | 8880.28 | 8973.5496 | 8973.8427 | 8952.5422 | 8864 | 8747.22
23 | 9449.35 | 8787.4311 | 8787.4311 | 8753.473 | 8656 | 8646.75
24 | 8806.54 | 8799.1551 | 8799.7413 | 8673.9655 | 8656 | 8359.6
Coil Load, Latent (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 1942.39 | 1663.0494 | 1658.0667 | 1660.9695 | 1684 | 1797.5
2 | 1914.24 | 1560.4644 | 1559.8782 | 1641.261 | 1747 | 1802.77
3 | 1933.51 | 1668.9114 | 1668.0321 | 1637.1772 | 1657 | 1745.07
4 | 1675.6 | 1655.7219 | 1654.8426 | 1588.4261 | 1644 | 1634.17
5 | 1785.95 | 1122.573 | 1081.2459 | 1476.8894 | 1420 | 1559.34
6 | 1444.63 | 1697.6352 | 1746.5829 | 1409.9863 | 1574 | 1911.15
7 | 2114.5 | 2733.7437 | 2884.9833 | 1683.5246 | 2173 | 2122.59
8 | 2563.08 | 1220.7615 | 1202.5893 | 1852.7556 | 1775 | 1887.81
9 | 2797.72 | 2913.1209 | 2968.8099 | 2265.1778 | 2660 | 2821.19
10 | 3132.98 | 3300.8922 | 3351.5985 | 2781.3597 | 3128 | 3595.03
11 | 4031.89 | 4643.2902 | 4787.4954 | 3417.3158 | 3991 | 4052.76
12 | 4438.4 | 3603.0783 | 3576.6993 | 3850.9165 | 3699 | 3468.23
13 | 3682.11 | 2583.9696 | 2485.7811 | 4187.139 | 3669 | 3749.01
14 | 2950.56 | 3170.1696 | 3180.135 | 3085.9376 | 3438 | 3446.79
15 | 3804.88 | 3190.6866 | 3195.9624 | 3652.3342 | 4145 | 4719.45
16 | 4437.98 | 5053.044 | 5187.87 | 4107.284 | 4925 | 5331.25
17 | 4183.03 | 4605.4803 | 4644.4626 | 3283.1293 | 3763 | 3811.95
18 | 4785.28 | 5103.4572 | 5146.2498 | 4323.8131 | 4582 | 4648.77
19 | 5170.89 | 4136.5203 | 4043.3145 | 4707.7678 | 4470 | 5094.59
20 | 5334.51 | 5549.8485 | 5586.1929 | 4980.857 | 5486 | 5771.92
21 | 4657.75 | 4133.0031 | 4142.3823 | 4382.6766 | 4447 | 4593.42
22 | 4684.26 | 4306.8114 | 4311.2079 | 4433.9592 | 4459 | 4608.6
23 | 5081.99 | 4404.4137 | 4404.7068 | 4437.0933 | 4482 | 4696.56
24 | 4885.22 | 4925.2524 | 4954.5624 | 4522.2365 | 4666 | 4613.06
Zone Humidity Ratio
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 0.0090778 | 0.0094 | 0.0094 | 0.0094054 | 0.009276 | 0.0092502
2 | 0.0090138 | 0.0093 | 0.0093 | 0.0093664 | 0.009302 | 0.0092582
3 | 0.0090644 | 0.0094 | 0.0094 | 0.0093723 | 0.009239 | 0.0092068
4 | 0.0089864 | 0.0094 | 0.0094 | 0.0093141 | 0.009201 | 0.0091047
5 | 0.0088405 | 0.0089 | 0.009 | 0.0091917 | 0.008969 | 0.0089519
6 | 0.0086578 | 0.0092 | 0.0092 | 0.0090454 | 0.009012 | 0.0091583
7 | 0.0091531 | 0.01 | 0.0098 | 0.0093227 | 0.00949 | 0.0094778
8 | 0.0095303 | 0.0094 | 0.0094 | 0.0096417 | 0.009314 | 0.0093737
9 | 0.0096727 | 0.0099 | 0.0099 | 0.0098152 | 0.009708 | 0.0097161
10 | 0.010058 | 0.0103 | 0.0102 | 0.010197 | 0.010041 | 0.010237
11 | 0.010408 | 0.0109 | 0.0107 | 0.010626 | 0.010588 | 0.010622
12 | 0.010684 | 0.0108 | 0.0108 | 0.010942 | 0.01058 | 0.010433
13 | 0.010087 | 0.0101 | 0.0102 | 0.010387 | 0.009975 | 0.0099715
14 | 0.0097987 | 0.01 | 0.01 | 0.0099642 | 0.009778 | 0.0097436
15 | 0.0095792 | 0.0098 | 0.0098 | 0.0098097 | 0.009579 | 0.0097834
16 | 0.0096663 | 0.01 | 0.0098 | 0.0099222 | 0.009733 | 0.0098255
17 | 0.01077 | 0.0107 | 0.0107 | 0.010633 | 0.01044 | 0.010257
18 | 0.011184 | 0.0112 | 0.0112 | 0.011174 | 0.010912 | 0.010859
19 | 0.011131 | 0.011 | 0.0111 | 0.011312 | 0.010914 | 0.011024
20 | 0.010991 | 0.0114 | 0.0113 | 0.011348 | 0.011269 | 0.011357
21 | 0.01114 | 0.0113 | 0.0113 | 0.011561 | 0.011348 | 0.011378
22 | 0.011177 | 0.0114 | 0.0114 | 0.0116 | 0.011383 | 0.011398
23 | 0.011176 | 0.0115 | 0.0115 | 0.011611 | 0.011416 | 0.01145
24 | 0.011275 | 0.0117 | 0.0117 | 0.011664 | 0.011507 | 0.011462
COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 3.5167 | 3.539 | 3.5406 | 3.5266 | 3.5195 | 3.5112
2 | 3.513 | 3.4985 | 3.4954 | 3.5164 | 3.4905 | 3.5017
3 | 3.517 | 3.5381 | 3.5411 | 3.5248 | 3.5168 | 3.5191
4 | 3.5074 | 3.5403 | 3.5411 | 3.5339 | 3.5156 | 3.5238
5 | 3.5458 | 3.5554 | 3.5375 | 3.5504 | 3.5354 | 3.4899
6 | 3.4465 | 3.4114 | 3.4219 | 3.4671 | 3.3999 | 3.2949
7 | 3.2635 | 3.12 | 3.1412 | 3.2116 | 3.1018 | 3.0648
8 | 3.079 | 2.9682 | 2.9516 | 3.0325 | 2.9584 | 2.948
9 | 3.018 | 2.9589 | 2.973 | 2.9972 | 2.9581 | 2.9787
10 | 2.9882 | 2.9902 | 2.9988 | 2.9868 | 2.9805 | 2.9726
11 | 2.9739 | 2.9233 | 2.9381 | 2.9418 | 2.9062 | 2.929
12 | 2.9504 | 2.9391 | 2.9363 | 2.9334 | 2.9189 | 2.9137
13 | 3.0122 | 2.9717 | 2.9568 | 3.0266 | 2.9771 | 2.9856
14 | 2.9638 | 2.9503 | 2.9472 | 2.961 | 2.939 | 2.9476
15 | 3.0663 | 3.0144 | 3.0097 | 3.0486 | 3.032 | 3.0672
16 | 3.0555 | 3.068 | 3.0716 | 3.0534 | 3.0571 | 3.0943
17 | 2.8959 | 2.9007 | 2.9182 | 2.8583 | 2.8673 | 2.8928
18 | 2.9474 | 2.9496 | 2.9608 | 2.9238 | 2.9298 | 2.9897
19 | 3.0508 | 3.084 | 3.0794 | 3.0382 | 3.0725 | 3.1242
20 | 3.1541 | 3.1852 | 3.1953 | 3.1443 | 3.1783 | 3.1865
21 | 3.1142 | 3.1115 | 3.1094 | 3.1083 | 3.1019 | 3.1155
22 | 3.1302 | 3.144 | 3.1466 | 3.1285 | 3.1316 | 3.1475
23 | 3.1892 | 3.1826 | 3.185 | 3.1612 | 3.1683 | 3.1734
24 | 3.1938 | 3.2014 | 3.2084 | 3.1783 | 3.1774 | 3.2033
ODB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8
2 | 18.05 | 18.3333 | 18.3333 | 18.1125 | 18.3 | 18.3
3 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8
4 | 17.8 | 17.7778 | 17.7778 | 17.8 | 17.8 | 17.8
5 | 17.5 | 17.2222 | 17.2222 | 17.425 | 17.2 | 17.2
6 | 18.3 | 19.4444 | 19.4444 | 18.575 | 19.4 | 19.4
7 | 22.2 | 25 | 25 | 22.9 | 25 | 25
8 | 26.1 | 27.2222 | 27.2222 | 26.375 | 27.2 | 27.2
9 | 28.05 | 28.8889 | 28.8889 | 28.2625 | 28.9 | 28.9
10 | 28.9 | 28.8889 | 28.8889 | 28.9 | 28.9 | 28.9
11 | 30 | 31.1111 | 31.1111 | 30.275 | 31.1 | 31.1
12 | 30.85 | 30.5556 | 30.5556 | 30.7875 | 30.6 | 30.6
13 | 30.85 | 31.1111 | 31.1111 | 30.9125 | 31.1 | 31.1
14 | 31.4 | 31.6667 | 31.6667 | 31.475 | 31.7 | 31.7
15 | 31.95 | 32.2222 | 32.2222 | 32.0125 | 32.2 | 32.2
16 | 32.2 | 32.2222 | 32.2222 | 32.2 | 32.2 | 32.2
17 | 31.95 | 31.6667 | 31.6667 | 31.8875 | 31.7 | 31.7
18 | 31.4 | 31.1111 | 31.1111 | 31.325 | 31.1 | 31.1
19 | 29.7 | 28.3333 | 28.3333 | 29.35 | 28.3 | 28.3
20 | 27.75 | 27.2222 | 27.2222 | 27.6125 | 27.2 | 27.2
21 | 27.2 | 27.2222 | 27.2222 | 27.2 | 27.2 | 27.2
22 | 26.95 | 26.6667 | 26.6667 | 26.8875 | 26.7 | 26.7
23 | 26.4 | 26.1111 | 26.1111 | 26.325 | 26.1 | 26.1
24 | 26.1 | 26.1111 | 26.1111 | 26.1 | 26.1 | 26.1
EDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 23.4068 | 23.8333 | 23.8333 | 23.9453 | 23.92 | 23.9367
2 | 23.3748 | 23.9444 | 23.9444 | 23.9638 | 24 | 23.9367
3 | 23.3833 | 23.8333 | 23.8333 | 23.9453 | 23.92 | 23.8958
4 | 23.3739 | 23.8333 | 23.8333 | 23.9171 | 23.92 | 23.8375
5 | 23.3503 | 23.7778 | 23.7778 | 23.8615 | 23.83 | 23.9757
6 | 23.4171 | 24.1111 | 24.1111 | 24.0337 | 24.16 | 24.5756
7 | 24.0395 | 24.9444 | 24.9444 | 24.6841 | 25 | 25.1643
8 | 24.5724 | 25.2778 | 25.2778 | 25.2076 | 25.33 | 25.4533
9 | 25.0937 | 25.5556 | 25.5556 | 25.4902 | 25.59 | 25.5785
10 | 25.2815 | 25.5556 | 25.5556 | 25.5859 | 25.59 | 25.7393
11 | 25.3592 | 25.8889 | 25.8889 | 25.7944 | 25.91 | 25.8631
12 | 25.5877 | 25.8333 | 25.8333 | 25.8706 | 25.84 | 25.8628
13 | 26.53 | 25.9444 | 25.9444 | 25.8841 | 25.91 | 25.9424
14 | 26.5617 | 26.0556 | 26.0556 | 25.9682 | 26 | 26.022
15 | 26.7812 | 26.1111 | 26.1111 | 26.0506 | 26.08 | 26.1296
16 | 26.5632 | 26.1667 | 26.1667 | 26.0819 | 26.08 | 26.0323
17 | 26.198 | 26.0556 | 26.0556 | 26.0383 | 26 | 25.943
18 | 26.2263 | 25.9444 | 25.9444 | 25.9541 | 25.91 | 25.6955
19 | 25.7001 | 25.5 | 25.5 | 25.6545 | 25.5 | 25.4093
20 | 25.1673 | 25.3333 | 25.3333 | 25.3924 | 25.33 | 25.3281
21 | 24.6544 | 25.3333 | 25.3333 | 25.332 | 25.33 | 25.291
22 | 24.7445 | 25.2222 | 25.2222 | 25.2853 | 25.25 | 25.2092
23 | 24.6707 | 25.1111 | 25.1111 | 25.2003 | 25.16 | 25.1645
24 | 24.7257 | 25.1111 | 25.1111 | 25.1665 | 25.16 | 25.0374
EWB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 16.9641 | 17.34 | 17.34 |  | 17.155 | 17.3042
2 | 16.9046 | 17.29 | 17.29 |  | 17.238 | 17.31
3 | 16.9418 | 17.34 | 17.37 |  | 17.12 | 17.2367
4 | 16.8619 | 17.34 | 17.37 |  | 17.102 | 17.0785
5 | 16.6966 | 16.85 | 16.94 |  | 16.787 | 17.0075
6 | 16.5734 | 17.3 | 17.3 |  | 17.032 | 17.5412
7 | 17.3192 | 18.39 | 18.23 |  | 17.911 | 17.9926
8 | 17.7945 | 17.78 | 17.78 |  | 17.646 | 17.9591
9 | 17.973 | 18.36 | 18.28 |  | 18.118 | 18.3251
10 | 18.3972 | 18.68 | 18.6 |  | 18.442 | 18.8543
11 | 18.8246 | 19.48 | 19.33 |  | 19.142 | 19.1876
12 | 19.1202 | 19.23 | 19.23 |  | 18.935 | 18.8671
13 | 18.8377 | 18.56 | 18.64 |  | 18.326 | 18.518
14 | 18.5548 | 18.6 | 18.6 |  | 18.269 | 18.4421
15 | 18.5486 | 18.46 | 18.46 |  | 18.239 | 18.6471
16 | 18.673 | 18.84 | 18.76 |  | 18.557 | 18.7965
17 | 19.4032 | 19.35 | 19.35 |  | 19.063 | 19.1104
18 | 19.7724 | 19.75 | 19.68 |  | 19.458 | 19.3936
19 | 19.5753 | 19.32 | 19.4 |  | 19.199 | 19.5323
20 | 19.3718 | 19.76 | 19.76 |  | 19.65 | 19.7431
21 | 19.438 | 19.76 | 19.76 |  | 19.706 | 19.7437
22 | 19.4846 | 19.8 | 19.8 |  | 19.697 | 19.7887
23 | 19.4693 | 19.84 | 19.84 |  | 19.694 | 19.8355
24 | 19.5725 | 20.14 | 20.06 |  | 19.805 | 19.7678
OHR (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
1 | 0.011255 | 0.0114 | 0.0114 | 0.011192 | 0.0111 | 0.011072
2 | 0.011255 | 0.0112 | 0.0112 | 0.011286 | 0.011462 | 0.011432
3 | 0.011255 | 0.0114 | 0.0114 | 0.01119 | 0.0111 | 0.011072
4 | 0.011075 | 0.0114 | 0.0114 | 0.011051 | 0.0111 | 0.011072
5 | 0.01061 | 0.0103 | 0.0103 | 0.010479 | 0.01018 | 0.010155
6 | 0.010568 | 0.0113 | 0.0113 | 0.010637 | 0.011001 | 0.01097
7 | 0.012071 | 0.0133 | 0.0133 | 0.012265 | 0.01314 | 0.013099
8 | 0.012173 | 0.0109 | 0.0109 | 0.011777 | 0.011075 | 0.011039
9 | 0.011538 | 0.0117 | 0.0117 | 0.011572 | 0.011995 | 0.011957
10 | 0.012388 | 0.0125 | 0.0125 | 0.012393 | 0.01276 | 0.012719
11 | 0.013776 | 0.0148 | 0.0148 | 0.013955 | 0.014809 | 0.014761
12 | 0.014041 | 0.0134 | 0.0134 | 0.013752 | 0.013253 | 0.013211
13 | 0.012315 | 0.0115 | 0.0115 | 0.011978 | 0.011329 | 0.011293
14 | 0.011543 | 0.0121 | 0.0121 | 0.011517 | 0.011729 | 0.011692
15 | 0.012069 | 0.0119 | 0.0119 | 0.012075 | 0.012379 | 0.01234
16 | 0.013324 | 0.0144 | 0.0144 | 0.013479 | 0.014232 | 0.014188
17 | 0.014505 | 0.0146 | 0.0146 | 0.014485 | 0.01473 | 0.014684
18 | 0.015234 | 0.0157 | 0.0157 | 0.015265 | 0.015684 | 0.015634
19 | 0.015134 | 0.0143 | 0.0143 | 0.014908 | 0.014539 | 0.014493
20 | 0.015748 | 0.0164 | 0.0164 | 0.015925 | 0.016878 | 0.016824
21 | 0.016886 | 0.0164 | 0.0164 | 0.016792 | 0.016878 | 0.016824
22 | 0.016863 | 0.0167 | 0.0167 | 0.016752 | 0.016832 | 0.016777
23 | 0.016867 | 0.0169 | 0.0169 | 0.016764 | 0.016889 | 0.016835
24 | 0.017112 | 0.0178 | 0.0178 | 0.017059 | 0.017329 | 0.017273
CE500, CE530 Average Daily Outputs
Energy Consumption, Total (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 3892.9389 | 3975.4583 | 3975.1667 | 4028.8242 | 3901.0417 | 4073
CE500Jun25 | 5044.9219 | 5204.3333 | 5204.0833 | 5228.78 | 5066.5 | 5230
CE530Apr30 | 3022.7732 | 3062 | 3061.7917 | 3101.4372 | 3091.5417 | 3144
CE530Jun25 | 3894.1233 | 3978.2083 | 3978.0833 | 4028.6999 | 3934.625 | 4043
Energy Consumption, Compressor (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 3014.619 | 3119.8333 | 3119.6667 | 3509.8969 | 3020.0417 | 3159
CE500Jun25 | 4083.8829 | 4263.5417 | 4263.4167 | 4663.2403 | 4105.9583 | 4239
CE530Apr30 | 2311.4724 | 2390.0417 | 2389.9167 | 2689.0399 | 2378.4583 | 2411
CE530Jun25 | 3118.0954 | 3243 | 3242.9583 | 3578.6202 | 3165.5833 | 3248
Energy Consumption, Condenser Fan (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 376.0762 | 389.125 | 389.0833 |  | 377.25 | 391
CE500Jun25 | 411.4946 | 426.3333 | 426.3333 |  | 411.3333 | 424
CE530Apr30 | 304.5625 | 311.1667 | 311.125 |  | 305.3333 | 314
CE530Jun25 | 332.2771 | 339.625 | 339.625 |  | 329.25 | 340
Energy Consumption, Indoor Fan (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 502.2437 | 466.5 | 466.4167 | 518.9273 | 503.75 | 522
CE500Jun25 | 549.5444 | 514.4583 | 514.3333 | 565.5397 | 549.2083 | 566
CE530Apr30 | 406.7383 | 360.7917 | 360.75 | 412.3973 | 407.75 | 419
CE530Jun25 | 443.7507 | 395.5833 | 395.5 | 450.0798 | 439.7917 | 454
Total Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 13185.6871 | 13732.6998 | 13732.9074 | 13655.2659 | 13169.5417 | 13673
CE500Jun25 | 13188.0504 | 13837.5319 | 13837.3853 | 13733.0749 | 13198.0833 | 13727
CE530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9775.2401 | 9365.4583 | 9798
CE530Jun25 | 9376.2963 | 9760.7918 | 9760.6941 | 9835.1361 | 9387.625 | 9834
Sensible Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 9374.7971 | 9924.8179 | 9925.0255 | 9883.6259 | 9365.4583 | 9902
CE500Jun25 | 9377.6867 | 9981.2396 | 9981.0931 | 9952.5713 | 9387.625 | 9946
CE530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9775.2401 | 9365.4583 | 9798
CE530Jun25 | 9376.2963 | 9760.7674 | 9760.6697 | 9835.1361 | 9387.625 | 9834
Latent Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 3810.89 | 3807.8819 | 3807.8819 | 3771.64 | 3804.375 | 3770
CE500Jun25 | 3810.3637 | 3856.2923 | 3856.2923 | 3780.5037 | 3810.4167 | 3780
CE530Apr30 | -5.4771e-13 | 0 | 0 | 5.713e-13 | 0 | 0
CE530Jun25 | 7.2905e-13 | 0.024425 | 0.024425 | 6.6831e-13 | 0 | 0
Humidity Ratio (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 0.010675 | 0.011 | 0.011 | 0.010984 | 0.010938 | 0.016
CE500Jun25 | 0.011168 | 0.0115 | 0.0115 | 0.011459 | 0.011479 | 0.011
CE530Apr30 | 0.006208 | 0.0071 | 0.0071 | 0.0067531 | 0.005485 | 0.00674
CE530Jun25 | 0.006208 | 0.0078 | 0.0078 | 0.0067531 | 0.005478 | 0.00674
COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 3.8448 | 3.9136 | 3.9139 | 3.8497 | 3.8372 | 3.85
CE500Jun25 | 2.9313 | 2.9505 | 2.9506 | 2.9431 | 2.9213 | 2.94
CE530Apr30 | 3.5431 | 3.5988 | 3.5991 | 3.4414 | 3.4604 | 3.59
CE530Jun25 | 2.7197 | 2.7245 | 2.7245 | 2.7795 | 2.69 | 2.74
ODB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96
CE500Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5
CE530Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96
CE530Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5
EDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg
CE500Apr30 | 24.6411 | 24.9444 | 24.9444 | 24.9818 | 25 | 25
CE500Jun25 | 24.5478 | 25 | 25 | 24.9828 | 25 | 25
CE530Apr30 | 24.365 | 24.9444 | 24.6667 | 25 | 25 | 25
CE530Jun25 | 24.3537 | 24.9444 | 24.9444 | 25 | 25 | 25
Hourly integrated maxima for consumptions and loads
=IF(ISBLANK(DOE21D!$C146),"",IF(ISTEXT(DOE21D!$C146),IF(TRIM(DOE21D!$C146)="","",DATEVALUE(DOE21D!$C146)),DOE21D!$C146))
Compressor + Condenser Fan + Indoor Fan Energy Consumption (Wh,e)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 | 11932 | 1900-07-20 | 15 | Compr + Both Fans Wh: 11548; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE310 | 12594.4016 | 20-Jul | 15 | 12583 | 2002-07-20 | 15 | 12595 | 2002-07-20 | 15 | 12540.8188 | 2010-07-20 | 15 | 12653 | 1900-07-20 | 15 | Compr + Both Fans Wh: 12162; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 16
CE320 | 13028.1986 | 20-Jul | 15 | 12916 | 2002-07-20 | 15 | 12981 | 2002-07-20 | 15 | 12954.4267 | 2010-07-20 | 15 | 13104 | 1900-07-20 | 15 | Compr + Both Fans Wh: 12875; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 14
CE330 | 13346.701 | 20-Jul | 15 | 13212 | 2002-07-20 | 15 | 13407 | 2002-07-20 | 15 | 13314.1099 | 2010-07-20 | 15 | 13467 | 1900-07-20 | 15 | Compr + Both Fans Wh: 13335; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE340 | 13180.9018 | 20-Jul | 15 | 13158 | 2002-07-20 | 15 | 13190 | 2002-07-20 | 15 | 13134.1703 | 2010-07-20 | 15 | 13277 | 1900-07-20 | 15 | Compr + Both Fans Wh: 13101; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 14
CE350 | 11626.889 | 20-Jul | 15 | 11654 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8619 | 2010-07-20 | 15 | 11932 | 1900-07-20 | 15 | Compr + Both Fans Wh: 11546; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE360 | 12769.5022 | 20-Jul | 15 | 12736 | 2002-07-20 | 15 | 12726 | 2002-07-20 | 15 | 12744.2783 | 2010-07-20 | 15 | 12863 | 1900-07-20 | 15 | Compr + Both Fans Wh: 12762; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 14
CE400 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11677 | 2004-09-18 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 11519; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE410 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | [6 empty] | Compr + Both Fans Wh: 11549; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE420 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 11548; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE430 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 11548; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE440 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11899.8597 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 11461; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 16
CE500 | 10166.4831 | 20-Jul | 15 | 10431 | 2002-07-20 | 15 | 10425 | 2002-07-20 | 15 | 10398.6872 | 2010-07-20 | 15 | 10177 | 1900-07-20 | 15 | Compr + Both Fans Wh: 10274; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 15
CE510 | 11204.8968 | 20-Jul | 15 | 11590 | 2002-07-20 | 15 | 11587 | 2002-07-20 | 15 | 11409.8034 | 2010-07-20 | 15 | 11186 | 1900-07-20 | 15 | Compr + Both Fans Wh: 11344; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 14
CE520 | 11035.3898 | 20-Jul | 15 | 10989 | 2002-07-20 | 15 | 11014 | 2002-07-20 | 15 | 11100.5253 | 2010-07-20 | 15 | 11044 | 1900-07-20 | 15 | Compr + Both Fans Wh: 10684; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 15
CE522 | 10430.7791 | 20-Jul | 15 | 10972 | 2002-07-20 | 15 | 10966 | 2002-07-20 | 15 | 10762.3872 | 2010-07-20 | 15 | 10639 | 1900-07-20 | 15 | Compr + Both Fans Wh: 10747; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 15
CE525 | 9366.7481 | 20-Jul | 15 | 9538 | 2002-07-20 | 15 | 9531 | 2002-07-20 | 15 | 9569.5705 | 2010-07-20 | 15 | 9419 | 1900-07-20 | 15 | Compr + Both Fans Wh: 9585; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 15
CE530 | 8028.3285 | 20-Jul | 15 | 8059 | 2002-07-20 | 15 | 8055 | 2002-07-20 | 15 | 8171.0479 | 2010-07-20 | 15 | 7992 | 1900-07-20 | 15 | Compr + Both Fans Wh: 8089; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 15
CE540 | 8698.9562 | 20-Jul | 15 | 8943 | 2002-07-20 | 15 | 8939 | 2002-07-20 | 15 | 8677.4025 | 2010-07-20 | 15 | 8846 | 1900-07-20 | 15 | Compr + Both Fans Wh: 8985; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 15
CE545 | 7204.827 | 20-Jul | 15 | 7350 | 2002-07-20 | 15 | 7346 | 2002-07-20 | 15 | 7762.756 | 2010-07-20 | 15 | 7351 | 1900-07-20 | 15 | Compr + Both Fans Wh: 7471; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 15
Sensible Coil Load (Wh,th)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 | 23457 | 1900-07-20 | 15 | Compr + Both Fans Wh: 22908; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 15
CE310 | 23094.3 | 10-Sep | 15 | 23080 | 2004-09-10 | 16 | 23119 | 2004-06-04 | 16 | 23276.4591 | 2010-07-11 | 16 | 23078 | 1900-09-10 | 15 | Compr + Both Fans Wh: 22649; Compr + Both Fans Date: 2003-06-13; Compr + Both Fans Hour: 16
CE320 | 31315.6 | 24-Apr | 16 | 31119 | 2004-04-24 | 16 | 31072 | 2002-04-24 | 16 | 31972.0849 | 2010-04-24 | 15 | 31134 | 1900-06-03 | 16 | Compr + Both Fans Wh: 30967; Compr + Both Fans Date: 2003-04-24; Compr + Both Fans Hour: 15
CE330 | 33226.1 | 14-Jun | 14 | 33410 | 2002-06-14 | 14 | 34490 | 2002-06-14 | 15 | 34764.7794 | 2010-06-14 | 15 | 33997 | 1900-04-24 | 16 | Compr + Both Fans Wh: 33421; Compr + Both Fans Date: 2003-09-09; Compr + Both Fans Hour: 14
CE340 | 32828.9 | 24-Apr | 15 | 32086 | 2002-05-16 | 16 | 32086 | 2002-05-16 | 16 | 32887.7843 | 2010-04-24 | 15 | 32940 | 1900-04-24 | 16 | Compr + Both Fans Wh: 32180; Compr + Both Fans Date: 2003-04-24; Compr + Both Fans Hour: 15
CE350 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8071 | 2010-07-20 | 15 | 23457 | 1900-07-20 | 15 | Compr + Both Fans Wh: 22876; Compr + Both Fans Date: 2003-07-10; Compr + Both Fans Hour: 15
CE360 | 32060.7 | 24-Apr | 16 | 32111 | 2003-04-24 | 16 | 32065 | 2004-04-24 | 16 | 32620.9131 | 2010-04-24 | 16 | 31981 | 1900-04-24 | 16 | Compr + Both Fans Wh: 32179; Compr + Both Fans Date: 2003-04-24; Compr + Both Fans Hour: 15
CE400 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 22877; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 16
CE410 | 23265.7 | 10-Sep | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | [6 empty] | Compr + Both Fans Wh: 22893; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 15
CE420 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 22893; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 15
CE430 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 22893; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 15
CE440 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 22875; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 16
CE500 | 19549.2 | 28-Oct | 15 | 20009 | 2003-06-04 | 16 | 20008 | 2002-09-10 | 16 | 19849.2901 | 2010-07-20 | 15 | 18776 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19818; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 15
CE510 | 21729.2 | 29-Apr | 19 | 22513 | 2002-07-11 | 15 | 22513 | 2003-07-11 | 15 | 22290.3117 | 2010-07-20 | 15 | 21121 | 1900-06-04 | 13 | Compr + Both Fans Wh: 22269; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 14
CE520 | 19415.9 | 28-Sep | 15 | 20159 | 2004-05-26 | 16 | 20154 | 2004-05-26 | 16 | 19999.2936 | 2010-07-20 | 15 | 18969 | 1900-07-20 | 16 | Compr + Both Fans Wh: 20378; Compr + Both Fans Date: 2003-05-23; Compr + Both Fans Hour: 15
CE522 | 19488.8 | 12-Mai | 15 | 20137 | 2002-07-11 | 16 | 20135 | 2002-07-11 | 16 | 19933.5062 | 2010-07-20 | 15 | 18785 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19920; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 15
CE525 | 19702.7 | 26-Jul | 16 | 19850 | 2002-04-24 | 16 | 19850 | 2002-04-24 | 16 | 19663.6722 | 2010-07-20 | 15 | 18759 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19661; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 15
CE530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19638.7657 | 2010-07-20 | 15 | 18776 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19626; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 15
CE540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19726.32 | 2010-07-20 | 15 | 18794 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19799; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 15
CE545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19539.7081 | 2010-07-20 | 15 | 18759 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19497; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 15
Latent Coil Load (Wh,th)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9394 | 2001-09-03 | 15 | 10234.8217 | 2010-07-10 | 13 | 10375 | 1900-09-03 | 15 | Compr + Both Fans Wh: 10392; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 15
CE310 | 15907 | 03-Sep | 15 | 15139 | 2001-09-03 | 15 | 15270 | 2001-09-03 | 15 | 16274.8379 | 2010-08-04 | 15 | 16112 | 1900-08-04 | 15 | Compr + Both Fans Wh: 16077; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 16
CE320 | 23147.3 | 02-Oct | 10 | 31497 | 2002-10-02 | 9 | 31503 | 2002-10-02 | 9 | 22195.4712 | 2010-10-02 | 10 | 21697 | 1900-09-17 | 12 | Compr + Both Fans Wh: 21929; Compr + Both Fans Date: 2003-10-01; Compr + Both Fans Hour: 20
CE330 | 27825.2 | 18-Sep | 16 | 26941 | 2003-09-18 | 15 | 40809 | 2002-10-02 | 9 | 27134.3149 | 2010-09-18 | 16 | 28184 | 1900-09-18 | 15 | Compr + Both Fans Wh: 27488; Compr + Both Fans Date: 2003-09-18; Compr + Both Fans Hour: 15
CE340 | 24848.3 | 02-Oct | 9 | 30451 | 2002-10-02 | 9 | 36011 | 2002-10-02 | 9 | 23911.2415 | 2010-10-02 | 10 | 24225 | 1900-09-03 | 17 | Compr + Both Fans Wh: 23794; Compr + Both Fans Date: 2003-10-01; Compr + Both Fans Hour: 20
CE350 | 9751.26 | 01-Oct | 13 | 9303 | 2001-09-03 | 15 | 9393 | 2001-09-03 | 15 | 10235.3532 | 2010-07-10 | 13 | 10755 | 1900-10-02 | 8 | Compr + Both Fans Wh: 11603; Compr + Both Fans Date: 2003-08-03; Compr + Both Fans Hour: 7
CE360 | 9275.16 | 02-Oct | 10 | 10026 | 2002-10-02 | 9 | 10336 | 2002-10-02 | 9 | 8520.3176 | 2010-10-02 | 11 | 8859 | 1900-09-03 | 17 | Compr + Both Fans Wh: 8934; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 17
CE400 | 27075.3 | 16-Sep | 15 | 25578 | 2002-09-18 | 14 | 32396 | 2003-09-18 | 15 | 26317.2818 | 2010-09-16 | 14 |  |  |  | Compr + Both Fans Wh: 26645; Compr + Both Fans Date: 2003-09-16; Compr + Both Fans Hour: 14
CE410 | 11138.9 | 16-Sep | 15 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | [6 empty] | Compr + Both Fans Wh: 10377; Compr + Both Fans Date: 2003-09-09; Compr + Both Fans Hour: 15
CE420 | 9751.04 | 01-Oct | 13 | 9304 | 2001-09-03 | 15 | 9394 | 2003-09-03 | 15 | 10234.8217 | 2010-07-10 | 13 |  |  |  | Compr + Both Fans Wh: 10394; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 15
CE430 | 9635.7 | 03-Sep | 16 | 11105 | 2004-10-24 | 14 | 11101 | 2003-05-21 | 15 | 11073.7739 | 2010-10-24 | 13 |  |  |  | Compr + Both Fans Wh: 10394; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 15
CE440 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | 10234.8217 | 2010-07-10 | 13 |  |  |  | Compr + Both Fans Wh: 10139; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 15
CE500 | 7965.46 | 06-Oct | 15 | 7733 | 2001-09-03 | 15 | 7733 | 2001-09-03 | 15 | 7838.7203 | 2010-06-29 | 16 | 7805 | 1900-06-29 | 16 | Compr + Both Fans Wh: 7762; Compr + Both Fans Date: 2003-06-29; Compr + Both Fans Hour: 15
CE510 | 8892.56 | 15-Sep | 11 | 8723 | 2002-10-02 | 9 | 8723 | 2003-10-02 | 9 | 8954.7918 | 2010-06-17 | 14 | 8850 | 1900-06-17 | 14 | Compr + Both Fans Wh: 8874; Compr + Both Fans Date: 2003-06-17; Compr + Both Fans Hour: 13
CE520 | 7913.7 | 28-Sep | 15 | 7785 | 2001-09-03 | 15 | 7785 | 2001-09-03 | 15 | 7698.5342 | 2010-06-29 | 16 | 7726 | 1900-06-30 | 16 | Compr + Both Fans Wh: 7964; Compr + Both Fans Date: 2003-05-23; Compr + Both Fans Hour: 15
CE522 | 7906.7 | 02-Mai | 15 | 7760 | 2001-09-03 | 15 | 7760 | 2001-09-03 | 15 | 7769.7702 | 2010-06-29 | 16 | 7743 | 1900-06-29 | 16 | Compr + Both Fans Wh: 7745; Compr + Both Fans Date: 2003-06-29; Compr + Both Fans Hour: 15
CE525 | 8037.07 | 26-Jul | 16 | 7663 | 2001-09-03 | 15 | 7663 | 2001-09-03 | 15 | 7947.3919 | 2010-06-29 | 16 | 7938 | 1900-06-29 | 16 | Compr + Both Fans Wh: 7820; Compr + Both Fans Date: 2003-06-29; Compr + Both Fans Hour: 15
CE530 | 1.6431e-11 | 18-Jun | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0587 | 2010-03-16 | 10 | 179 | 1900-03-11 | 11 | Compr + Both Fans Wh: 35.9; Compr + Both Fans Date: 2003-11-01; Compr + Both Fans Hour: 20
CE540 | 627.186 | 11-Mar | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1654.9514 | 2010-03-11 | 10 | 845 | 1900-03-11 | 10 | Compr + Both Fans Wh: 1181; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 10
CE545 | 1.8119e-11 | 01-Jul | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2784e-12 | 2010-05-23 | 15 | 4 | 1900-07-20 | 15 | Compr + Both Fans Wh: 0; Compr + Both Fans Date: 2003-01-01; Compr + Both Fans Hour: 1
Sensible + Latent Coil Load (Wh,th)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 | 32502 | 1900-07-20 | 15 | Compr + Both Fans Wh: 32072; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE310 | 37328 | 03-Sep | 15 | 36750 | 2004-09-03 | 16 | 37033 | 2004-09-03 | 16 | 37126.4795 | 2010-09-17 | 15 | 37261 | 1900-09-03 | 15 | Compr + Both Fans Wh: 36991; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 16
CE320 | 40317.6 | 03-Sep | 16 | 53813 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9 | 39765.1828 | 2010-09-03 | 16 | 39904 | 1900-09-03 | 16 | Compr + Both Fans Wh: 39920; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 16
CE330 | 43492 | 02-Oct | 9 | 43628 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9 | 43445.0808 | 2010-10-02 | 9 | 43978 | 1900-10-02 | 9 | Compr + Both Fans Wh: 42415; Compr + Both Fans Date: 2003-07-10; Compr + Both Fans Hour: 11
CE340 | 41651.7 | 02-Oct | 10 | 50819 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9 | 41328.2736 | 2010-10-02 | 10 | 41366 | 1900-09-03 | 15 | Compr + Both Fans Wh: 41132; Compr + Both Fans Date: 2003-09-03; Compr + Both Fans Hour: 16
CE350 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31454 | 2001-07-20 | 15 | 32733.265 | 2010-07-20 | 15 | 32502 | 1900-07-20 | 15 | Compr + Both Fans Wh: 32077; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE360 | 38857.16 | 02-Oct | 10 | 40613 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9 | 38459.7282 | 2010-10-02 | 11 | 38322 | 1900-10-02 | 10 | Compr + Both Fans Wh: 38451; Compr + Both Fans Date: 2003-10-02; Compr + Both Fans Hour: 10
CE400 | 41178.6 | 16-Sep | 15 | 40543 | 2002-09-18 | 14 | 49838 | 2003-09-18 | 15 | 40728.1422 | 2010-09-16 | 15 |  |  |  | Compr + Both Fans Wh: 40774; Compr + Both Fans Date: 2003-09-16; Compr + Both Fans Hour: 14
CE410 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | [6 empty] | Compr + Both Fans Wh: 32073; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE420 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 32072; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE430 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 32072; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE440 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2003-07-20 | 15 | 32733.2556 | 2010-07-20 | 15 |  |  |  | Compr + Both Fans Wh: 31777; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 16
CE500 | 27485.51 | 28-Oct | 15 | 27707 | 2001-08-16 | 16 | 27706 | 2001-08-16 | 16 | 27646.4256 | 2010-06-29 | 16 | 26567 | 1900-06-29 | 16 | Compr + Both Fans Wh: 27555; Compr + Both Fans Date: 2003-06-29; Compr + Both Fans Hour: 15
CE510 | 30593.05 | 29-Apr | 19 | 31188 | 2001-07-20 | 15 | 31188 | 2001-07-20 | 15 | 31177.751 | 2010-06-17 | 14 | 29948 | 1900-06-17 | 14 | Compr + Both Fans Wh: 31097; Compr + Both Fans Date: 2003-06-17; Compr + Both Fans Hour: 13
CE520 | 27329.6 | 28-Sep | 15 | 27878 | 2004-08-14 | 16 | 27878 | 2004-07-23 | 16 | 27652.6954 | 2010-06-29 | 16 | 26675 | 1900-07-20 | 16 | Compr + Both Fans Wh: 28343; Compr + Both Fans Date: 2003-05-23; Compr + Both Fans Hour: 15
CE522 | 27383.59 | 12-Mai | 15 | 27868 | 2002-08-16 | 16 | 27866 | 2002-08-16 | 16 | 27658.7918 | 2010-06-29 | 16 | 26514 | 1900-06-29 | 16 | Compr + Both Fans Wh: 27636; Compr + Both Fans Date: 2003-06-29; Compr + Both Fans Hour: 15
CE525 | 27739.77 | 26-Jul | 16 | 27466 | 2002-07-08 | 16 | 27466 | 2002-07-08 | 16 | 27576.5137 | 2010-06-29 | 16 | 26683 | 1900-06-29 | 16 | Compr + Both Fans Wh: 27462; Compr + Both Fans Date: 2003-06-29; Compr + Both Fans Hour: 15
CE530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19638.7657 | 2010-07-20 | 15 | 18776 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19626; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 15
CE540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19726.32 | 2010-07-20 | 15 | 18794 | 1900-06-04 | 15 | Compr + Both Fans Wh: 19799; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 15
CE545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19539.7081 | 2010-07-20 | 15 | 18764 | 1900-07-20 | 15 | Compr + Both Fans Wh: 19497; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 15
Weather Data Checks, CE300 only, Maxima
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
ODB | 34.7 | 20-Jul | 15 | 35 | 2002-07-20 | 15 | 35 | 2002-07-20 | 15 | 34.775 | 2010-07-20 | 15 | 35 | 1900-07-20 | 15 | Compr + Both Fans Wh: 35; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
OHR | 0.021878 | 02-Oct | 9 | 0.0225 | 2002-10-02 | 9 | 0.0225 | 2002-10-02 | 9 | 0.021842 | 2010-10-02 | 9 | 0.022406 | 1900-10-02 | 9 | Compr + Both Fans Wh: 0.0223; Compr + Both Fans Date: 2003-10-02; Compr + Both Fans Hour: 9
Maxima, Minima for COP2 and zone conditions
Maximum COP2
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 4.1683 | 16-Apr | 3 | 3.869 | 2002-04-30 | 16 | 3.857 | 2002-04-30 | 16 | 3.9252 | 2010-04-30 | 15 | 3.8706 | 1900-04-30 | 16 | Compr + Both Fans Wh: 3.88; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 16
CE310 | 4.1433 | 30-Apr | 15 | 4.141 | 2002-04-30 | 16 | 4.128 | 2002-04-30 | 16 | 4.1729 | 2010-04-30 | 15 | 4.1276 | 1900-04-30 | 15 | Compr + Both Fans Wh: 4.12; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 15
CE320 | 4.1683 | 16-Apr | 3 | 5.143 | 2002-10-02 | 9 | 4.967 | 2002-10-02 | 9 | 3.9395 | 2010-09-16 | 15 | 3.9433 | 1900-09-16 | 15 | Compr + Both Fans Wh: 4.38; Compr + Both Fans Date: 2003-12-18; Compr + Both Fans Hour: 3
CE330 | 4.1683 | 16-Apr | 3 | 4.109 | 2003-06-17 | 16 | 5.595 | 2002-10-02 | 9 | 4.0715 | 2010-09-16 | 14 | 4.1219 | 1900-06-17 | 16 | Compr + Both Fans Wh: 4.05; Compr + Both Fans Date: 2003-06-17; Compr + Both Fans Hour: 16
CE340 | 4.1683 | 16-Apr | 3 | 4.621 | 2002-10-02 | 9 | 5.339 | 2002-10-02 | 9 | 3.9866 | 2010-09-16 | 15 | 4.0172 | 1900-09-16 | 16 | Compr + Both Fans Wh: 3.95; Compr + Both Fans Date: 2003-09-16; Compr + Both Fans Hour: 16
CE350 | 4.1683 | 16-Apr | 3 | 3.889 | 2003-04-27 | 5 | 3.863 | 2004-10-05 | 3 | 4.5552 | 2010-10-13 | 1 | 3.9321 | 1900-10-04 | 24 | Compr + Both Fans Wh: 3.88; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 16
CE360 | 4.401 | 05-Oct | 1 | 4.428 | 2002-10-04 | 24 | 4.427 | 2002-10-04 | 24 | 4.4554 | 2010-10-04 | 24 | 4.432 | 1900-10-04 | 24 | Compr + Both Fans Wh: 4.44; Compr + Both Fans Date: 2003-10-04; Compr + Both Fans Hour: 24
CE400 | 4.0769 | 16-Sep | 15 | 4.088 | 2003-06-17 | 16 | 4.776 | 2003-09-18 | 15 | 4.0715 | 2010-09-16 | 14 |  |  |  | Compr + Both Fans Wh: 4.05; Compr + Both Fans Date: 2003-06-17; Compr + Both Fans Hour: 16
CE410 | 3.8879 | 30-Apr | 15 | 3.903 | 2002-04-30 | 15 | 3.855 | 2002-04-30 | 16 | [6 empty] | Compr + Both Fans Wh: 3.84; Compr + Both Fans Date: 2003-05-21; Compr + Both Fans Hour: 15
CE420 | 3.7813 | 27-Sep | 16 | 3.807 | 2003-05-21 | 15 | 3.759 | 2003-09-27 | 15 | 3.8214 | 2010-05-21 | 15 |  |  |  | Compr + Both Fans Wh: 3.94; Compr + Both Fans Date: 2003-05-21; Compr + Both Fans Hour: 13
CE430 | 3.7813 | 27-Sep | 16 | 3.805 | 2003-10-24 | 15 | 3.759 | 2003-09-27 | 15 | 3.7927 | 2010-05-21 | 16 |  |  |  | Compr + Both Fans Wh: 3.93; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 13
CE440 | 3.8835 | 12-Dez | 7 | 3.774 | 2002-09-27 | 15 | 3.759 | 2002-09-27 | 15 | 3.8018 | 2010-05-21 | 15 |  |  |  | Compr + Both Fans Wh: 3.81; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 15
CE500 | 4.2751 | 13-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.198 | 2010-03-16 | 10 | 4.1846 | 1900-03-16 | 10 | Compr + Both Fans Wh: 4.14; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 16
CE510 | 4.6925 | 05-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.6847 | 2010-10-05 | 1 | 4.6896 | 1900-10-04 | 24 | Compr + Both Fans Wh: 4.53; Compr + Both Fans Date: 2003-05-04; Compr + Both Fans Hour: 3
CE520 | 3.8137 | 30-Apr | 15 | 4.896 | 2004-03-16 | 10 | 4.652 | 2003-03-16 | 10 | 3.9377 | 2010-04-30 | 15 | 3.8017 | 1900-04-30 | 16 | Compr + Both Fans Wh: 3.84; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 16
CE522 | 3.9855 | 16-Mar | 10 | 6.233 | 2004-03-11 | 10 | 5.678 | 2004-03-11 | 10 | 4.0424 | 2010-04-30 | 15 | 3.9858 | 1900-04-30 | 16 | Compr + Both Fans Wh: 4; Compr + Both Fans Date: 2003-04-30; Compr + Both Fans Hour: 16
CE525 | 4.7178 | 13-Oct | 1 | 6.325 | 2004-04-12 | 9 | 6.031 | 2004-03-16 | 10 | 4.704 | 2010-03-16 | 10 | 4.6381 | 1900-03-16 | 10 | Compr + Both Fans Wh: 4.4; Compr + Both Fans Date: 2003-03-16; Compr + Both Fans Hour: 10
CE530 | 4.0061 | 02-Nov | 1 | 3.981 | 2004-03-11 | 10 | 3.85 | 2004-10-13 | 9 | 3.925 | 2010-03-16 | 10 | 3.84 | 1900-03-16 | 10 | Compr + Both Fans Wh: 3.88; Compr + Both Fans Date: 2003-03-16; Compr + Both Fans Hour: 10
CE540 | 3.456 | 30-Apr | 15 | 3.456 | 2004-04-30 | 16 | 3.455 | 2004-04-30 | 16 | 3.6959 | 2010-03-16 | 10 | 3.6667 | 1900-03-11 | 22 | Compr + Both Fans Wh: 3.69; Compr + Both Fans Date: 2003-10-17; Compr + Both Fans Hour: 5
CE545 | 4.2505 | 16-Mar | 10 | 4.275 | 2004-03-16 | 10 | 4.428 | 2004-03-16 | 10 | 4.1661 | 2010-03-16 | 10 | 4.1565 | 1900-03-16 | 10 | Compr + Both Fans Wh: 4.17; Compr + Both Fans Date: 2003-03-16; Compr + Both Fans Hour: 10
Minimum COP2
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 2.7931 | 24-Apr | 17 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7815 | 2010-06-13 | 17 | 2.7856 | 1900-06-13 | 17 | Compr + Both Fans Wh: 2.81; Compr + Both Fans Date: 2003-06-14; Compr + Both Fans Hour: 12
CE310 | 2.8652 | 01-Dec | 15 | 2.85 | 2002-12-01 | 14 | 2.851 | 2002-12-01 | 12 | 2.8927 | 2010-12-01 | 15 | 2.8726 | 1900-12-01 | 15 | Compr + Both Fans Wh: 2.87; Compr + Both Fans Date: 2003-12-01; Compr + Both Fans Hour: 14
CE320 | 2.8252 | 31-Mar | 14 | 2.801 | 2002-12-01 | 14 | 2.805 | 2003-12-01 | 15 | 2.8415 | 2010-03-31 | 15 | 2.8145 | 1900-03-31 | 15 | Compr + Both Fans Wh: 2.83; Compr + Both Fans Date: 2003-03-31; Compr + Both Fans Hour: 14
CE330 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8441 | 2010-03-31 | 15 | 2.8233 | 1900-03-31 | 15 | Compr + Both Fans Wh: 2.84; Compr + Both Fans Date: 2003-03-31; Compr + Both Fans Hour: 14
CE340 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8441 | 2010-03-31 | 15 | 2.8233 | 1900-03-31 | 15 | Compr + Both Fans Wh: 2.84; Compr + Both Fans Date: 2003-03-31; Compr + Both Fans Hour: 14
CE350 | 2.7904 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7815 | 2010-06-13 | 17 | 2.7859 | 1900-06-13 | 17 | Compr + Both Fans Wh: 2.81; Compr + Both Fans Date: 2003-06-14; Compr + Both Fans Hour: 12
CE360 | 2.8252 | 31-Mar | 14 | 2.799 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8441 | 2010-03-31 | 15 | 2.8233 | 1900-03-31 | 15 | Compr + Both Fans Wh: 2.84; Compr + Both Fans Date: 2003-03-31; Compr + Both Fans Hour: 14
CE400 | 2.7819 | 31-Mar | 19 | 2.734 | 2002-12-03 | 15 | 2.735 | 2003-12-03 | 13 | 2.7815 | 2010-06-13 | 17 |  |  |  | Compr + Both Fans Wh: 2.81; Compr + Both Fans Date: 2003-06-14; Compr + Both Fans Hour: 12
CE410 | 2.7858 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | [6 empty] | Compr + Both Fans Wh: 2.81; Compr + Both Fans Date: 2003-06-14; Compr + Both Fans Hour: 12
CE420 | 2.7931 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7815 | 2010-06-13 | 17 |  |  |  | Compr + Both Fans Wh: 2.81; Compr + Both Fans Date: 2003-06-14; Compr + Both Fans Hour: 12
CE430 | 2.7711 | 30-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7815 | 2010-06-13 | 17 |  |  |  | Compr + Both Fans Wh: 2.81; Compr + Both Fans Date: 2003-06-14; Compr + Both Fans Hour: 12
CE440 | 2.7825 | 31-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7815 | 2010-06-13 | 17 |  |  |  | Compr + Both Fans Wh: 2.81; Compr + Both Fans Date: 2003-04-08; Compr + Both Fans Hour: 13
CE500 | 2.6852 | 30-Jul | 12 | 2.693 | 2002-07-29 | 12 | 2.652 | 2004-03-30 | 17 | 2.7055 | 2010-07-30 | 12 | 2.6665 | 1900-07-30 | 12 | Compr + Both Fans Wh: 2.71; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 12
CE510 | 2.888 | 31-Mar | 15 | 2.817 | 2004-04-05 | 17 | 2.652 | 2004-03-30 | 17 | 2.8653 | 2010-03-31 | 18 | 2.8817 | 1900-03-31 | 15 | Compr + Both Fans Wh: 2.9; Compr + Both Fans Date: 2003-03-31; Compr + Both Fans Hour: 14
CE520 | 2.4417 | 30-Jul | 12 | 2.463 | 2004-04-05 | 17 | 2.394 | 2004-04-05 | 17 | 2.5316 | 2010-07-30 | 12 | 2.3333 | 1900-01-28 | 10 | Compr + Both Fans Wh: 2.47; Compr + Both Fans Date: 2003-07-30; Compr + Both Fans Hour: 12
CE522 | 2.5689 | 08-Jul | 17 | 2.572 | 2002-07-29 | 12 | 2.562 | 2004-03-31 | 17 | 2.6134 | 2010-07-30 | 12 | 2.4286 | 1900-03-30 | 17 | Compr + Both Fans Wh: 2.59; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 12
CE525 | 2.9111 | 14-Jul | 17 | 2.939 | 2003-07-30 | 12 | 2.814 | 2004-03-31 | 17 | 2.9396 | 2010-07-30 | 12 | 2.8941 | 1900-07-29 | 12 | Compr + Both Fans Wh: 2.9; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 12
CE530 | 2.5013 | 30-Jul | 12 | 2.495 | 2002-07-29 | 12 | 2.498 | 2002-07-29 | 12 | 2.532 | 2010-07-30 | 12 | 2.4733 | 1900-07-29 | 12 | Compr + Both Fans Wh: 2.52; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 12
CE540 | 2.253 | 30-Jul | 12 | 2.261 | 2003-07-29 | 12 | 2.262 | 2012-07-30 | 12 | 2.3828 | 2010-07-30 | 12 | 2.1429 | 1900-04-05 | 20 | Compr + Both Fans Wh: 2.28; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 12
CE545 | 2.7325 | 14-Jul | 17 | 2.72 | 2003-07-29 | 12 | 2.722 | 2002-07-30 | 12 | 2.66 | 2010-07-30 | 12 | 2.692 | 1900-07-29 | 12 | Compr + Both Fans Wh: 2.72; Compr + Both Fans Date: 2003-07-29; Compr + Both Fans Hour: 12
Maximum IDB (°C)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0025 | 2010-09-23 | 8 | 25.05 | 1900-02-20 | 17 | Compr + Both Fans Wh: 26.19; Compr + Both Fans Date: 2003-11-03; Compr + Both Fans Hour: 15
CE310 | 27.0778 | 20-Jul | 15 | 26.89 | 2004-07-20 | 16 | 26.72 | 2002-07-20 | 16 | 26.4747 | 2010-07-20 | 16 | 26.62 | 1900-07-20 | 15 | Compr + Both Fans Wh: 27.19; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 15
CE320 | 32.3604 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.5 | 2003-07-08 | 16 | 31.7089 | 2010-07-20 | 15 | 32.32 | 1900-07-20 | 15 | Compr + Both Fans Wh: 31.65; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 15
CE330 | 32.2321 | 20-Jul | 15 | 31.72 | 2004-07-08 | 16 | 32 | 2003-07-20 | 16 | 31.0686 | 2010-07-08 | 16 | 31.9 | 1900-07-20 | 15 | Compr + Both Fans Wh: 31.3; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 15
CE340 | 32.3066 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.56 | 2003-07-08 | 16 | 31.4977 | 2010-07-20 | 15 | 32.15 | 1900-07-20 | 15 | Compr + Both Fans Wh: 31.58; Compr + Both Fans Date: 2003-07-08; Compr + Both Fans Hour: 15
CE350 | 34.5841 | 01-Oct | 24 | 34.94 | 2003-06-23 | 24 | 34.94 | 2004-06-24 | 24 | 35.0021 | 2010-10-01 | 2 | 35 | 1900-04-21 | 1 | Compr + Both Fans Wh: 35; Compr + Both Fans Date: 2003-04-21; Compr + Both Fans Hour: 2
CE360 | 33.7585 | 10-Jul | 13 | 32.78 | 2002-07-20 | 15 | 32.56 | 2004-07-20 | 16 | 32.5106 | 2010-07-10 | 13 | 33 | 1900-07-20 | 15 | Compr + Both Fans Wh: 33.13; Compr + Both Fans Date: 2003-07-10; Compr + Both Fans Hour: 12
CE400 | 27.1148 | 16-Sep | 15 | 27.56 | 2003-09-16 | 16 | 28.83 | 2002-09-18 | 16 | 26.9099 | 2010-09-16 | 16 |  |  |  | Compr + Both Fans Wh: 26.04; Compr + Both Fans Date: 2003-08-15; Compr + Both Fans Hour: 15
CE410 | 26.8256 | 23-Oct | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | [6 empty] | Compr + Both Fans Wh: 26.19; Compr + Both Fans Date: 2003-11-03; Compr + Both Fans Hour: 15
CE420 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0025 | 2010-09-23 | 8 |  |  |  | Compr + Both Fans Wh: 26.23; Compr + Both Fans Date: 2003-10-20; Compr + Both Fans Hour: 15
CE430 | 27.1992 | 01-Nov | 16 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.003 | 2010-05-18 | 19 |  |  |  | Compr + Both Fans Wh: 26.45; Compr + Both Fans Date: 2003-10-23; Compr + Both Fans Hour: 15
CE440 | 27.0452 | 28-Apr | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.003 | 2010-04-24 | 19 |  |  |  | Compr + Both Fans Wh: 26.26; Compr + Both Fans Date: 2003-10-23; Compr + Both Fans Hour: 15
CE500 | 25.8054 | 30-Apr | 15 | 25.11 | 2001-04-21 | 16 | 25.11 | 2001-04-21 | 16 | 24.9998 | 2010-03-31 | 18 | 25.02 | 1900-03-30 | 17 | Compr + Both Fans Wh: 25; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 11
CE510 | 26.1003 | 09-Jul | 15 | 25.11 | 2001-04-21 | 3 | 25.11 | 2001-04-21 | 3 | 24.9998 | 2010-03-31 | 18 | 25.02 | 1900-03-30 | 17 | Compr + Both Fans Wh: 25; Compr + Both Fans Date: 2003-04-24; Compr + Both Fans Hour: 12
CE520 | 16.1232 | 15-Aug | 15 | 16.11 | 2002-08-16 | 16 | 15.94 | 2004-07-10 | 16 | 15.0005 | 2010-04-16 | 1 | 15.98 | 1900-07-20 | 15 | Compr + Both Fans Wh: 18.62; Compr + Both Fans Date: 2003-06-04; Compr + Both Fans Hour: 16
CE522 | 21.0091 | 16-Jul | 15 | 20.11 | 2001-04-21 | 15 | 20.11 | 2003-04-21 | 15 | 20.0004 | 2010-04-16 | 20 | 20.05 | 1900-03-13 | 22 | Compr + Both Fans Wh: 20.93; Compr + Both Fans Date: 2003-04-21; Compr + Both Fans Hour: 15
CE525 | 36.08 | 10-Mai | 16 | 35.06 | 2003-04-21 | 16 | 35.06 | 2003-04-21 | 16 | 34.9995 | 2010-03-11 | 12 | 35 | 1900-03-11 | 10 | Compr + Both Fans Wh: 35; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 11
CE530 | 26.116 | 04-Jun | 15 | 25.06 | 2001-04-21 | 16 | 25.06 | 2001-04-21 | 16 | 25.0003 | 2010-03-30 | 17 | 25.02 | 1900-03-30 | 17 | Compr + Both Fans Wh: 25; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 11
CE540 | 16.1465 | 21-Sep | 16 | 15.11 | 2004-05-31 | 16 | 15.11 | 2004-05-31 | 16 | 15.0005 | 2010-03-25 | 8 | 15.05 | 1900-01-27 | 20 | Compr + Both Fans Wh: 15; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 10
CE545 | 35.6715 | 20-Jul | 15 | 35 | 2003-04-21 | 15 | 35 | 2004-04-21 | 15 | 35 | 2010-07-09 | 22 | 35 | 1900-03-11 | 10 | Compr + Both Fans Wh: 35; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 11
Minimum IDB (°C)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE310 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7174 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE320 | 7.93 | 06-Jan | 6 | 10.83 | 2001-01-06 | 7 | 10.78 | 2001-01-06 | 7 | 7.7537 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE330 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.716 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE340 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.716 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE350 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE360 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7177 | 2010-01-06 | 6 | 8 | 1900-01-05 | 5 | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE400 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE410 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | [6 empty] | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE420 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE430 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | Compr + Both Fans Wh: 6.99; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE440 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7175 | 2010-01-06 | 6 |  |  |  | Compr + Both Fans Wh: 7; Compr + Both Fans Date: 2003-01-06; Compr + Both Fans Hour: 5
CE500 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9388 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | Compr + Both Fans Wh: 24.04; Compr + Both Fans Date: 2003-04-15; Compr + Both Fans Hour: 5
CE510 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9388 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | Compr + Both Fans Wh: 24.04; Compr + Both Fans Date: 2003-04-15; Compr + Both Fans Hour: 5
CE520 | 8.3053 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.835 | 2010-12-21 | 1 | 8.51 | 1900-12-20 | 20 | Compr + Both Fans Wh: 13.57; Compr + Both Fans Date: 2003-11-01; Compr + Both Fans Hour: 7
CE522 | 8.4141 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.8978 | 2010-12-21 | 1 | 8.54 | 1900-12-20 | 20 | Compr + Both Fans Wh: 15.98; Compr + Both Fans Date: 2003-04-12; Compr + Both Fans Hour: 19
CE525 | 8.4442 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 9.0147 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | Compr + Both Fans Wh: 33.01; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 8
CE530 | 8.4215 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9381 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | Compr + Both Fans Wh: 24.04; Compr + Both Fans Date: 2003-04-15; Compr + Both Fans Hour: 5
CE540 | 8.2278 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.8327 | 2010-12-21 | 1 | 8.51 | 1900-12-20 | 20 | Compr + Both Fans Wh: 14.95; Compr + Both Fans Date: 2003-12-19; Compr + Both Fans Hour: 1
CE545 | 8.4486 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 9.0132 | 2010-12-21 | 2 | 8.54 | 1900-12-20 | 20 | Compr + Both Fans Wh: 33.01; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 8
Maximum Humidity Ratio (kg/kg)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 0.013284 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.013626 | 2010-11-16 | 17 | 0.013457 | 1900-11-16 | 16 | Compr + Both Fans Wh: 0.0134; Compr + Both Fans Date: 2003-11-16; Compr + Both Fans Hour: 16
CE310 | 0.01575 | 01-Oct | 23 | 0.0188 | 2002-10-15 | 9 | 0.0189 | 2002-10-15 | 9 | 0.015637 | 2010-10-01 | 8 | 0.015432 | 1900-10-02 | 8 | Compr + Both Fans Wh: 0.0157; Compr + Both Fans Date: 2003-10-02; Compr + Both Fans Hour: 8
CE320 | 0.018017 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0176 | 2002-07-10 | 12 | 0.017807 | 2010-07-10 | 13 | 0.017547 | 1900-07-10 | 12 | Compr + Both Fans Wh: 0.0177; Compr + Both Fans Date: 2003-07-10; Compr + Both Fans Hour: 12
CE330 | 0.017651 | 10-Jul | 12 | 0.0178 | 2003-10-02 | 9 | 0.0177 | 2002-07-10 | 13 | 0.017934 | 2010-07-10 | 12 | 0.017045 | 1900-07-10 | 13 | Compr + Both Fans Wh: 0.0177; Compr + Both Fans Date: 2003-07-10; Compr + Both Fans Hour: 12
CE340 | 0.017871 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0174 | 2002-07-10 | 12 | 0.017787 | 2010-07-10 | 12 | 0.017272 | 1900-07-10 | 13 | Compr + Both Fans Wh: 0.0177; Compr + Both Fans Date: 2003-07-10; Compr + Both Fans Hour: 12
CE350 | 0.016758 | 01-Oct | 24 | 0.0199 | 2002-08-02 | 22 | 0.0199 | 2002-08-02 | 22 | 0.01719 | 2010-10-02 | 1 | 0.016479 | 1900-10-02 | 2 | Compr + Both Fans Wh: 0.0166; Compr + Both Fans Date: 2003-10-02; Compr + Both Fans Hour: 1
CE360 | 0.013433 | 10-Jul | 13 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01386 | 2010-07-10 | 13 | 0.013457 | 1900-11-16 | 16 | Compr + Both Fans Wh: 0.0134; Compr + Both Fans Date: 2003-11-16; Compr + Both Fans Hour: 16
CE400 | 0.016944 | 05-Apr | 22 | 0.017 | 2002-04-05 | 21 | 0.017 | 2003-04-05 | 21 | 0.016876 | 2010-04-05 | 22 |  |  |  | Compr + Both Fans Wh: 0.0173; Compr + Both Fans Date: 2003-04-22; Compr + Both Fans Hour: 6
CE410 | 0.016835 | 05-Apr | 22 | 0.0169 | 2002-04-02 | 5 | 0.0169 | 2002-04-02 | 5 | [6 empty] | Compr + Both Fans Wh: 0.0173; Compr + Both Fans Date: 2003-04-22; Compr + Both Fans Hour: 6
CE420 | 0.014297 | 02-Apr | 10 | 0.0147 | 2003-04-01 | 21 | 0.0141 | 2002-04-17 | 3 | 0.014593 | 2010-04-02 | 18 |  |  |  | Compr + Both Fans Wh: 0.0147; Compr + Both Fans Date: 2003-04-02; Compr + Both Fans Hour: 18
CE430 | 0.016231 | 02-Apr | 5 | 0.0156 | 2002-04-02 | 4 | 0.0156 | 2003-04-02 | 4 | 0.016135 | 2010-04-02 | 5 |  |  |  | Compr + Both Fans Wh: 0.0158; Compr + Both Fans Date: 2003-04-02; Compr + Both Fans Hour: 5
CE440 | 0.013313 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.013626 | 2010-11-16 | 17 |  |  |  | Compr + Both Fans Wh: 0.0134; Compr + Both Fans Date: 2003-11-16; Compr + Both Fans Hour: 16
CE500 | 0.01172 | 11-Jul | 15 | 0.0119 | 2004-07-20 | 15 | 0.0118 | 2004-04-06 | 10 | 0.011685 | 2010-07-20 | 15 | 0.011713 | 1900-07-20 | 15 | Compr + Both Fans Wh: 0.0115; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 10
CE510 | 0.011871 | 07-Sep | 15 | 0.0119 | 2001-07-20 | 15 | 0.0119 | 2001-07-20 | 15 | 0.011689 | 2010-07-20 | 15 | 0.011716 | 1900-07-20 | 15 | Compr + Both Fans Wh: 0.0115; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 10
CE520 | 0.0075403 | 07-Sep | 15 | 0.0077 | 2004-07-10 | 16 | 0.0078 | 2004-03-29 | 10 | 0.0070236 | 2010-07-20 | 15 | 0.007566 | 1900-07-20 | 15 | Compr + Both Fans Wh: 0.0106; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 16
CE522 | 0.0094264 | 20-Jul | 16 | 0.0095 | 2003-06-04 | 15 | 0.0138 | 2004-04-06 | 10 | 0.009111 | 2010-07-20 | 15 | 0.009398 | 1900-07-20 | 15 | Compr + Both Fans Wh: 0.0107; Compr + Both Fans Date: 2003-01-01; Compr + Both Fans Hour: 2
CE525 | 0.017932 | 10-Mai | 16 | 0.018 | 2004-07-20 | 15 | 0.018 | 2002-07-20 | 15 | 0.018486 | 2010-07-20 | 15 | 0.017626 | 1900-07-20 | 15 | Compr + Both Fans Wh: 0.0173; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE530 | 0.0069892 | 01-Jan | 1 | 0.0081 | 2001-07-20 | 15 | 0.0081 | 2004-07-20 | 15 | 0.0067755 | 2010-03-11 | 1 | 0.005491 | 1900-04-01 | 1 | Compr + Both Fans Wh: 0.00677; Compr + Both Fans Date: 2003-10-26; Compr + Both Fans Hour: 9
CE540 | 0.006084 | 01-Jan | 1 | 0.005 | 2003-06-04 | 13 | 0.0063 | 2004-04-08 | 8 | 0.0067755 | 2010-03-11 | 1 | 0.003256 | 1900-04-01 | 1 | Compr + Both Fans Wh: 0.00634; Compr + Both Fans Date: 2003-03-11; Compr + Both Fans Hour: 9
CE545 | 0.0069892 | 01-Jan | 1 | 0.0122 | 2004-07-20 | 15 | 0.0122 | 2004-07-20 | 15 | 0.0067755 | 2010-12-31 | 7 | 0.006689 | 1900-04-01 | 1 | Compr + Both Fans Wh: 0.00763; Compr + Both Fans Date: 2003-11-05; Compr + Both Fans Hour: 9
Minimum Humidity Ratio (kg/kg)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE310 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019433 | 2010-01-05 | 7 | 0.002019 | 1900-01-04 | 7 | Compr + Both Fans Wh: 0.00196; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 7
CE320 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019336 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE330 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE340 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE350 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE360 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 | 0.001968 | 1900-01-10 | 3 | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE400 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE410 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | [6 empty] | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE420 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE430 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 6
CE440 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019277 | 2010-01-11 | 3 |  |  |  | Compr + Both Fans Wh: 0.00197; Compr + Both Fans Date: 2003-01-05; Compr + Both Fans Hour: 7
CE500 | 0.0068276 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0070048 | 2010-12-20 | 12 | 0.006908 | 1900-12-20 | 20 | Compr + Both Fans Wh: 0.0103; Compr + Both Fans Date: 2003-11-02; Compr + Both Fans Hour: 2
CE510 | 0.0068276 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0070048 | 2010-12-20 | 12 | 0.006908 | 1900-12-20 | 20 | Compr + Both Fans Wh: 0.0105; Compr + Both Fans Date: 2003-04-02; Compr + Both Fans Hour: 22
CE520 | 0.006103 | 26-Nov | 2 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0065213 | 2010-11-10 | 9 | 0.006525 | 1900-11-27 | 23 | Compr + Both Fans Wh: 0.00657; Compr + Both Fans Date: 2003-11-01; Compr + Both Fans Hour: 7
CE522 | 0.0068215 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0069847 | 2010-12-20 | 12 | 0.006908 | 1900-12-20 | 20 | Compr + Both Fans Wh: 0.00783; Compr + Both Fans Date: 2003-04-02; Compr + Both Fans Hour: 21
CE525 | 0.0068356 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0070421 | 2010-12-20 | 12 | 0.006909 | 1900-12-20 | 20 | Compr + Both Fans Wh: 0.0154; Compr + Both Fans Date: 2003-11-02; Compr + Both Fans Hour: 2
CE530 | 0.006208 | 01-Apr | 1 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0067348 | 2010-10-18 | 12 | 0.005454 | 1900-11-01 | 21 | Compr + Both Fans Wh: 0.00663; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 5
CE540 | 0.0041096 | 05-Oct | 3 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0038186 | 2010-10-18 | 9 | 0.003253 | 1900-04-29 | 23 | Compr + Both Fans Wh: 0.0042; Compr + Both Fans Date: 2003-10-15; Compr + Both Fans Hour: 5
CE545 | 0.006208 | 01-Apr | 1 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0067755 | 2010-04-01 | 2 | 0.006685 | 1900-07-20 | 15 | Compr + Both Fans Wh: 0.007; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 8
Maximum Relative Humidity (%)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 68.3673 | 2010-11-16 | 17 | 68 | 1900-11-16 | 16 | Compr + Both Fans Wh: 67.44; Compr + Both Fans Date: 2003-11-16; Compr + Both Fans Hour: 16
CE310 | 77.7029 | 02-Oct | 4 | 100.18 | 2002-10-15 | 9 | 100.7 | 2002-10-15 | 9 | 78.6439 | 2010-10-02 | 8 | 77 | 1900-06-12 | 8 | Compr + Both Fans Wh: 78.19; Compr + Both Fans Date: 2003-10-02; Compr + Both Fans Hour: 8
CE320 | 81.8358 | 18-Sep | 10 | 83.41 | 2004-10-02 | 9 | 83.67 | 2003-04-22 | 18 | 82.9666 | 2010-09-18 | 10 | 83 | 1900-09-03 | 17 | Compr + Both Fans Wh: 81.88; Compr + Both Fans Date: 2003-09-16; Compr + Both Fans Hour: 20
CE330 | 76.6591 | 22-Sep | 20 | 78.46 | 2004-10-02 | 9 | 77.94 | 2003-09-18 | 9 | 76.8755 | 2010-09-03 | 10 | 76 | 1900-06-10 | 18 | Compr + Both Fans Wh: 78.7; Compr + Both Fans Date: 2003-09-02; Compr + Both Fans Hour: 12
CE340 | 79.9293 | 18-Sep | 10 | 81.37 | 2004-09-18 | 9 | 81.26 | 2003-04-22 | 18 | 80.796 | 2010-09-18 | 10 | 80 | 1900-09-03 | 17 | Compr + Both Fans Wh: 80.25; Compr + Both Fans Date: 2003-09-16; Compr + Both Fans Hour: 20
CE350 | 68.7892 | 16-Nov | 17 | 81.12 | 2003-08-07 | 21 | 81.12 | 2003-08-07 | 21 | 68.3673 | 2010-11-16 | 17 | 70 | 1900-10-02 | 8 | Compr + Both Fans Wh: 72.65; Compr + Both Fans Date: 2003-08-03; Compr + Both Fans Hour: 7
CE360 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 68.3671 | 2010-11-16 | 17 | 68 | 1900-11-16 | 16 | Compr + Both Fans Wh: 67.44; Compr + Both Fans Date: 2003-11-16; Compr + Both Fans Hour: 16
CE400 | 83.7534 | 05-Apr | 22 | 85.57 | 2002-04-05 | 21 | 85.57 | 2003-04-05 | 21 | 84.6363 | 2010-04-05 | 22 |  |  |  | Compr + Both Fans Wh: 86.31; Compr + Both Fans Date: 2003-04-22; Compr + Both Fans Hour: 6
CE410 | 83.2247 | 05-Apr | 22 | 84.79 | 2002-04-02 | 5 | 84.79 | 2002-04-02 | 5 | [6 empty] | Compr + Both Fans Wh: 86.18; Compr + Both Fans Date: 2003-04-22; Compr + Both Fans Hour: 6
CE420 | 70.8411 | 02-Apr | 10 | 74.51 | 2003-04-17 | 7 | 71.53 | 2002-04-17 | 3 | 73.284 | 2010-04-02 | 18 |  |  |  | Compr + Both Fans Wh: 73.85; Compr + Both Fans Date: 2003-04-02; Compr + Both Fans Hour: 18
CE430 | 80.7087 | 02-Apr | 5 | 78.43 | 2002-04-02 | 4 | 78.43 | 2003-04-02 | 4 | 80.7427 | 2010-04-02 | 5 |  |  |  | Compr + Both Fans Wh: 78.94; Compr + Both Fans Date: 2003-04-02; Compr + Both Fans Hour: 5
CE440 | 68.7242 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 68.3673 | 2010-11-16 | 17 |  |  |  | Compr + Both Fans Wh: 67.51; Compr + Both Fans Date: 2003-11-16; Compr + Both Fans Hour: 16
CE500 | 100 | 21-Nov | 24 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 2010-11-21 | 9 | 100 | 1900-11-14 | 5 | Compr + Both Fans Wh: 60.08; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 5
CE510 | 100 | 21-Nov | 24 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 2010-11-21 | 9 | 100 | 1900-11-14 | 5 | Compr + Both Fans Wh: 57.51; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 5
CE520 | 90.2299 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 93.8137 | 2010-12-20 | 11 | 95 | 1900-12-20 | 17 | Compr + Both Fans Wh: 71.77; Compr + Both Fans Date: 2003-08-16; Compr + Both Fans Hour: 17
CE522 | 100 | 18-Dec | 8 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 2010-12-15 | 22 | 100 | 1900-12-15 | 1 | Compr + Both Fans Wh: 71.32; Compr + Both Fans Date: 2003-04-05; Compr + Both Fans Hour: 17
CE525 | 100 | 12-Nov | 20 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 2010-11-12 | 19 | 100 | 1900-11-11 | 23 | Compr + Both Fans Wh: 51.12; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 8
CE530 | 91.0445 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 96.1602 | 2010-12-20 | 11 | 79 | 1900-12-20 | 8 | Compr + Both Fans Wh: 36.01; Compr + Both Fans Date: 2003-04-20; Compr + Both Fans Hour: 21
CE540 | 61.275 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 55.1794 | 2010-12-20 | 11 | 47 | 1900-12-20 | 6 | Compr + Both Fans Wh: 39.96; Compr + Both Fans Date: 2003-04-18; Compr + Both Fans Hour: 18
CE545 | 90.8772 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 96.2348 | 2010-12-20 | 11 | 97 | 1900-12-20 | 4 | Compr + Both Fans Wh: 24.14; Compr + Both Fans Date: 2003-12-24; Compr + Both Fans Hour: 1
Minimum Relative Humidity (%)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnergyPlus | Date | Hour | CODY | Date | Hour | Compr + Both Fans Wh: HOT3000; Compr + Both Fans Date: Date; Compr + Both Fans Hour: Hour; Compr + Both Fans Wh: Tested Prg; Sensible Date: Date; Sensible Hour: Hour
CE300 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4023 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | Compr + Both Fans Wh: 14.94; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 8
CE310 | 13.3898 | 06-Nov | 6 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 15.5023 | 2010-11-06 | 8 | 16 | 1900-11-06 | 8 | Compr + Both Fans Wh: 15.93; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 8
CE320 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.6416 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | Compr + Both Fans Wh: 12.92; Compr + Both Fans Date: 2003-12-20; Compr + Both Fans Hour: 5
CE330 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4025 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | Compr + Both Fans Wh: 14.94; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 8
CE340 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4025 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | Compr + Both Fans Wh: 14.94; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 8
CE350 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4023 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | Compr + Both Fans Wh: 14.94; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 8
CE360 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.4023 | 2010-11-06 | 6 | 15 | 1900-11-06 | 5 | Compr + Both Fans Wh: 14.94; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 8
CE400 | 13.209 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 2010-11-06 | 6 |  |  |  | Compr + Both Fans Wh: 14.57; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 5
CE410 | 13.2091 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | [6 empty] | Compr + Both Fans Wh: 14.58; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 5
CE420 | 13.2099 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9257 | 2010-11-06 | 6 |  |  |  | Compr + Both Fans Wh: 14.59; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 5
CE430 | 13.2078 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 2010-11-06 | 6 |  |  |  | Compr + Both Fans Wh: 14.58; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 5
CE440 | 13.2069 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 2010-11-06 | 6 |  |  |  | Compr + Both Fans Wh: 14.54; Compr + Both Fans Date: 2003-11-06; Compr + Both Fans Hour: 5
CE500 | 53.4054 | 30-Apr | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 55.1668 | 2010-04-30 | 4 | 54 | 1900-10-04 | 24 | Compr + Both Fans Wh: 52.83; Compr + Both Fans Date: 2003-10-05; Compr + Both Fans Hour: 1
CE510 | 52.0879 | 04-Oct | 23 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 55.2884 | 2010-05-04 | 3 | 54 | 1900-10-04 | 23 | Compr + Both Fans Wh: 53.15; Compr + Both Fans Date: 2003-05-04; Compr + Both Fans Hour: 4
CE520 | 61.2679 | 25-Nov | 24 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 61.7266 | 2010-11-27 | 24 | 61 | 1900-11-27 | 22 | Compr + Both Fans Wh: 61.9; Compr + Both Fans Date: 2003-07-20; Compr + Both Fans Hour: 15
CE522 | 58.5054 | 30-Apr | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 59.1798 | 2010-04-30 | 4 | 60 | 1900-10-04 | 23 | Compr + Both Fans Wh: 57.97; Compr + Both Fans Date: 2003-10-05; Compr + Both Fans Hour: 1
CE525 | 45.5284 | 30-Apr | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 47.8518 | 2010-10-05 | 2 | 44 | 1900-05-04 | 4 | Compr + Both Fans Wh: 44.4; Compr + Both Fans Date: 2003-10-05; Compr + Both Fans Hour: 1
CE530 | 29.5934 | 04-Jun | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 34.0277 | 2010-04-18 | 18 | 28 | 1900-04-01 | 10 | Compr + Both Fans Wh: 33.68; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 13
CE540 | 36.4749 | 21-Sep | 16 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 36.0017 | 2010-09-28 | 16 | 31 | 1900-04-01 | 1 | Compr + Both Fans Wh: 39.74; Compr + Both Fans Date: 2003-10-05; Compr + Both Fans Hour: 1
CE545 | 17.1244 | 20-Jul | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 19.227 | 2010-04-18 | 17 | 19 | 1900-04-01 | 10 | Compr + Both Fans Wh: 20.14; Compr + Both Fans Date: 2003-04-01; Compr + Both Fans Hour: 12
DIFFERENCE COMPARISONS ("DELTA") START AT 1450
SENSITIVITY DIFFERENCE COMPARISONS ("DELTA")
Delta Total Consumption |  |  | (kWh)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 4339.6026 | 4629 | 4629 | 4544.7265 | 4543.158 | 4538
CE320-CE300 | 4425.8798 | 3995 | 4037 | 4333.4627 | 4424.404 | 4387
CE330-CE300 | 5329.5231 | 4958 | 4683 | 5397.736 | 5558.726 | 5260
CE330-CE320 | 903.6433 | 963 | 646 | 1064.2734 | 1134.322 | 873
CE340-CE300 | 4985.5179 | 4608 | 4510 | 5037.381 | 5088.85 | 4877
CE330-CE340 | 344.0053 | 350 | 173 | 360.355 | 469.876 | 383
CE350-CE300 | -3396.7978 | -4203 | -4207 | -3600.5239 | -3389.819 | -3328
CE360-CE300 | 19665.0145 | 19314 | 19261 | 19959.0734 | 19866.847 | 19998
CE400-CE300 | -3588.6237 | -3904 | -3879 | -3732.9566 |  | -3657
CE410-CE300 | -3555.3454 | -3082 | -3056 |  |  | -3567
CE420-CE300 | -2246.7696 | -2220 | -1845 | -2010.1329 |  | -1862
CE430-CE300 | -3095.7459 | -2818 | -2944 | -2973.2406 |  | -3252
CE440-CE300 | -1942.4562 | -1718 | -1782 | -1713.9923 |  | -1822
CE500-CE300 | -13295.8902 | -11933 | -11933 | -11711.0294 | -12653.458 | -11932
CE510-CE500 | 17217.9243 | 18099 | 18100 | 17736.3726 | 17414.1 | 17794
CE525-CE520 | -4665.708 | -4981 | -4969 | -4315.6173 | -4889.357 | -4458
CE530-CE500 | -5056.616 | -5277 | -5285 | -5292.6649 | -4880.485 | -5263
CE545-CE540 | -3743.2989 | -4076 | -4083 | -2425.3866 | -3745.491 | -3825
Delta Compressor Consumption |  |  | (kWh)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 3986.0911 | 4244 | 4244 | 4544.7265 | 4166.82 | 4177
CE320-CE300 | 4079.6031 | 3681 | 3721 | 4333.4627 | 4076.025 | 4036
CE330-CE300 | 4946.1978 | 4603 | 4352 | 5397.736 | 5157.732 | 4899
CE330-CE320 | 866.5947 | 922 | 631 | 1064.2734 | 1081.707 | 863
CE340-CE300 | 4609.403 | 4260 | 4172 | 5037.381 | 4702.789 | 4524
CE330-CE340 | 336.7947 | 343 | 180 | 360.355 | 454.943 | 375
CE350-CE300 | -3036.6939 | -3767 | -3772 | -3600.5239 | -3031.946 | -2985
CE360-CE300 | 17752.3056 | 17430 | 17382 | 19959.0734 | 17927.161 | 18065
CE400-CE300 | -3174.5856 | -3463 | -3442 | -3732.9566 |  | -3247
CE410-CE300 | -3149.0399 | -2746 | -2723 |  |  | -3191
CE420-CE300 | -1994.9489 | -1973 | -1639 | -2010.1329 |  | -1662
CE430-CE300 | -2754.9132 | -2510 | -2622 | -2973.2406 |  | -2910
CE440-CE300 | -1724.4011 | -1527 | -1584 | -1713.9923 |  | -1627
CE500-CE300 | -4499.2388 | -3096 | -3095 | -3477.264 | -3912.149 | -3354
CE510-CE500 | 13805.7311 | 14303 | 14304 | 15702.0336 | 13913.445 | 14230
CE525-CE520 | -2963.4018 | -3241 | -3233 | -3476.844 | -3148.17 | -2742
CE530-CE500 | -4197.3004 | -4346 | -4354 | -4754.5558 | -4001.924 | -4350
CE545-CE540 | -2398.8748 | -2713 | -2720 | -1987.0433 | -2413.197 | -2449
Delta Condenser Fan Consumption |  |  | (kWh)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 353.5115 | 385 | 385 |  | 376.338 | 368
CE320-CE300 | 346.2767 | 314 | 316 |  | 348.379 | 358
CE330-CE300 | 383.3254 | 355 | 331 |  | 400.994 | 370
CE330-CE320 | 37.0487 | 41 | 15 |  | 52.615 | 12
CE340-CE300 | 376.1148 | 348 | 338 |  | 386.061 | 361
CE330-CE340 | 7.2105 | 7 | -7 |  | 14.933 | 9
CE350-CE300 | -360.1038 | -436 | -435 |  | -357.873 | -353
CE360-CE300 | 1912.7089 | 1884 | 1879 |  | 1939.686 | 1949
CE400-CE300 | -414.0381 | -441 | -437 |  |  | -421
CE410-CE300 | -406.3054 | -336 | -333 |  |  | -387
CE420-CE300 | -251.8207 | -247 | -206 |  |  | -208
CE430-CE300 | -340.8327 | -308 | -322 |  |  | -353
CE440-CE300 | -218.0552 | -191 | -198 |  |  | -203
CE500-CE300 | -480.5531 | -326 | -327 |  | -414.621 | -347
CE510-CE500 | 1461.0219 | 1534 | 1534 |  | 1498.872 | 1526
CE525-CE520 | -728.888 | -752 | -750 |  | -745.624 | -733
CE530-CE500 | -367.939 | -395 | -395 |  | -376.185 | -391
CE545-CE540 | -575.6512 | -606 | -606 |  | -570.545 | -589
Delta ID Fan Consumption |  | (kWh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE320-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE330-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE330-CE320 | 0 | 0 | 0 | 0 | 0 | 0
CE340-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE400-CE300 | 0 | 0 | 0 | 0 |  | 0
CE410-CE300 | 0 | 0 | 0 |  |  | 0
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0
CE430-CE300 | 0 | 0 | 0 | 0 |  | 0
CE440-CE300 | 0 | 0 | 0 | 0 |  | 0
CE500-CE300 | -8316.0984 | -8511 | -8511 | -8233.7654 | -8326.688 | -8241
CE510-CE500 | 1951.1712 | 2262 | 2262 | 2034.3391 | 2001.783 | 2038
CE525-CE520 | -973.4182 | -988 | -986 | -838.7733 | -995.563 | -979
CE530-CE500 | -491.3766 | -536 | -536 | -538.1091 | -502.376 | -522
CE545-CE540 | -768.7729 | -757 | -757 | -438.3434 | -761.749 | -787
Delta Total Coil Load |  | (kWh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 18915.2641 | 20111.3496 | 20120.1426 | 19129.6407 | 19551.277 | 19004
CE320-CE300 | 19364.8105 | 19072.8963 | 19201.2741 | 18765.6099 | 19396.718 | 18700
CE330-CE300 | 24586.004 | 23446.5345 | 23701.5315 | 24893.4107 | 25968.326 | 23751
CE330-CE320 | 5221.1935 | 4373.6382 | 4500.2574 | 6127.8007 | 6571.608 | 5051
CE340-CE300 | 22301.1114 | 21744.2097 | 21931.2075 | 22390.5659 | 22931.621 | 21496
CE330-CE340 | 2284.8926 | 1702.3248 | 1770.324 | 2502.8448 | 3036.705 | 2255
CE350-CE300 | -11038.8699 | -13547.082 | -13657.2876 | -11527.5816 | -10884.426 | -10868
CE360-CE300 | 82547.1951 | 82523.7705 | 82561.8735 | 83930.4952 | 83455.59 | 83911
CE400-CE300 | -11634.0454 | -12365.889 | -12266.8212 | -11904.1083 |  | -11359
CE410-CE300 | -11754.0136 | -10503.8247 | -10448.4288 |  |  | -12082
CE420-CE300 | -7817.5601 | -7672.4787 | -6409.8039 | -6968.483 |  | -6454
CE430-CE300 | -10670.5555 | -9642.6969 | -10072.6746 | -10176.5973 |  | -11057
CE440-CE300 | -6715.504 | -5903.3271 | -6110.8419 | -5900.6427 |  | -6228
CE500-CE300 | -17069.7612 | -11287.5741 | -11299.5912 | -11746.7665 | -14639.223 | -12643
CE510-CE500 | 60530.8791 | 63325.1343 | 63324.8412 | 62438.3562 | 60539.443 | 62424
CE525-CE520 | -128.599 | -1172.1069 | -1170.3483 | -1114.4751 | -210.544 | -991
CE530-CE500 | -18311.2583 | -19361.5998 | -19361.5998 | -18626.8261 | -18229.952 | -18612
CE545-CE540 | -131.4753 | -890.1447 | -890.1447 | -684.7141 | -204.732 | -794
Delta Sensible Coil Load
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | -405.371 | 504.132 | 507.9423 | -26.7995 | -24.393 | -108
CE320-CE300 | 6197.4569 | 6900.1602 | 6942.0735 | 6791.4957 | 6799.339 | 7543
CE330-CE300 | 6421.6281 | 7514.2047 | 7522.9977 | 8526.6982 | 7439.994 | 6631
CE330-CE320 | 224.1712 | 614.0445 | 580.9242 | 1735.2025 | 640.655 | -912
CE340-CE300 | 6370.8576 | 7256.5698 | 7305.8106 | 7633.8781 | 7171.095 | 6215
CE330-CE340 | 50.7704 | 257.6349 | 217.1871 | 892.82 | 268.899 | 416
CE350-CE300 | -6290.9181 | -8112.4218 | -8128.2492 | -6706.9451 | -6620.663 | -6423
CE360-CE300 | 78315.0867 | 79122.9312 | 79134.9483 | 80035.2385 | 78996.242 | 79506
CE400-CE300 | -14709.3889 | -14377.7274 | -14367.762 | -14564.2107 |  | -14010
CE410-CE300 | -10985.1029 | -8138.2146 | -8144.9559 |  |  | -9606
CE420-CE300 | -6271.9238 | -6130.7727 | -5192.5596 | -5728.0295 |  | -5207
CE430-CE300 | -8798.4022 | -8065.5258 | -8350.7121 | -8513.3758 |  | -9048
CE440-CE300 | -5785.676 | -5204.2836 | -5312.7306 | -5191.7822 |  | -5406
CE500-CE300 | -11617.9484 | -8147.0076 | -8158.7316 | -7760.7172 | -10335.24 | -7661
CE510-CE500 | 43046.1977 | 45710.1174 | 45709.8243 | 45090.7524 | 43050.834 | 45083
CE525-CE520 | -130.6037 | -883.9896 | -882.231 | -1056.6213 | -201.619 | -949
CE530-CE500 | 2.048 | -1076.2632 | -1075.9701 | -546.8842 | 0 | -528
CE545-CE540 | -130.4955 | -808.6629 | -808.6629 | -676.1559 | -201.642 | -792
Delta Latent Coil Load
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 19320.6351 | 19607.2176 | 19612.2003 | 19156.4402 | 19575.693 | 19111
CE320-CE300 | 13167.3536 | 12172.7361 | 12259.2006 | 11974.1143 | 12597.449 | 11157
CE330-CE300 | 18164.3759 | 15932.3298 | 16178.5338 | 16366.7125 | 18528.23 | 17119
CE330-CE320 | 4997.0223 | 3759.5937 | 3919.3332 | 4392.5982 | 5930.781 | 5962
CE340-CE300 | 15930.2538 | 14487.6399 | 14625.3969 | 14756.6878 | 15760.481 | 15279
CE330-CE340 | 2234.1221 | 1444.6899 | 1553.1369 | 1610.0247 | 2767.749 | 1840
CE350-CE300 | -4747.9518 | -5434.6602 | -5529.0384 | -4820.6365 | -4263.749 | -4446
CE360-CE300 | 4232.1084 | 3400.8393 | 3426.9252 | 3895.2567 | 4459.339 | 4403
CE400-CE300 | 3075.3436 | 2011.8384 | 2100.9408 | 2660.1023 |  | 2650
CE410-CE300 | -768.9108 | -2365.6101 | -2303.4729 |  |  | -2477
CE420-CE300 | -1545.6363 | -1541.706 | -1217.2443 | -1240.4535 |  | -1212
CE430-CE300 | -1872.1533 | -1577.1711 | -1721.9625 | -1663.2215 |  | -2010
CE440-CE300 | -929.828 | -699.0435 | -798.1113 | -708.8605 |  | -823
CE500-CE300 | -5451.8128 | -3140.5665 | -3140.8596 | -3986.0493 | -4304.002 | -4983
CE510-CE500 | 17484.6814 | 17615.0169 | 17615.0169 | 17347.6038 | 17488.438 | 17340
CE525-CE520 | 2.0047 | -288.1173 | -288.1173 | -57.8538 | -8.624 | -42
CE530-CE500 | -18313.3062 | -18285.3366 | -18285.6297 | -18079.9419 | -18229.955 | -18084
CE545-CE540 | -0.97976 | -81.4818 | -81.4818 | -8.5582 | -3.086 | -2
Delta Mean COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0.16552 | 0.1798 | 0.18013 | 0.15538 | 0.17086 | 0.15
CE320-CE300 | 0.17083 | 0.22029 | 0.21969 | 0.16788 | 0.17958 | 0.16
CE330-CE300 | 0.24166 | 0.25649 | 0.29907 | 0.25338 | 0.2709 | 0.23
CE330-CE320 | 0.070831 | 0.036201 | 0.079382 | 0.085508 | 0.091321 | 0.07
CE340-CE300 | 0.20521 | 0.23966 | 0.25826 | 0.21034 | 0.22316 | 0.19
CE330-CE340 | 0.036452 | 0.016833 | 0.040815 | 0.043047 | 0.047744 | 0.04
CE350-CE300 | -0.00011501 | 0.003096 | -0.0019178 | 0.0063283 | 0.0025325 | 0
CE360-CE300 | 0.41996 | 0.46293 | 0.46845 | 0.4406 | 0.44031 | 0.43
CE400-CE300 | 0.0012106 | 0.013724 | 0.014548 | 0.0089602 |  | 0.03
CE410-CE300 | -0.0095511 | -0.025269 | -0.026661 |  |  | -0.02
CE420-CE300 | -0.023 | -0.022394 | -0.019831 | -0.02108 |  | -0.02
CE430-CE300 | -0.02827 | -0.024649 | -0.025889 | -0.026368 |  | -0.02
CE440-CE300 | -0.017725 | -0.015393 | -0.015474 | -0.015876 |  | -0.01
CE500-CE300 | -0.045013 | -0.010183 | -0.010822 | -0.024005 | -0.034365 | -0.03
CE510-CE500 | 0.40948 | 0.41598 | 0.41577 | 0.40797 | 0.39713 | 0.41
CE525-CE520 | 0.58247 | 0.57414 | 0.57204 | 0.50377 | 0.60629 | 0.49
CE530-CE500 | -0.24223 | -0.25849 | -0.25718 | -0.21398 | -0.27645 | -0.22
CE545-CE540 | 0.5601 | 0.55853 | 0.56036 | 0.33359 | 0.54604 | 0.51
Delta Mean IDB
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0.1313 | 0.055556 | 0 | 0.0013565 | 0.0080616 | 0.02
CE320-CE300 | 0.27622 | 0.33333 | 0.33333 | 0.16367 | 0.24571 | 0.54
CE330-CE300 | 0.25545 | 0.22222 | 0.22222 | 0.18266 | 0.21382 | 0.19
CE330-CE320 | -0.02077 | -0.11111 | -0.11111 | 0.018995 | -0.031885 | -0.35
CE340-CE300 | 0.25135 | 0.22222 | 0.22222 | 0.20752 | 0.22722 | 0.22
CE330-CE340 | 0.0041016 | 0 | 0 | -0.024858 | -0.013394 | -0.03
CE350-CE300 | 2.0352 | 2.1111 | 2.1111 | 2.1509 | 2.187 | 2.16
CE360-CE300 | 1.7407 | 1.5556 | 1.5 | 1.2324 | 1.3992 | 1.38
CE400-CE300 | 0.50202 | 0 | 0 | 0.0012363 |  | 0
CE410-CE300 | 0.49787 | 0 | 0 |  |  | 0
CE420-CE300 | 0.3019 | 0 | 0 | -9.3106e-05 |  | 0
CE430-CE300 | 0.36731 | 0 | 0 | -0.00010336 |  | 0
CE440-CE300 | 0.2875 | 0 | 0 | -5.3781e-05 |  | 0
CE500-CE300 | -3.3901 | -3.3889 | -3.5 | -3.7113 | -2.9838 | -1.13
CE510-CE500 | 1.2445 | 0.11111 | 0.11111 | -0.022745 | 0 | 0
CE525-CE520 | 13.3272 | 13.6111 | 13.5556 | 13.5272 | 13.6289 | 15.8
CE530-CE500 | -0.20888 | -0.055556 | 0 | 0.20651 | 0 | 0
CE545-CE540 | 13.3159 | 13.5556 | 13.5556 | 13.5189 | 13.576 | 15.71
Delta Mean Humidity Ratio
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0.0020018 | 0.0021 | 0.0021 | 0.0019746 | 0.0019998 | 0.0019
CE320-CE300 | 0.00091896 | 0.0009 | 0.0009 | 0.00082797 | 0.00087438 | 0.0007
CE330-CE300 | 0.00067186 | 0.0007 | 0.0007 | 0.0006823 | 0.00063678 | 0.0007
CE330-CE320 | -0.00024709 | -0.0002 | -0.0002 | -0.00014568 | -0.00023759 | 0
CE340-CE300 | 0.00072232 | 0.0007 | 0.0007 | 0.00069759 | 0.00069351 | 0.0007
CE330-CE340 | -5.0461e-05 | 0 | 0 | -1.5289e-05 | -5.6729e-05 | 0
CE350-CE300 | 0.00063685 | 0.0008 | 0.0008 | 0.00063956 | 0.00058373 | 0.00057
CE360-CE300 | -0.0005696 | -0.0005 | -0.0005 | -0.00052024 | -0.00062237 | -0.00062
CE400-CE300 | 0.00073206 | 0.0008 | 0.0008 | 0.00080072 |  | 0.0008
CE410-CE300 | 0.00067139 | 0.0003 | 0.0003 |  |  | 0.0003
CE420-CE300 | 0.00019481 | 0.0002 | 0.0002 | 0.00016242 |  | 0.0001
CE430-CE300 | 0.00024119 | 0.0002 | 0.0002 | 0.00020337 |  | 0.0002
CE440-CE300 | 8.8738e-05 | 0.0001 | 0.0001 | 4.8002e-05 |  | 0
CE500-CE300 | 0.00070622 |  |  | 8.6686e-05 | 0.0010435 | 0.0015
CE510-CE500 | 0.00037457 | 0 | 0 | 7.3411e-06 | -8.8998e-07 | 0
CE525-CE520 | 0.0070203 |  |  | 0.0077564 | 0.0069569 | 0.00747
CE530-CE500 | -0.0035488 |  |  | -0.0026606 | -0.0044208 | -0.00403
CE545-CE540 | 0.0017664 |  |  | 0.0023868 | 0.0028945 | 0.00259
Delta Mean Relative Humidity
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 9.7158 | 10.25 | 10.25 | 9.9598 | 10.0148 | 9.87
CE320-CE300 | 3.3904 | 2.95 | 2.97 | 3.2494 | 3.2773 | 2.01
CE330-CE300 | 2.2296 | 2.32 | 2.37 | 2.5851 | 2.2587 | 2.77
CE330-CE320 | -1.1608 | -0.63 | -0.6 | -0.66425 | -1.0186 | 0.76
CE340-CE300 | 2.4702 | 2.43 | 2.45 | 2.5566 | 2.4705 | 2.85
CE330-CE340 | -0.24056 | -0.11 | -0.08 | 0.028551 | -0.21187 | -0.08
CE350-CE300 | -3.1309 | -2.81 | -2.73 | -3.4182 | -3.5099 | -3.37
CE360-CE300 | -7.5814 | -6.77 | -6.79 | -6.2219 | -6.9551 | -6.72
CE400-CE300 | 2.156 | 3.95 | 3.97 | 3.9572 |  | 4.08
CE410-CE300 | 1.8822 | 1.39 | 1.35 |  |  | 1.82
CE420-CE300 | 0.16451 | 0.88 | 0.69 | 0.80676 |  | 0.83
CE430-CE300 | 0.20708 | 0.91 | 1.02 | 1.0089 |  | 1.24
CE440-CE300 | -0.28509 | 0.2 | 0.29 | 0.23749 |  | 0.3
CE500-CE300 | 17.9113 |  |  | 10.6062 | 18.1158 | 15.8
CE510-CE500 | -2.3476 | -0.11 | -0.11 | 0.11417 | -0.010621 | 0.11
CE525-CE520 | -8.4071 |  |  | -6.4105 | -10.0881 | -14.8
CE530-CE500 | -19.7962 |  |  | -10.2243 | -24.4903 | -24.13
CE545-CE540 | -11.8961 |  |  | -7.6766 | -3.1763 | -14.62
Hourly Integrated Maxima and Minima Sensitivities
Delta Max Compressor+ODfan+IDfan Consumption
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 968.3645 | 1019 | 993 | 640.9591 | 721 | 614
CE320-CE300 | 1402.1615 | 1352 | 1379 | 1054.567 | 1172 | 1327
CE330-CE300 | 1720.664 | 1648 | 1805 | 1414.2502 | 1535 | 1787
CE330-CE320 | 318.5024 | 296 | 426 | 359.6832 | 363 | 460
CE340-CE300 | 1554.8648 | 1594 | 1588 | 1234.3106 | 1345 | 1553
CE330-CE340 | 165.7992 | 54 | 217 | 179.9396 | 190 | 234
CE350-CE300 | 0.85194 | 90 | 0 | 0.0021837 | 0 | -2
CE360-CE300 | 1143.4651 | 1172 | 1124 | 844.4186 | 931 | 1214
CE400-CE300 | 1.8307 | 0 | 75 | -1.7556e-06 |  | -29
CE410-CE300 | 1.8307 | 0 | 0 |  |  | 1
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0
CE430-CE300 | 0 | 0 | 0 | -1.0004e-10 |  | 0
CE440-CE300 | 0 | 0 | 0 | 0 |  | -87
CE500-CE300 | -1459.5539 | -1133 | -1177 | -1501.1724 | -1755 | -1274
CE510-CE500 | 1038.4136 | 1159 | 1162 | 1011.1162 | 1009 | 1070
CE525-CE520 | -1668.6417 | -1451 | -1483 | -1530.9547 | -1625 | -1099
CE530-CE500 | -2138.1546 | -2372 | -2370 | -2227.6394 | -2185 | -2185
CE545-CE540 | -1494.1291 | -1593 | -1593 | -914.6465 | -1495 | -1514
Delta Sensible Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | -183.1 | -123 | -86 | -254.3484 | -379 | -259
CE320-CE300 | 8038.2 | 7916 | 7867 | 8441.2775 | 7677 | 8059
CE330-CE300 | 9948.7 | 10207 | 11285 | 11233.9719 | 10540 | 10513
CE330-CE320 | 1910.5 | 2291 | 3418 | 2792.6945 | 2863 | 2454
CE340-CE300 | 9551.5 | 8883 | 8881 | 9356.9768 | 9483 | 9272
CE330-CE340 | 397.2 | 1324 | 2404 | 1876.9952 | 1057 | 1241
CE350-CE300 | 0.1 | 0 | 0 | -0.00037974 | 0 | -32
CE360-CE300 | 8783.3 | 8908 | 8860 | 9090.1056 | 8524 | 9271
CE400-CE300 | 0.1 | 0 | 0 | -7.3683e-06 |  | -31
CE410-CE300 | -11.7 | 0 | 0 |  |  | -15
CE420-CE300 | 0 | 0 | 0 | -2.9104e-11 |  | -15
CE430-CE300 | 0 | 0 | 0 | -4.1473e-10 |  | -15
CE440-CE300 | 0 | 0 | 0 | -1.6371e-10 |  | -33
CE500-CE300 | -3728.2 | -3194 | -3197 | -3681.5174 | -4681 | -3090
CE510-CE500 | 2180 | 2504 | 2505 | 2441.0216 | 2345 | 2451
CE525-CE520 | 286.8 | -309 | -304 | -335.6215 | -210 | -717
CE530-CE500 | 284.9 | -433 | -433 | -210.5244 | 0 | -192
CE545-CE540 | 500.2 | -291 | -292 | -186.6119 | -35 | -302
Delta Latent Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 6271.3 | 5835 | 5876 | 6040.0162 | 5737 | 5685
CE320-CE300 | 13511.6 | 22193 | 22109 | 11960.6494 | 11322 | 11537
CE330-CE300 | 18189.5 | 17637 | 31415 | 16899.4932 | 17809 | 17096
CE330-CE320 | 4677.9 | -4556 | 9306 | 4938.8437 | 6487 | 5559
CE340-CE300 | 15212.6 | 21147 | 26617 | 13676.4198 | 13850 | 13402
CE330-CE340 | 2976.9 | -3510 | 4798 | 3223.0734 | 3959 | 3694
CE350-CE300 | 115.56 | -1 | -1 | 0.53144 | 380 | 1211
CE360-CE300 | -360.54 | 722 | 942 | -1714.5041 | -1516 | -1458
CE400-CE300 | 17439.6 | 16274 | 23002 | 16082.4601 |  | 16253
CE410-CE300 | 1503.2 | 0 | -3 |  |  | -15
CE420-CE300 | 115.34 | 0 | 0 | -5.6389e-11 |  | 2
CE430-CE300 | 0 | 1801 | 1707 | 838.9522 |  | 2
CE440-CE300 | 0 | 0 | -3 | -2.9104e-11 |  | -253
CE500-CE300 | -1670.24 | -1571 | -1661 | -2396.1014 | -2570 | -2630
CE510-CE500 | 927.1 | 990 | 990 | 1116.0715 | 1045 | 1112
CE525-CE520 | 123.37 | -122 | -122 | 248.8578 | 212 | -144
CE530-CE500 | -7965.46 | -7733 | -7733 | -7837.6616 | -7626 | -7726.1
CE545-CE540 | -627.186 | 0 | 0 | -1654.9514 | -841 | -1181
Delta Sensible+Latent Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 5153.95 | 5349 | 5578 | 4393.2239 | 4759 | 4919
CE320-CE300 | 8143.55 | 22412 | 22368 | 7031.9273 | 7402 | 7848
CE330-CE300 | 11317.95 | 12227 | 33117 | 10711.8252 | 11476 | 10343
CE330-CE320 | 3174.4 | -10185 | 10749 | 3679.898 | 4074 | 2495
CE340-CE300 | 9477.65 | 19418 | 28094 | 8595.018 | 8864 | 9060
CE330-CE340 | 1840.3 | -7191 | 5023 | 2116.8072 | 2612 | 1283
CE350-CE300 | -82.32 | 0 | -1 | 0.0093743 | 0 | 5
CE360-CE300 | 6683.11 | 9212 | 9564 | 5726.4726 | 5820 | 6379
CE400-CE300 | 9004.55 | 9142 | 18383 | 7994.8866 |  | 8702
CE410-CE300 | -82.32 | 0 | 0 |  |  | 1
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0
CE430-CE300 | 0 | 0 | 0 | -5.5297e-10 |  | 0
CE440-CE300 | 0 | 0 | 0 | -2.7649e-10 |  | -295
CE500-CE300 | -4688.54 | -3694 | -3749 | -5086.83 | -5935 | -4517
CE510-CE500 | 3107.54 | 3481 | 3482 | 3531.3254 | 3381 | 3542
CE525-CE520 | 410.17 | -412 | -412 | -76.1817 | 8 | -881
CE530-CE500 | -7651.41 | -8131 | -8131 | -8007.6599 | -7791 | -7929
CE545-CE540 | 500.2 | -291 | -292 | -186.6119 | -30 | -302
Delta Max COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | -0.025037 | 0.272 | 0.271 | 0.2477 | 0.25703 | 0.24
CE320-CE300 | 0 | 1.274 | 1.11 | 0.014298 | 0.072694 | 0.5
CE330-CE300 | 0 | 0.24 | 1.738 | 0.14626 | 0.25134 | 0.17
CE330-CE320 | 0 | -1.034 | 0.628 | 0.13196 | 0.17864 | -0.33
CE340-CE300 | 0 | 0.752 | 1.482 | 0.061376 | 0.14655 | 0.07
CE330-CE340 | 0 | -0.512 | 0.256 | 0.084885 | 0.10479 | 0.1
CE350-CE300 | 0 | 0.02 | 0.006 | 0.63002 | 0.061488 | 0
CE360-CE300 | 0.23263 | 0.559 | 0.57 | 0.53014 | 0.5614 | 0.56
CE400-CE300 | -0.091398 | 0.219 | 0.919 | 0.14625 |  | 0.17
CE410-CE300 | -0.28043 | 0.034 | -0.002 |  |  | -0.04
CE420-CE300 | -0.38705 | -0.062 | -0.098 | -0.10384 |  | 0.06
CE430-CE300 | -0.38705 | -0.064 | -0.098 | -0.13253 |  | 0.05
CE440-CE300 | -0.28486 | -0.095 | -0.098 | -0.12338 |  | -0.07
CE500-CE300 | 0.1068 | 3.498 | 1.444 | 0.27276 | 0.31401 | 0.26
CE510-CE500 | 0.4174 | 0 | 0 | 0.48669 | 0.50496 | 0.39
CE525-CE520 | 0.90402 | 1.429 | 1.379 | 0.76636 | 0.83633 | 0.56
CE530-CE500 | -0.26907 | -3.386 | -1.451 | -0.27296 | -0.34458 | -0.26
CE545-CE540 | 0.79448 | 0.819 | 0.973 | 0.47021 | 0.48982 | 0.48
Delta Min COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0.072169 | 0.052 | 0.05 | 0.11113 | 0.087015 | 0.06
CE320-CE300 | 0.032137 | 0.003 | 0.004 | 0.059984 | 0.028893 | 0.02
CE330-CE300 | 0.032137 | 0 | 0 | 0.062559 | 0.037696 | 0.03
CE330-CE320 | 0 | -0.003 | -0.004 | 0.0025756 | 0.0088028 | 0.01
CE340-CE300 | 0.032137 | 0 | 0 | 0.062559 | 0.037696 | 0.03
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300 | -0.0026372 | 0 | 0 | -4.2544e-07 | 0.00027963 | 0
CE360-CE300 | 0.032137 | 0.001 | 0 | 0.062561 | 0.037696 | 0.03
CE400-CE300 | -0.011155 | -0.064 | -0.066 | -3.9918e-07 |  | 0
CE410-CE300 | -0.0072339 | 0 | 0 |  |  | 0
CE420-CE300 | 0 | 0 | 0 | 0 |  | 0
CE430-CE300 | -0.021929 | -0.064 | -0.066 | 0 |  | 0
CE440-CE300 | -0.010585 | -0.064 | -0.066 | -4.885e-15 |  | 0
CE500-CE300 | -0.10787 | -0.105 | -0.149 | -0.076073 | -0.11916 | -0.1
CE510-CE500 | 0.20276 | 0.124 | 0 | 0.15983 | 0.21527 | 0.19
CE525-CE520 | 0.46939 | 0.476 | 0.42 | 0.40795 | 0.56074 | 0.43
CE530-CE500 | -0.18393 | -0.198 | -0.154 | -0.1735 | -0.19318 | -0.19
CE545-CE540 | 0.4795 | 0.459 | 0.46 | 0.27714 | 0.54916 | 0.44
Delta Max IDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0.8779 | 1.78 | 1.61 | 1.4722 | 1.57 | 1
CE320-CE300 | 6.1605 | 6.5 | 6.39 | 6.7065 | 7.27 | 5.46
CE330-CE300 | 6.0322 | 6.61 | 6.89 | 6.0662 | 6.85 | 5.11
CE330-CE320 | -0.1283 | 0.11 | 0.5 | -0.64028 | -0.42 | -0.35
CE340-CE300 | 6.1067 | 6.5 | 6.45 | 6.4953 | 7.1 | 5.39
CE330-CE340 | -0.0745 | 0.11 | 0.44 | -0.4291 | -0.25 | -0.28
CE350-CE300 | 8.3842 | 9.83 | 9.83 | 9.9997 | 9.95 | 8.81
CE360-CE300 | 7.5586 | 7.67 | 7.45 | 7.5081 | 7.95 | 6.94
CE400-CE300 | 0.9149 | 2.45 | 3.72 | 1.9074 |  | -0.15
CE410-CE300 | 0.6257 | 0 | 0 |  |  | 0
CE420-CE300 | 0 | 0 | 0 | -1.5401e-11 |  | 0.04
CE430-CE300 | 0.9993 | 0 | 0 | 0.00056794 |  | 0.26
CE440-CE300 | 0.8453 | 0 | 0 | 0.00049509 |  | 0.07
CE500-CE300 | -0.3945 | 0 | 0 | -0.0026447 | -0.03 | -1.19
CE510-CE500 | 0.2949 | 0 | 0 | -2.2958e-08 | 0 | 0
CE525-CE520 | 19.9568 | 18.95 | 19.12 | 19.999 | 19.02 | 16.38
CE530-CE500 | 0.3106 | -0.05 | -0.05 | 0.00043309 | 0 | 0
CE545-CE540 | 19.525 | 19.89 | 19.89 | 19.9995 | 19.95 | 20
Delta Min IDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0 | 0 | 0 | -0.00012889 | 0 | 0
CE320-CE300 | 0 | 1.94 | 1.95 | -0.9638 | 0 | 0
CE330-CE300 | 0 | 0 | 0 | -0.0015681 | 0 | 0
CE330-CE320 | 0 | -1.94 | -1.95 | 0.96224 | 0 | 0
CE340-CE300 | 0 | 0 | 0 | -0.0015681 | 0 | 0
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300 | 0 | 0 | 0 | 0.00017983 | 0 | 0
CE400-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0
CE410-CE300 | 0 | 0 | 0 |  |  | 0
CE420-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0
CE430-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0
CE440-CE300 | 0 | 0 | 0 | -3.0198e-14 |  | 0.01
CE500-CE300 | 0.49703 | -0.72 | -0.89 | 0.22125 | 0.54 | 17.05
CE510-CE500 | 0 | 0 | 0 | 1.2601e-08 | 0 | 0
CE525-CE520 | 0.13889 | 0.06 | 0.05 | 0.17974 | 0.03 | 19.44
CE530-CE500 | -0.00551 | 0 | 0 | -0.00068516 | 0 | 0
CE545-CE540 | 0.22078 | 0.06 | 0.05 | 0.18049 | 0.03 | 18.06
Delta Max Humidity Ratio (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0.0024658 | 0.005 | 0.0052 | 0.0020112 | 0.001975 | 0.0023
CE320-CE300 | 0.0047326 | 0.0039 | 0.0039 | 0.0041811 | 0.00409 | 0.0043
CE330-CE300 | 0.0043671 | 0.004 | 0.004 | 0.0043074 | 0.003588 | 0.0043
CE330-CE320 | -0.0003655 | 0.0001 | 0.0001 | 0.00012627 | -0.000502 | 0
CE340-CE300 | 0.0045871 | 0.0039 | 0.0037 | 0.0041608 | 0.003815 | 0.0043
CE330-CE340 | -0.00022 | 0.0001 | 0.0003 | 0.00014662 | -0.000227 | 0
CE350-CE300 | 0.0034739 | 0.0061 | 0.0062 | 0.0035636 | 0.003022 | 0.0032
CE360-CE300 | 0.0001491 | 0 | 0 | 0.00023399 | 0 | 0
CE400-CE300 | 0.0036593 | 0.0032 | 0.0033 | 0.00325 |  | 0.0039
CE410-CE300 | 0.0035512 | 0.0031 | 0.0032 |  |  | 0.0039
CE420-CE300 | 0.0010125 | 0.0009 | 0.0004 | 0.00096639 |  | 0.0013
CE430-CE300 | 0.0029463 | 0.0018 | 0.0019 | 0.0025083 |  | 0.0024
CE440-CE300 | 2.85e-05 | 0 | 0 | 1.3697e-12 |  | 0
CE500-CE300 | -0.0015646 | -0.0019 | -0.0019 | -0.0019411 | -0.001744 | -0.0019
CE510-CE500 | 0.0001517 | 0 | 0.0001 | 3.4061e-06 | 3e-06 | 0
CE525-CE520 | 0.010392 | 0.0103 | 0.0102 | 0.011462 | 0.01006 | 0.0067
CE530-CE500 | -0.0047305 | -0.0038 | -0.0037 | -0.0049096 | -0.006222 | -0.00473
CE545-CE540 | 0.0009051 | 0.0072 | 0.0059 | 1.8956e-13 | 0.003433 | 0.00129
Delta Min Humidity Ratio (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 1e-08 | 0 | 0 | 1.5608e-05 | 5.1e-05 | -1e-05
CE320-CE300 | 0 | 0 | 0 | 5.8672e-06 | 0 | 0
CE330-CE300 | 0 | 0 | 0 | -1.7036e-08 | 0 | 0
CE330-CE320 | 0 | 0 | 0 | -5.8842e-06 | 0 | 0
CE340-CE300 | 0 | 0 | 0 | -1.7036e-08 | 0 | 0
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300 | 0 | 0 | 0 | -2.2318e-11 | 0 | 0
CE400-CE300 | 0 | 0 | 0 | 2.2054e-12 |  | 0
CE410-CE300 | 0 | 0 | 0 |  |  | 0
CE420-CE300 | 0 | 0 | 0 | -1.2812e-12 |  | 0
CE430-CE300 | 0 | 0 | 0 | 2.2054e-12 |  | 0
CE440-CE300 | 0 | 0 | 0 | -1.7443e-12 |  | 0
CE500-CE300 | 0.0049507 |  |  | 0.0050771 | 0.00494 | 0.00833
CE510-CE500 | 0 |  |  | 6.179e-12 | 0 | 0.0002
CE525-CE520 | 0.00073266 |  |  | 0.00052082 | 0.000384 | 0.00883
CE530-CE500 | -0.00061959 |  |  | -0.00027005 | -0.001454 | -0.00367
CE545-CE540 | 0.0020983 |  |  | 0.002957 | 0.003432 | 0.0028
Delta Max Relative Humidity (%)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 8.9137 | 30.83 | 31.85 | 10.2766 | 9 | 10.75
CE320-CE300 | 13.0466 | 14.06 | 14.82 | 14.5993 | 15 | 14.44
CE330-CE300 | 7.8699 | 9.11 | 9.09 | 8.5081 | 8 | 11.26
CE330-CE320 | -5.1767 | -4.95 | -5.73 | -6.0911 | -7 | -3.18
CE340-CE300 | 11.1401 | 12.02 | 12.41 | 12.4287 | 12 | 12.81
CE330-CE340 | -3.2702 | -2.91 | -3.32 | -3.9205 | -4 | -1.55
CE350-CE300 | 0 | 11.77 | 12.27 | 4.9738e-13 | 2 | 5.21
CE360-CE300 | 0 | 0 | 0 | -0.00016648 | 0 | 0
CE400-CE300 | 14.9642 | 16.22 | 16.72 | 16.269 |  | 18.87
CE410-CE300 | 14.4355 | 15.44 | 15.94 |  |  | 18.74
CE420-CE300 | 2.0519 | 5.16 | 2.68 | 4.9167 |  | 6.41
CE430-CE300 | 11.9195 | 9.08 | 9.58 | 12.3754 |  | 11.5
CE440-CE300 | -0.065 | 0 | 0 | 6.6574e-09 |  | 0.07
CE500-CE300 | 31.2108 |  |  | 31.6327 | 32 | -7.36
CE510-CE500 | 0 |  |  | 0 | 0 | -2.57
CE525-CE520 | 9.7701 |  |  | 6.1863 | 5 | -20.65
CE530-CE500 | -8.9555 |  |  | -3.8398 | -21 | -24.07
CE545-CE540 | 29.6022 |  |  | 41.0554 | 50 | -15.82
Delta Min Relative Humidity (%)
| TRNSYS | DOE21E-J | DOE21E-E | EnergyPlus | CODY | HOT3000 | Tested Prg | Extra | Extra
CE310-CE300 | 0.0586 | 0 | 0 | 1.1 | 1 | 0.99
CE320-CE300 | 0 | 0 | 0 | 0.23921 | 0 | -2.02
CE330-CE300 | 0 | 0 | 0 | 0.00010511 | 0 | 0
CE330-CE320 | 0 | 0 | 0 | -0.23911 | 0 | 2.02
CE340-CE300 | 0 | 0 | 0 | 0.00010511 | 0 | 0
CE330-CE340 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300 | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300 | 0 | 0 | 0 | -5.7187e-05 | 0 | 0
CE400-CE300 | -0.1222 | 0 | 0 | -0.47678 |  | -0.37
CE410-CE300 | -0.1221 | 0 | 0 |  |  | -0.36
CE420-CE300 | -0.1213 | 0 | 0 | -0.47665 |  | -0.35
CE430-CE300 | -0.1234 | 0 | 0 | -0.47678 |  | -0.36
CE440-CE300 | -0.1243 | 0 | 0 | -0.47678 |  | -0.4
CE500-CE300 | 40.0742 |  |  | 40.7644 | 39 | 37.89
CE510-CE500 | -1.3175 |  |  | 0.12165 | 0 | 0.32
CE525-CE520 | -15.7395 |  |  | -13.8748 | -17 | -17.5
CE530-CE500 | -23.812 |  |  | -21.139 | -26 | -19.15
CE545-CE540 | -19.3505 |  |  | -16.7748 | -12 | -19.6

## Qdata
0 | ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
0 | Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
0 | 0
0 | Table B16.5.2-1. Annual Space Cooling Electricity Consumption (Total, Compressor)
0 | Energy Consumption, Total (kWh,e)
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg |  |  |  | For QtotINIT plot (results before BESTESTing); results imported from various files as appropriate for first runs of software and specific cases.
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg | (max-min)/mean |  |  |  | TRNSYS TUD | DOE21E-J NREL | DOE21E-E NREL | EnergyPlus GARD | CODYRUN UR | HOT3000 NRCan | N/A | (max-min)/mean
0 | CE300 Base, 15% OA | 35633.7773 | 34750 | 34755 | 34745.6375 | 34976.411 | 35070 |  |  |  |  | CE300 Base, 15% OA | 35633.7773 | 34608 | 37908 | 35149 | 31988 | 35029 |  | 0.16889
0 | CE310, High Latent | 39973.3798 | 39379 | 39384 | 39290.3641 | 39519.569 | 39608 |  |  |  |  | CE310, High Latent | 39973.3798 | 39268 | 43821 | 39999 | 35628 | 39626 |  | 0.20627
0 | CE320, High Infiltration | 40059.657 | 38745 | 38792 | 39079.1002 | 39400.815 | 39457 |  |  |  |  | CE320, High Infiltration | 38897 | 38692 | 41626 | 39274 | 43434 | 38575 |  | 0.12122
0 | CE330, 100% OA | 40963.3004 | 39708 | 39438 | 40143.3736 | 40535.137 | 40330 |  |  |  |  | CE330, 100% OA | 40963.3004 | 39445 | 43103 | 40373 | 44484 | 38770 |  | 0.13872
0 | CE340, 50% OA, 50% Infl | 40619.2951 | 39358 | 39265 | 39783.0185 | 40065.261 | 39947 |  |  |  |  | CE340, 50% OA, 50% Infl | 39665 | 39181 | 42648 | 39997 | 44077 | 39373 |  | 0.11993
0 | CE350, Tstat Set Up | 32236.9795 | 30547 | 30548 | 31145.1136 | 31586.592 | 31742 |  |  |  |  | CE350, Tstat Set Up | 32236.9795 | 30394 | 33326 | 31447 | 31862 | 31627 |  | 0.092156
0 | CE360, Undersized System | 55298.7917 | 54064 | 54016 | 54704.711 | 54843.258 | 55068 |  |  |  |  | CE360, Undersized System | 55298.7917 | 53819 | 55028 | 55351 | 54306 | 54924 |  | 0.027962
0 | CE400, Ec. Temp. Ctrl. | 32045.1536 | 30846 | 30876 | 31012.681 | 0 | 31413 |  |  |  |  | CE400, Ec. Temp. Ctrl. | 32045.1536 | 30784 | 37594 | 34331 |  | 31413 |  | 0.20491
0 | CE410, Ec. Comp. Lockout | 32078.4319 | 31668 | 31699 | 0 | 0 | 31503 |  |  |  |  | CE410, Ec. Comp. Lockout | 32078.4319 | 31632 | 33629 | 34331 |  | 31503 |  | 0.086656
0 | CE420, Ec. ODB Limit | 33387.0076 | 32530 | 32910 | 32735.5046 | 0 | 33208 |  |  |  |  | CE420, Ec. ODB Limit | 33387.0076 | 32787 | 35245 | 34331 |  | 33208 |  | 0.07274
0 | CE430, Ec. Enthalpy Ctrl. | 32538.0313 | 31932 | 31811 | 31772.397 | 0 | 31818 |  |  |  |  | CE430, Ec. Enthalpy Ctrl. | 32538.0313 | 31754 | 35630 | 34035 |  | 31818 |  | 0.11691
0 | CE440, Ec. Enthalpy Limit | 33691.321 | 33032 | 32973 | 33031.6453 | 0 | 33248 |  |  |  |  | CE440, Ec. Enthalpy Limit | 32041.3688 | 32892 | 35905 | 34035 |  | 33248 |  | 0.11491
0 | CE500, Base w/ 0%OA | 22337.887 | 22817 | 22822 | 23034.6081 | 22322.953 | 23138 |  |  |  |  | CE500, Base w/ 0%OA | 22337.887 | 22802 | 22808 | 23055 | 22438 | 23138 |  | 0.035149
0 | CE500 May-Sep | 17390.8511 | 17872 | 17870 | 17996.1112 | 17434.537 | 18051 |  |  |  |  | CE500 May-Sep | 17390.8511 | 17854 | 17854 | 18006 | 17459 | 18051 |  | 0.037151
0 | CE510 May-Sep, High PLR | 34608.7754 | 35971 | 35970 | 35732.4838 | 34848.637 | 35845 |  |  |  |  | CE510 May-Sep, High PLR | 34608.7754 | 35955 | 35954 | 35720 | 34908 | 35845 |  | 0.037923
0 | CE520, EDB = 15°C | 24986.582 | 25389 | 25390 | 25017.1776 | 25131.07 | 25781 |  |  |  |  | CE520, EDB = 15°C | 24986.582 | 26043 | 27201 | 24051 | 25161 | 25781 |  | 0.12335
0 | CE522, EDB = 20°C | 23544.1607 | 24293 | 24307 | 24077.7247 | 23619.744 | 24360 |  |  |  |  | CE522, EDB = 20°C | 23544.1607 | 24424 | 24462 | 24027 | 23741 | 24360 |  | 0.038096
0 | CE525, EDB = 35°C | 20320.874 | 20408 | 20421 | 20701.5603 | 20241.713 | 21323 |  |  |  |  | CE525, EDB = 35°C | 20320.874 | 20077 | 20074 | 20718 | 20303 | 21323 |  | 0.061018
0 | CE530, Dry Coil | 17281.271 | 17540 | 17537 | 17741.9432 | 17442.468 | 17875 |  |  |  |  | CE530, Dry Coil | 17281.271 | 17558 | 17548 | 17738 | 17447 | 17875 |  | 0.033783
0 | CE540, Dry, EDB = 15°C | 19430.3785 | 19878 | 19874 | 19061.1125 | 19536.572 | 20164 |  |  |  |  | CE540, Dry, EDB = 15°C | 19430.3785 | 20145 | 21685 | 17789 | 19566 | 20164 |  | 0.1968
0 | CE545, Dry, EDB = 35°C | 15687.0796 | 15802 | 15791 | 16635.7259 | 15791.081 | 16339 |  |  |  |  | CE545, Dry, EDB = 35°C | 15687.0796 | 15741 | 15740 | 16643 | 15781 | 16339 |  | 0.059788
| Energy Consumption, Compressor (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
| Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
| CE300 Base, 15% OA | 22353.5343 | 21569 | 21573 | 0 | 21770.001 | 21876
| CE310, High Latent | 26339.6254 | 25813 | 25817 | 0 | 25936.821 | 26053
| CE320, High Infiltration | 26433.1374 | 25250 | 25294 | 0 | 25846.026 | 25912
| CE330, 100% OA | 27299.7321 | 26172 | 25925 | 0 | 26927.733 | 26775
| CE340, 50% OA, 50% Infl | 26962.9373 | 25829 | 25745 | 0 | 26472.79 | 26400
| CE350, Tstat Set Up | 19316.8404 | 17802 | 17801 | 0 | 18738.055 | 18891
| CE360, Undersized System | 40105.8399 | 38999 | 38955 | 0 | 39697.162 | 39941
| CE400, Ec. Temp. Ctrl. | 19178.9487 | 18106 | 18131 | 0 | 0 | 18629
| CE410, Ec. Comp. Lockout | 19204.4944 | 18823 | 18850 | 0 | 0 | 18685
| CE420, Ec. ODB Limit | 20358.5854 | 19596 | 19934 | 0 | 0 | 20214
| CE430, Ec. Enthalpy Ctrl. | 19598.6211 | 19059 | 18951 | 0 | 0 | 18966
| CE440, Ec. Enthalpy Limit | 20629.1333 | 20042 | 19989 | 0 | 0 | 20249
| CE500, Base w/ 0%OA | 17854.2956 | 18473 | 18478 | 0 | 17857.852 | 18522
| CE500 May-Sep | 13942.1479 | 14508 | 14506 | 0 | 13988.512 | 14491
| CE510 May-Sep, High PLR | 27747.879 | 28811 | 28810 | 0 | 27901.957 | 28721
| CE520, EDB = 15°C | 19521.2767 | 20121 | 20126 | 0 | 19654.972 | 20185
| CE522, EDB = 20°C | 18620.3108 | 19407 | 19418 | 0 | 18689.799 | 19281
| CE525, EDB = 35°C | 16557.8748 | 16880 | 16893 | 0 | 16506.802 | 17443
| CE530, Dry Coil | 13656.9951 | 14127 | 14124 | 0 | 13855.928 | 14172
| CE540, Dry, EDB = 15°C | 15020.7433 | 15680 | 15677 | 0 | 15163.82 | 15664
| CE545, Dry, EDB = 35°C | 12621.8685 | 12967 | 12957 | 0 | 12750.623 | 13215
| Energy Consumption, Supply Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
| Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
| CE300 Base, 15% OA | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
| CE310, High Latent | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
| CE320, High Infiltration | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
| CE330, 100% OA | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
| CE340, 50% OA, 50% Infl | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
| CE350, Tstat Set Up | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
| CE360, Undersized System | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880
| CE400, Ec. Temp. Ctrl. | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880
| CE410, Ec. Comp. Lockout | 10879.92 | 10880 | 10880 | 0 | 0 | 10880
| CE420, Ec. ODB Limit | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880
| CE430, Ec. Enthalpy Ctrl. | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880
| CE440, Ec. Enthalpy Limit | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880
| CE500, Base w/ 0%OA | 2563.8216 | 2369 | 2369 | 2628.3265 | 2553.232 | 2639
| CE500 May-Sep | 1972.0485 | 1837 | 1837 | 2028.9634 | 1970.497 | 2035
| CE510 May-Sep, High PLR | 3923.2198 | 4099 | 4099 | 4063.3025 | 3972.28 | 4073
| CE520, EDB = 15°C | 3125.1884 | 2874 | 2871 | 3018.6693 | 3131.271 | 3200
| CE522, EDB = 20°C | 2815.5716 | 2704 | 2707 | 2842.5564 | 2819.112 | 2904
| CE525, EDB = 35°C | 2151.7702 | 1886 | 1885 | 2179.8959 | 2135.708 | 2221
| CE530, Dry Coil | 2072.4451 | 1833 | 1833 | 2090.2174 | 2050.856 | 2117
0 | CE540, Dry, EDB = 15°C | 2521.5317 | 2258 | 2258 | 2309.2457 | 2500.416 | 2573
0 | CE545, Dry, EDB = 35°C | 1752.7588 | 1501 | 1501 | 1870.9023 | 1738.667 | 1786
0 | Energy Consumption, Condenser Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 2400.3229 | 2301 | 2302 | 0 | 2326.49 | 2323
0 | CE310, High Latent | 2753.8345 | 2686 | 2687 | 0 | 2702.828 | 2691
0 | CE320, High Infiltration | 2746.5996 | 2615 | 2618 | 0 | 2674.869 | 2681
0 | CE330, 100% OA | 2783.6483 | 2656 | 2633 | 0 | 2727.484 | 2693
0 | CE340, 50% OA, 50% Infl | 2776.4378 | 2649 | 2640 | 0 | 2712.551 | 2684
0 | CE350, Tstat Set Up | 2040.2191 | 1865 | 1867 | 0 | 1968.617 | 1970
0 | CE360, Undersized System | 4313.0318 | 4185 | 4181 | 0 | 4266.176 | 4272
0 | CE400, Ec. Temp. Ctrl. | 1986.2848 | 1860 | 1865 | 0 | 0 | 1902
0 | CE410, Ec. Comp. Lockout | 1994.0175 | 1965 | 1969 | 0 | 0 | 1936
0 | CE420, Ec. ODB Limit | 2148.5022 | 2054 | 2096 | 0 | 0 | 2115
0 | CE430, Ec. Enthalpy Ctrl. | 2059.4903 | 1993 | 1980 | 0 | 0 | 1970
0 | CE440, Ec. Enthalpy Limit | 2182.2678 | 2110 | 2104 | 0 | 0 | 2120
0 | CE500, Base w/ 0%OA | 1919.7698 | 1975 | 1975 | 0 | 1911.869 | 1976
0 | CE500 May-Sep | 1476.6547 | 1527 | 1527 | 0 | 1475.528 | 1524
0 | CE510 May-Sep, High PLR | 2937.6766 | 3061 | 3061 | 0 | 2974.4 | 3050
0 | CE520, EDB = 15°C | 2340.1169 | 2394 | 2393 | 0 | 2344.827 | 2396
0 | CE522, EDB = 20°C | 2108.2783 | 2182 | 2182 | 0 | 2110.833 | 2174
0 | CE525, EDB = 35°C | 1611.2289 | 1642 | 1643 | 0 | 1599.203 | 1663
0 | CE530, Dry Coil | 1551.8309 | 1580 | 1580 | 0 | 1535.684 | 1585
| CE540, Dry, EDB = 15°C | 1888.1035 | 1940 | 1939 | 0 | 1872.336 | 1926
| CE545, Dry, EDB = 35°C | 1312.4522 | 1334 | 1333 | 0 | 1301.791 | 1337
0
0 | Table B16.5.2-3. Weather Data Checks, CE300 Only | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Variable | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | Annual Mean Output | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | ODB (°C) | 19.9145 | 19.8889 | 19.8889 | 19.9141 | 19.9145 | 19.91
0 | OHR (kg/kg) | 0.011643 | 0.0116 | 0.0116 | 0.011593 | 0.011649 | 0.0116
0 | Annual Hourly Integrated Maxima | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | ODB (°C) | 34.7 | 35 | 35 | 34.775 | 35 | 35
0 | OHR (kg/kg) | 0.021878 | 0.0225 | 0.0225 | 0.021842 | 0.022406 | 0.0223
0
#REF!
#REF!
#REF!
#REF!
#REF!
0 | Table B16.5.2-4. Annual Space Cooling Coil Loads ( Total, Sensible ) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Total Sensible + Latent (kWh,thermal) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 80426.8675 | 77283.4356 | 77291.9355 | 77317.9497 | 77744.589 | 78257
0 | CE310, High Latent | 99342.1316 | 97394.7852 | 97412.0781 | 96447.5904 | 97295.866 | 97261
0 | CE320, High Infiltration | 99791.678 | 96356.3319 | 96493.2096 | 96083.5597 | 97141.307 | 96957
0 | CE330, 100% OA | 105012.8715 | 100729.9701 | 100993.467 | 102211.3604 | 103712.915 | 102008
0 | CE340, 50% OA, 50% Infl | 102727.9789 | 99027.6453 | 99223.143 | 99708.5156 | 100676.21 | 99753
0 | CE350, Tstat Set Up | 69387.9976 | 63736.3536 | 63634.6479 | 65790.3681 | 66860.163 | 67389
0 | CE360, Undersized System | 162974.0626 | 159807.2061 | 159853.809 | 161248.445 | 161200.179 | 162168
0 | CE400, Ec. Temp. Ctrl. | 68792.8221 | 64917.5466 | 65025.1143 | 65413.8414 | 0 | 66898
0 | CE410, Ec. Comp. Lockout | 68672.8538 | 66779.6109 | 66843.5067 | 0 | 0 | 66175
0 | CE420, Ec. ODB Limit | 72609.3074 | 69610.9569 | 70882.1316 | 70349.4668 | 0 | 71803
0 | CE430, Ec. Enthalpy Ctrl. | 69756.312 | 67640.7387 | 67219.2609 | 67141.3524 | 0 | 67200
0 | CE440, Ec. Enthalpy Limit | 73711.3635 | 71380.1085 | 71181.0936 | 71417.307 | 0 | 72029
0 | CE500, Base w/ 0%OA | 63357.1063 | 65995.8615 | 65992.3443 | 65571.1832 | 63105.366 | 65614
0 | CE500 May-Sep | 48443.4308 | 50692.8174 | 50690.4726 | 50354.2901 | 48439.57 | 50357
0 | CE510 May-Sep, High PLR | 108974.3099 | 114017.9517 | 114015.3138 | 112792.6463 | 108979.013 | 112781
0 | CE520, EDB = 15°C | 63421.5444 | 66571.2168 | 66565.3548 | 66087.7865 | 63212.102 | 66146
0 | CE522, EDB = 20°C | 63389.2228 | 66373.0812 | 66371.9088 | 65850.6755 | 63157.03 | 65900
0 | CE525, EDB = 35°C | 63292.9454 | 65399.1099 | 65395.0065 | 64973.3114 | 63001.558 | 65155
0 | CE530, Dry Coil | 45045.848 | 46634.2617 | 46630.7445 | 46944.3571 | 44875.414 | 47002
0 | CE540, Dry, EDB = 15°C | 45112.827 | 47129.8938 | 47126.0835 | 47296.6053 | 44979.842 | 47462
0 | CE545, Dry, EDB = 35°C | 44981.3517 | 46239.7491 | 46235.9388 | 46611.8912 | 44775.11 | 46668
0 | Sensible Coil Load (kWh,thermal) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 56661.7484 | 55796.8608 | 55804.7745 | 55251.9574 | 55209.465 | 55191
0 | CE310, High Latent | 56256.3775 | 56300.9928 | 56312.7168 | 55225.158 | 55185.072 | 55083
0 | CE320, High Infiltration | 62859.2053 | 62697.021 | 62746.848 | 62043.4531 | 62008.804 | 62734
0 | CE330, 100% OA | 63083.3765 | 63311.0655 | 63327.7722 | 63778.6556 | 62649.459 | 61822
0 | CE340, 50% OA, 50% Infl | 63032.6061 | 63053.4306 | 63110.5851 | 62885.8356 | 62380.56 | 61406
0 | CE350, Tstat Set Up | 50370.8304 | 47684.439 | 47676.5253 | 48545.0123 | 48588.802 | 48768
0 | CE360, Undersized System | 134976.8351 | 134919.792 | 134939.7228 | 135287.1959 | 134205.707 | 134697
0 | CE400, Ec. Temp. Ctrl. | 41952.3595 | 41419.1334 | 41437.0125 | 40687.7468 | 0 | 41181
0 | CE410, Ec. Comp. Lockout | 45676.6456 | 47658.6462 | 47659.8186 | 0 | 0 | 45585
0 | CE420, Ec. ODB Limit | 50389.8247 | 49666.0881 | 50612.2149 | 49523.9279 | 0 | 49984
0 | CE430, Ec. Enthalpy Ctrl. | 47863.3462 | 47731.335 | 47454.0624 | 46738.5816 | 0 | 46143
0 | CE440, Ec. Enthalpy Limit | 50876.0725 | 50592.5772 | 50492.0439 | 50060.1752 | 0 | 49785
0 | CE500, Base w/ 0%OA | 45043.8 | 47649.8532 | 47646.0429 | 47491.2402 | 44874.225 | 47530
0 | CE500 May-Sep | 34443.2344 | 36595.5867 | 36593.2419 | 36475.5877 | 34448.151 | 36480
0 | CE510 May-Sep, High PLR | 77489.4321 | 82305.7041 | 82303.0662 | 81566.3401 | 77498.985 | 81563
0 | CE520, EDB = 15°C | 45109.6141 | 48101.5203 | 48095.6583 | 47986.359 | 44976.724 | 48059
0 | CE522, EDB = 20°C | 45076.0312 | 47962.2978 | 47961.4185 | 47757.6997 | 44924.113 | 47795
0 | CE525, EDB = 35°C | 44979.0103 | 47217.5307 | 47213.4273 | 46929.7377 | 44775.105 | 47110
0 | CE530, Dry Coil | 45045.848 | 46573.59 | 46570.0728 | 46944.356 | 44874.225 | 47002
0 | CE540, Dry, EDB = 15°C | 45111.8473 | 47022.9123 | 47019.102 | 47288.0472 | 44976.747 | 47460
0 | CE545, Dry, EDB = 35°C | 44981.3517 | 46214.2494 | 46210.4391 | 46611.8912 | 44775.105 | 46668
0 | Latent Coil Load(kWh,thermal) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 23765.119 | 21486.5748 | 21487.161 | 22065.9923 | 22535.143 | 23067
0 | CE310, High Latent | 43085.7541 | 41093.7924 | 41099.3613 | 41222.4325 | 42110.836 | 42178
0 | CE320, High Infiltration | 36932.4726 | 33659.3109 | 33746.3616 | 34040.1066 | 35132.592 | 34224
0 | CE330, 100% OA | 41929.495 | 37418.9046 | 37665.6948 | 38432.7048 | 41063.373 | 40186
0 | CE340, 50% OA, 50% Infl | 39695.3729 | 35974.2147 | 36112.5579 | 36822.6801 | 38295.624 | 38346
0 | CE350, Tstat Set Up | 19017.1672 | 16051.9146 | 15958.1226 | 17245.3558 | 18271.394 | 18621
0 | CE360, Undersized System | 27997.2274 | 24887.4141 | 24914.0862 | 25961.249 | 26994.482 | 27470
0 | CE400, Ec. Temp. Ctrl. | 26840.4626 | 23498.4132 | 23588.1018 | 24726.0946 | 0 | 25717
0 | CE410, Ec. Comp. Lockout | 22996.2083 | 19120.9647 | 19183.6881 | 0 | 0 | 20590
0 | CE420, Ec. ODB Limit | 22219.4827 | 19944.8688 | 20269.9167 | 20825.5388 | 0 | 21855
0 | CE430, Ec. Enthalpy Ctrl. | 21892.9657 | 19909.4037 | 19765.1985 | 20402.7708 | 0 | 21057
0 | CE440, Ec. Enthalpy Limit | 22835.291 | 20787.5313 | 20689.0497 | 21357.1318 | 0 | 22244
0 | CE500, Base w/ 0%OA | 18313.3062 | 18346.0083 | 18346.3014 | 18079.943 | 18231.141 | 18084
0 | CE500 May-Sep | 14000.1964 | 14097.2307 | 14097.2307 | 13878.7023 | 13991.418 | 13877
0 | CE510 May-Sep, High PLR | 31484.8778 | 31712.2476 | 31712.2476 | 31226.3062 | 31479.856 | 31217
0 | CE520, EDB = 15°C | 18311.9303 | 18469.6965 | 18469.6965 | 18101.4275 | 18235.133 | 18087
0 | CE522, EDB = 20°C | 18313.1916 | 18410.7834 | 18410.4903 | 18092.9758 | 18233.151 | 18104
0 | CE525, EDB = 35°C | 18313.9351 | 18181.5792 | 18181.5792 | 18043.5737 | 18226.509 | 18045
0 | CE530, Dry Coil | 0 | 60.6717 | 60.6717 | 0.0011462 | 1.186 | 0
0 | CE540, Dry, EDB = 15°C | 0.97976 | 106.9815 | 106.9815 | 8.5582 | 3.09 | 2
0 | CE545, Dry, EDB = 35°C | 0 | 25.4997 | 25.4997 | 3.4549e-12 | 0.004 | 0
0 | * ABS[ (Max-Min) / (Mean of Example Simulation Results) ] | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0 | Table B16.5.2-7. Various Annual Means (Humidity Ratio, Zone Relative Humidity) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 3.2491 | 3.2377 | 3.2374 | 3.2373 | 3.2264 | 3.23
0 | CE310, High Latent | 3.4146 | 3.4175 | 3.4175 | 3.3927 | 3.3972 | 3.38
0 | CE320, High Infiltration | 3.4199 | 3.458 | 3.4571 | 3.4052 | 3.406 | 3.39
0 | CE330, 100% OA | 3.4907 | 3.4942 | 3.5364 | 3.4907 | 3.4973 | 3.46
0 | CE340, 50% OA, 50% Infl | 3.4543 | 3.4773 | 3.4956 | 3.4476 | 3.4495 | 3.42
0 | CE350, Tstat Set Up | 3.2489 | 3.2408 | 3.2354 | 3.2436 | 3.2289 | 3.23
0 | CE360, Undersized System | 3.669 | 3.7006 | 3.7058 | 3.6779 | 3.6667 | 3.66
0 | CE400, Ec. Temp. Ctrl. | 3.2503 | 3.2514 | 3.2519 | 3.2462 | 0 | 3.26
0 | CE410, Ec. Comp. Lockout | 3.2395 | 3.2124 | 3.2107 | 0 | 0 | 3.21
0 | CE420, Ec. ODB Limit | 3.2261 | 3.2153 | 3.2175 | 3.2162 | 0 | 3.21
0 | CE430, Ec. Enthalpy Ctrl. | 3.2208 | 3.213 | 3.2115 | 3.2109 | 0 | 3.21
0 | CE440, Ec. Enthalpy Limit | 3.2313 | 3.2223 | 3.2219 | 3.2214 | 0 | 3.22
0 | CE500, Base w/ 0%OA | 3.2041 | 3.2275 | 3.2265 | 3.2133 | 3.192 | 3.2
0 | CE500 May-Sep | 3.1418 | 3.1614 | 3.1616 | 3.1536 | 3.1324 | 3.14
0 | CE510 May-Sep, High PLR | 3.5513 | 3.5774 | 3.5774 | 3.5616 | 3.5295 | 3.55
0 | CE520, EDB = 15°C | 2.9011 | 2.9567 | 2.956 | 3.0042 | 2.8733 | 2.92
0 | CE522, EDB = 20°C | 3.0581 | 3.0744 | 3.0728 | 3.101 | 3.0363 | 3.07
0 | CE525, EDB = 35°C | 3.4835 | 3.5309 | 3.528 | 3.508 | 3.4796 | 3.41
0 | CE530, Dry Coil | 2.9618 | 2.969 | 2.9694 | 2.9993 | 2.9156 | 2.98
0 | CE540, Dry, EDB = 15°C | 2.668 | 2.6748 | 2.6752 | 2.8234 | 2.6403 | 2.69
0 | CE545, Dry, EDB = 35°C | 3.2281 | 3.2333 | 3.2355 | 3.157 | 3.1863 | 3.2
| IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
| Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
| CE300 Base, 15% OA | 23.6243 | 24.0556 | 24.0556 | 24.0907 | 24.0816 | 23.99
| CE310, High Latent | 23.7556 | 24.1111 | 24.0556 | 24.0921 | 24.0897 | 24.01
| CE320, High Infiltration | 23.9005 | 24.3889 | 24.3889 | 24.2544 | 24.3274 | 24.53
| CE330, 100% OA | 23.8797 | 24.2778 | 24.2778 | 24.2734 | 24.2955 | 24.18
| CE340, 50% OA, 50% Infl | 23.8756 | 24.2778 | 24.2778 | 24.2983 | 24.3089 | 24.21
| CE350, Tstat Set Up | 25.6595 | 26.1667 | 26.1667 | 26.2416 | 26.2686 | 26.15
| CE360, Undersized System | 25.3649 | 25.6111 | 25.5556 | 25.3232 | 25.4809 | 25.37
| CE400, Ec. Temp. Ctrl. | 24.1263 | 24.0556 | 24.0556 | 24.092 | 0 | 23.99
| CE410, Ec. Comp. Lockout | 24.1221 | 24.0556 | 24.0556 | 0 | 0 | 23.99
| CE420, Ec. ODB Limit | 23.9262 | 24.0556 | 24.0556 | 24.0906 | 0 | 23.99
| CE430, Ec. Enthalpy Ctrl. | 23.9916 | 24.0556 | 24.0556 | 24.0906 | 0 | 23.99
| CE440, Ec. Enthalpy Limit | 23.9118 | 24.0556 | 24.0556 | 24.0907 | 0 | 23.99
| CE500, Base w/ 0%OA | 20.2342 | 20.6667 | 20.5556 | 20.3795 | 21.0978 | 22.86
| CE500 May-Sep | 24.5723 | 25 | 25 | 24.9823 | 25 | 25
| CE510 May-Sep, High PLR | 25.8168 | 25.1111 | 25.1111 | 24.9596 | 25 | 25
| CE520, EDB = 15°C | 13.5171 | 13.7778 | 13.7222 | 13.5769 | 14.1421 | 14.89
| CE522, EDB = 20°C | 16.9456 | 17.2778 | 17.2222 | 16.9966 | 17.729 | 18.7
| CE525, EDB = 35°C | 26.8443 | 27.3889 | 27.2778 | 27.1041 | 27.7709 | 30.69
| CE530, Dry Coil | 20.0253 | 20.6111 | 20.5556 | 20.586 | 21.0978 | 22.86
| CE540, Dry, EDB = 15°C | 13.2893 | 13.7778 | 13.7222 | 13.7934 | 14.1406 | 14.98
| CE545, Dry, EDB = 35°C | 26.6052 | 27.3333 | 27.2778 | 27.3123 | 27.7166 | 30.69
| Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
| Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
| CE300 Base, 15% OA | 0.0090691 | 0.0092 | 0.0092 | 0.0092861 | 0.0091748 | 0.0092
| CE310, High Latent | 0.011071 | 0.0113 | 0.0113 | 0.011261 | 0.011175 | 0.0111
| CE320, High Infiltration | 0.009988 | 0.0101 | 0.0101 | 0.010114 | 0.010049 | 0.0099
| CE330, 100% OA | 0.0097409 | 0.0099 | 0.0099 | 0.0099684 | 0.0098116 | 0.0099
| CE340, 50% OA, 50% Infl | 0.0097914 | 0.0099 | 0.0099 | 0.0099837 | 0.0098683 | 0.0099
| CE350, Tstat Set Up | 0.0097059 | 0.01 | 0.01 | 0.0099257 | 0.0097585 | 0.00977
| CE360, Undersized System | 0.0084995 | 0.0087 | 0.0087 | 0.0087659 | 0.0085524 | 0.00858
| CE400, Ec. Temp. Ctrl. | 0.0098011 | 0.01 | 0.01 | 0.010087 | 0 | 0.01
| CE410, Ec. Comp. Lockout | 0.0097405 | 0.0095 | 0.0095 | 0 | 0 | 0.0095
| CE420, Ec. ODB Limit | 0.0092639 | 0.0094 | 0.0094 | 0.0094486 | 0 | 0.0093
| CE430, Ec. Enthalpy Ctrl. | 0.0093103 | 0.0094 | 0.0094 | 0.0094895 | 0 | 0.0094
| CE440, Ec. Enthalpy Limit | 0.0091578 | 0.0093 | 0.0093 | 0.0093341 | 0 | 0.0092
| CE500, Base w/ 0%OA | 0.0097753 | 0 | 0 | 0.0093728 | 0.010218 | 0.0107
| CE500 May-Sep | 0.011021 | 0.0114 | 0.0114 | 0.011322 | 0.011329 | 0.0109
| CE510 May-Sep, High PLR | 0.011395 | 0.0114 | 0.0114 | 0.011329 | 0.011328 | 0.0109
| CE520, EDB = 15°C | 0.0066924 | 0 | 0 | 0.0060452 | 0.0070234 | 0.00763
| CE522, EDB = 20°C | 0.0081904 | 0 | 0 | 0.0076074 | 0.0085797 | 0.00901
| CE525, EDB = 35°C | 0.013713 | 0 | 0 | 0.013802 | 0.01398 | 0.0151
| CE530, Dry Coil | 0.0062265 | 0 | 0 | 0.0067122 | 0.0057975 | 0.00667
| CE540, Dry, EDB = 15°C | 0.0044601 | 0 | 0 | 0.0043466 | 0.0038546 | 0.00463
| CE545, Dry, EDB = 35°C | 0.0062265 | 0 | 0 | 0.0067334 | 0.006749 | 0.00722
| Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 48.6149 | 48.26 | 48.28 | 48.5913 | 47.8261 | 47.93
0 | CE310, High Latent | 58.3307 | 58.51 | 58.53 | 58.5512 | 57.841 | 57.8
0 | CE320, High Infiltration | 52.0053 | 51.21 | 51.25 | 51.8407 | 51.1034 | 49.94
0 | CE330, 100% OA | 50.8445 | 50.58 | 50.65 | 51.1765 | 50.0848 | 50.7
0 | CE340, 50% OA, 50% Infl | 51.085 | 50.69 | 50.73 | 51.1479 | 50.2967 | 50.78
0 | CE350, Tstat Set Up | 45.484 | 45.45 | 45.55 | 45.1731 | 44.3162 | 44.56
0 | CE360, Undersized System | 41.0335 | 41.49 | 41.49 | 42.3695 | 40.871 | 41.21
0 | CE400, Ec. Temp. Ctrl. | 50.7709 | 52.21 | 52.25 | 52.5485 | 0 | 52.01
0 | CE410, Ec. Comp. Lockout | 50.4971 | 49.65 | 49.63 | 0 | 0 | 49.75
0 | CE420, Ec. ODB Limit | 48.7794 | 49.14 | 48.97 | 49.3981 | 0 | 48.76
0 | CE430, Ec. Enthalpy Ctrl. | 48.8219 | 49.17 | 49.3 | 49.6002 | 0 | 49.17
0 | CE440, Ec. Enthalpy Limit | 48.3298 | 48.46 | 48.57 | 48.8288 | 0 | 48.23
0 | CE500, Base w/ 0%OA | 66.5261 | 0 | 0 | 59.1976 | 65.9419 | 63.73
0 | CE500 May-Sep | 57.0476 | 57.47 | 57.47 | 57.3219 | 57.0722 | 55.13
0 | CE510 May-Sep, High PLR | 54.7001 | 57.36 | 57.36 | 57.4361 | 57.0615 | 55.24
0 | CE520, EDB = 15°C | 69.8745 | 0 | 0 | 61.4049 | 70.2268 | 72.17
0 | CE522, EDB = 20°C | 68.6774 | 0 | 0 | 60.7524 | 68.2314 | 68.11
0 | CE525, EDB = 35°C | 61.4674 | 0 | 0 | 54.9944 | 60.1387 | 57.37
0 | CE530, Dry Coil | 46.7299 | 0 | 0 | 48.9733 | 41.4516 | 39.6
0 | CE540, Dry, EDB = 15°C | 48.521 | 0 | 0 | 46.3072 | 40.0509 | 43.82
0 | CE545, Dry, EDB = 35°C | 36.6249 | 0 | 0 | 38.6306 | 36.8747 | 29.2
0
0
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF! | Table B16.5.2-8. f(ODB) Sensitivity CE500 and CE530, April 30 and June 25 (Energy, Coil Loads) |  |  |  |  | 0 | 0 | #REF!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | 0
0 | Case | TUD | NREL | NREL | GARD | UR | NRCan | Tested Prg
0 | Daily Consumptions | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE500 Apr30, Low ODB | 3892.9389 | 3975.4583 | 3975.1667 | 4028.8242 | 3901.0417 | 4073
0 | CE500 Jun25, High ODB | 5044.9219 | 5204.3333 | 5204.0833 | 5228.78 | 5066.5 | 5230
0 | CE500 ODB Sensitivity | 1151.9831 | 1228.875 | 1228.9167 | 1199.9558 | 1165.4583 | 1157
0 | CE530 Apr30, Low ODB | 3022.7732 | 3062 | 3061.7917 | 3101.4372 | 3091.5417 | 3144
0 | CE530 Jun25, high ODB | 3894.1233 | 3978.2083 | 3978.0833 | 4028.6999 | 3934.625 | 4043
0 | CE530 ODB Sensitivity | 871.3501 | 916.2083 | 916.2917 | 927.2627 | 843.0833 | 899 |  |  | Note: Apr30, Jnue 25 compressor data not plotted
0 | CE500 Apr30, Low ODB | 376.0762 | 389.125 | 389.0833 | 0 | 377.25 | 391 |  |  | Energy Consumption, Compressor (Wh,e) | [6 empty] | Your Software
0 | CE500 Jun25, High ODB | 411.4946 | 426.3333 | 426.3333 | 0 | 411.3333 | 424 |  |  | CE500Apr30 | 3014.619 | 3119.8333 | 3119.6667 | 0 | 3020.0417 | 3159
0 | CE500 ODB Sensitivity | 35.4184 | 37.2083 | 37.25 | 0 | 34.0833 | 33 |  |  | CE500Jun25 | 4083.8829 | 4263.5417 | 4263.4167 | 0 | 4105.9583 | 4239
0 | CE530 Apr30, Low ODB | 304.5625 | 311.1667 | 311.125 | 0 | 305.3333 | 314 |  |  | Del CE500 | 1069.2639 | 1143.7083 | 1143.75 | 0 | 1085.9167 | 1080
0 | CE530 Jun25, high ODB | 332.2771 | 339.625 | 339.625 | 0 | 329.25 | 340 |  |  | CE530Apr30 | 2311.4724 | 2390.0417 | 2389.9167 | 0 | 2378.4583 | 2411
0 | CE530 ODB Sensitivity | 27.7146 | 28.4583 | 28.5 | 0 | 23.9167 | 26 |  |  | CE530Jun25 | 3118.0954 | 3243 | 3242.9583 | 0 | 3165.5833 | 3248
0 | CE500 Apr30, Low ODB | 502.2437 | 466.5 | 466.4167 | 518.9273 | 503.75 | 522 |  |  | Del CE530 | 806.623 | 852.9583 | 853.0417 | 0 | 787.125 | 837
0 | CE500 Jun25, High ODB | 549.5444 | 514.4583 | 514.3333 | 565.5397 | 549.2083 | 566
0 | CE500 ODB Sensitivity | 47.3007 | 47.9583 | 47.9167 | 46.6123 | 45.4583 | 44
0 | CE530 Apr30, Low ODB | 406.7383 | 360.7917 | 360.75 | 412.3973 | 407.75 | 419
0 | CE530 Jun25, high ODB | 443.7507 | 395.5833 | 395.5 | 450.0798 | 439.7917 | 454
0 | CE530 ODB Sensitivity | 37.0125 | 34.7917 | 34.75 | 37.6824 | 32.0417 | 35
0 | Sensible + Latent Coil Load (Wh,th) | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE500 Apr30, Low ODB | 13185.6871 | 13732.6998 | 13732.9074 | 13655.2659 | 13169.5417 | 13673
0 | CE500 Jun25, High ODB | 13188.0504 | 13837.5319 | 13837.3853 | 13733.0749 | 13198.0833 | 13727
0 | CE500 ODB Sensitivity | 2.3633 | 104.8321 | 104.4779 | 77.809 | 28.5417 | 54
0 | CE530 Apr30, Low ODB | 9353.1633 | 9721.15 | 9721.3943 | 9775.2401 | 9365.4583 | 9798
0 | CE530 Jun25, high ODB | 9376.2963 | 9760.7918 | 9760.6941 | 9835.1361 | 9387.625 | 9834
0 | CE530 ODB Sensitivity | 23.1329 | 39.6418 | 39.2998 | 59.896 | 22.1667 | 36
0 | CE500 Apr30, Low ODB | 9374.7971 | 9924.8179 | 9925.0255 | 9883.6259 | 9365.4583 | 9902
0 | CE500 Jun25, High ODB | 9377.6867 | 9981.2396 | 9981.0931 | 9952.5713 | 9387.625 | 9946
0 | CE500 ODB Sensitivity | 2.8896 | 56.4217 | 56.0676 | 68.9454 | 22.1667 | 44
0 | CE530 Apr30, Low ODB | 9353.1633 | 9721.15 | 9721.3943 | 9775.2401 | 9365.4583 | 9798
0 | CE530 Jun25, high ODB | 9376.2963 | 9760.7674 | 9760.6697 | 9835.1361 | 9387.625 | 9834
0 | CE530 ODB Sensitivity | 23.1329 | 39.6174 | 39.2754 | 59.896 | 22.1667 | 36
0 | CE500 Apr30, Low ODB | 3810.89 | 3807.8819 | 3807.8819 | 3771.64 | 3804.375 | 3770
0 | CE500 Jun25, High ODB | 3810.3637 | 3856.2923 | 3856.2923 | 3780.5037 | 3810.4167 | 3780
0 | CE500 ODB Sensitivity | -0.52625 | 48.4104 | 48.4104 | 8.8636 | 6.0417 | 10
0 | CE530 Apr30, Low ODB | -5.4771e-13 | 0 | 0 | 5.713e-13 | 0 | 0
0 | CE530 Jun25, high ODB | 7.2905e-13 | 0.024425 | 0.024425 | 6.6831e-13 | 0 | 0
0 | CE530 ODB Sensitivity | 1.2768e-12 | 0.024425 | 0.024425 | 9.7013e-14 | 0 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0 | Table B16.5.2-9. f(ODB) Sensitivity CE500 and CE530, April 30 and June 25 (COP2, Zone Conditions) |  |  |  |  | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TUD | NREL | NREL | GARD | UR | NRCan | Org
0 | Humidity Ratio (kg/kg) | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE500 Apr30, Low ODB | 0.010675 | 0.011 | 0.011 | 0.010984 | 0.010938 | 0.016
0 | CE500 Jun25, High ODB | 0.011168 | 0.0115 | 0.0115 | 0.011459 | 0.011479 | 0.011
0 | CE500 ODB Sensitivity | 0.00049288 | 0.0005 | 0.0005 | 0.00047513 | 0.00054117 | -0.005
0 | CE530 Apr30, Low ODB | 0.006208 | 0.0071 | 0.0071 | 0.0067531 | 0.005485 | 0.00674
0 | CE530 Jun25, high ODB | 0.006208 | 0.0078 | 0.0078 | 0.0067531 | 0.005478 | 0.00674
0 | CE530 ODB Sensitivity | 0 | 0.0007 | 0.0007 | 9.3415e-16 | -7e-06 | 0
0 | COP2 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE500 Apr30, Low ODB | 3.8448 | 3.9136 | 3.9139 | 3.8497 | 3.8372 | 3.85
0 | CE500 Jun25, High ODB | 2.9313 | 2.9505 | 2.9506 | 2.9431 | 2.9213 | 2.94
0 | CE500 ODB Sensitivity | -0.9135 | -0.9631 | -0.96334 | -0.90662 | -0.91589 | -0.91
0 | CE530 Apr30, Low ODB | 3.5431 | 3.5988 | 3.5991 | 3.4414 | 3.4604 | 3.59
0 | CE530 Jun25, high ODB | 2.7197 | 2.7245 | 2.7245 | 2.7795 | 2.69 | 2.74
0 | CE530 ODB Sensitivity | -0.82341 | -0.87433 | -0.87464 | -0.66187 | -0.7704 | -0.85
0 | ODB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | CE500 Apr30, Low ODB | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96
0 | CE500 Jun25, High ODB | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5
0 | CE500 ODB Sensitivity | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54
0 | CE530 Apr30, Low ODB | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96
0 | CE530 Jun25, high ODB | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5
| CE530 ODB Sensitivity | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54
| EDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CE500 Apr30, Low ODB | 24.6411 | 24.9444 | 24.9444 | 24.9818 | 25 | 25
| CE500 Jun25, High ODB | 24.5478 | 25 | 25 | 24.9828 | 25 | 25
| CE500 ODB Sensitivity | -0.093296 | 0.055556 | 0.055556 | 0.0010234 | 0 | 0
| CE530 Apr30, Low ODB | 24.365 | 24.9444 | 24.6667 | 25 | 25 | 25
| CE530 Jun25, high ODB | 24.3537 | 24.9444 | 24.9444 | 25 | 25 | 25
| CE530 ODB Sensitivity | -0.011358 | 0 | 0.27778 | 7.121e-08 | 0 | 0

## Rdata
0 | ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
0 | Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
0
0
0
0
0 | Table B16.5.2-10. Hourly Integrated Maxima (Total Cooling System Energy Consumption and Total Coil Load) | 0
0 | Energy Consumption, Compressor + Both Fans (Wh,e) | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 11626.0371 | 11564 | 11602 | 11899.8597 | 11932 | 11548
0 | CE310, High Latent | 12594.4016 | 12583 | 12595 | 12540.8188 | 12653 | 12162
0 | CE320, High Infiltration | 13028.1986 | 12916 | 12981 | 12954.4267 | 13104 | 12875
0 | CE330, 100% OA | 13346.701 | 13212 | 13407 | 13314.1099 | 13467 | 13335
0 | CE340, 50% OA, 50% Infl | 13180.9018 | 13158 | 13190 | 13134.1703 | 13277 | 13101
0 | CE350, Tstat Set Up | 11626.889 | 11654 | 11602 | 11899.8619 | 11932 | 11546
0 | CE360, Undersized System | 12769.5022 | 12736 | 12726 | 12744.2783 | 12863 | 12762
0 | CE400, Ec. Temp. Ctrl. | 11627.8677 | 11564 | 11677 | 11899.8597 | 0 | 11519
0 | CE410, Ec. Comp. Lockout | 11627.8677 | 11564 | 11602 | 0 | 0 | 11549
0 | CE420, Ec. ODB Limit | 11626.0371 | 11564 | 11602 | 11899.8597 | 0 | 11548
0 | CE430, Ec. Enthalpy Ctrl. | 11626.0371 | 11564 | 11602 | 11899.8597 | 0 | 11548
0 | CE440, Ec. Enthalpy Limit | 11626.0371 | 11564 | 11602 | 11899.8597 | 0 | 11461
0 | CE500, Base w/ 0%OA | 10166.4831 | 10431 | 10425 | 10398.6872 | 10177 | 10274
0 | CE510 High PLR | 11204.8968 | 11590 | 11587 | 11409.8034 | 11186 | 11344
0 | CE520, EDB = 15°C | 11035.3898 | 10989 | 11014 | 11100.5253 | 11044 | 10684
0 | CE522, EDB = 20°C | 10430.7791 | 10972 | 10966 | 10762.3872 | 10639 | 10747
0 | CE525, EDB = 35°C | 9366.7481 | 9538 | 9531 | 9569.5705 | 9419 | 9585
0 | CE530, Dry Coil | 8028.3285 | 8059 | 8055 | 8171.0479 | 7992 | 8089
0 | CE540, Dry, EDB = 15°C | 8698.9562 | 8943 | 8939 | 8677.4025 | 8846 | 8985
0 | CE545, Dry, EDB = 35°C | 7204.827 | 7350 | 7346 | 7762.756 | 7351 | 7471
0 | Sensible Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 23277.4 | 23203 | 23205 | 23530.8075 | 23457 | 22908
0 | CE310, High Latent | 23094.3 | 23080 | 23119 | 23276.4591 | 23078 | 22649
0 | CE320, High Infiltration | 31315.6 | 31119 | 31072 | 31972.0849 | 31134 | 30967
0 | CE330, 100% OA | 33226.1 | 33410 | 34490 | 34764.7794 | 33997 | 33421
0 | CE340, 50% OA, 50% Infl | 32828.9 | 32086 | 32086 | 32887.7843 | 32940 | 32180
0 | CE350, Tstat Set Up | 23277.5 | 23203 | 23205 | 23530.8071 | 23457 | 22876
0 | CE360, Undersized System | 32060.7 | 32111 | 32065 | 32620.9131 | 31981 | 32179
0 | CE400, Ec. Temp. Ctrl. | 23277.5 | 23203 | 23205 | 23530.8075 | 0 | 22877
0 | CE410, Ec. Comp. Lockout | 23265.7 | 23203 | 23205 | 0 | 0 | 22893
0 | CE420, Ec. ODB Limit | 23277.4 | 23203 | 23205 | 23530.8075 | 0 | 22893
0 | CE430, Ec. Enthalpy Ctrl. | 23277.4 | 23203 | 23205 | 23530.8075 | 0 | 22893
0 | CE440, Ec. Enthalpy Limit | 23277.4 | 23203 | 23205 | 23530.8075 | 0 | 22875
0 | CE500, Base w/ 0%OA | 19549.2 | 20009 | 20008 | 19849.2901 | 18776 | 19818
0 | CE510 High PLR | 21729.2 | 22513 | 22513 | 22290.3117 | 21121 | 22269
0 | CE520, EDB = 15°C | 19415.9 | 20159 | 20154 | 19999.2936 | 18969 | 20378
0 | CE522, EDB = 20°C | 19488.8 | 20137 | 20135 | 19933.5062 | 18785 | 19920
0 | CE525, EDB = 35°C | 19702.7 | 19850 | 19850 | 19663.6722 | 18759 | 19661
0 | CE530, Dry Coil | 19834.1 | 19576 | 19575 | 19638.7657 | 18776 | 19626
0 | CE540, Dry, EDB = 15°C | 19575 | 19766 | 19766 | 19726.32 | 18794 | 19799
0 | CE545, Dry, EDB = 35°C | 20075.2 | 19475 | 19474 | 19539.7081 | 18759 | 19497
0 | Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 9635.7 | 9304 | 9394 | 10234.8217 | 10375 | 10392
0 | CE310, High Latent | 15907 | 15139 | 15270 | 16274.8379 | 16112 | 16077
0 | CE320, High Infiltration | 23147.3 | 31497 | 31503 | 22195.4712 | 21697 | 21929
0 | CE330, 100% OA | 27825.2 | 26941 | 40809 | 27134.3149 | 28184 | 27488
0 | CE340, 50% OA, 50% Infl | 24848.3 | 30451 | 36011 | 23911.2415 | 24225 | 23794
0 | CE350, Tstat Set Up | 9751.26 | 9303 | 9393 | 10235.3532 | 10755 | 11603
0 | CE360, Undersized System | 9275.16 | 10026 | 10336 | 8520.3176 | 8859 | 8934
0 | CE400, Ec. Temp. Ctrl. | 27075.3 | 25578 | 32396 | 26317.2818 | 0 | 26645
0 | CE410, Ec. Comp. Lockout | 11138.9 | 9304 | 9391 | 0 | 0 | 10377
0 | CE420, Ec. ODB Limit | 9751.04 | 9304 | 9394 | 10234.8217 | 0 | 10394
0 | CE430, Ec. Enthalpy Ctrl. | 9635.7 | 11105 | 11101 | 11073.7739 | 0 | 10394
0 | CE440, Ec. Enthalpy Limit | 9635.7 | 9304 | 9391 | 10234.8217 | 0 | 10139
0 | CE500, Base w/ 0%OA | 7965.46 | 7733 | 7733 | 7838.7203 | 7805 | 7762
0 | CE510 High PLR | 8892.56 | 8723 | 8723 | 8954.7918 | 8850 | 8874
0 | CE520, EDB = 15°C | 7913.7 | 7785 | 7785 | 7698.5342 | 7726 | 7964
0 | CE522, EDB = 20°C | 7906.7 | 7760 | 7760 | 7769.7702 | 7743 | 7745
0 | CE525, EDB = 35°C | 8037.07 | 7663 | 7663 | 7947.3919 | 7938 | 7820
0 | CE530, Dry Coil | 1.6431e-11 | 0 | 0 | 1.0587 | 179 | 35.9
0 | CE540, Dry, EDB = 15°C | 627.186 | 0 | 0 | 1654.9514 | 845 | 1181
0 | CE545, Dry, EDB = 35°C | 1.8119e-11 | 0 | 0 | 8.2784e-12 | 4 | 0
0 | Senstible + Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 32174.05 | 31401 | 31455 | 32733.2556 | 32502 | 32072
0 | CE310, High Latent | 37328 | 36750 | 37033 | 37126.4795 | 37261 | 36991
0 | CE320, High Infiltration | 40317.6 | 53813 | 53823 | 39765.1828 | 39904 | 39920
0 | CE330, 100% OA | 43492 | 43628 | 64572 | 43445.0808 | 43978 | 42415
0 | CE340, 50% OA, 50% Infl | 41651.7 | 50819 | 59549 | 41328.2736 | 41366 | 41132
0 | CE350, Tstat Set Up | 32091.73 | 31401 | 31454 | 32733.265 | 32502 | 32077
0 | CE360, Undersized System | 38857.16 | 40613 | 41019 | 38459.7282 | 38322 | 38451
0 | CE400, Ec. Temp. Ctrl. | 41178.6 | 40543 | 49838 | 40728.1422 | 0 | 40774
0 | CE410, Ec. Comp. Lockout | 32091.73 | 31401 | 31455 | 0 | 0 | 32073
0 | CE420, Ec. ODB Limit | 32174.05 | 31401 | 31455 | 32733.2556 | 0 | 32072
0 | CE430, Ec. Enthalpy Ctrl. | 32174.05 | 31401 | 31455 | 32733.2556 | 0 | 32072
0 | CE440, Ec. Enthalpy Limit | 32174.05 | 31401 | 31455 | 32733.2556 | 0 | 31777
0 | CE500, Base w/ 0%OA | 27485.51 | 27707 | 27706 | 27646.4256 | 26567 | 27555
0 | CE510 High PLR | 30593.05 | 31188 | 31188 | 31177.751 | 29948 | 31097
0 | CE520, EDB = 15°C | 27329.6 | 27878 | 27878 | 27652.6954 | 26675 | 28343
0 | CE522, EDB = 20°C | 27383.59 | 27868 | 27866 | 27658.7918 | 26514 | 27636
0 | CE525, EDB = 35°C | 27739.77 | 27466 | 27466 | 27576.5137 | 26683 | 27462
0 | CE530, Dry Coil | 19834.1 | 19576 | 19575 | 19638.7657 | 18776 | 19626
0 | CE540, Dry, EDB = 15°C | 19575 | 19766 | 19766 | 19726.32 | 18794 | 19799
0 | CE545, Dry, EDB = 35°C | 20075.2 | 19475 | 19474 | 19539.7081 | 18764 | 19497
0 | * ABS[ (Max-Min) / (Mean of Example Simulation Results) ] | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
0 | Table B16.5.2-12. Hourly Integrated Maxima and Minima (COP2) | [6 empty] | 0
0 | Maximum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 4.1683 | 3.869 | 3.857 | 3.9252 | 3.8706 | 3.88
0 | CE310, High Latent | 4.1433 | 4.141 | 4.128 | 4.1729 | 4.1276 | 4.12
0 | CE320, High Infiltration | 4.1683 | 5.143 | 4.967 | 3.9395 | 3.9433 | 4.38
0 | CE330, 100% OA | 4.1683 | 4.109 | 5.595 | 4.0715 | 4.1219 | 4.05
0 | CE340, 50% OA, 50% Infl | 4.1683 | 4.621 | 5.339 | 3.9866 | 4.0172 | 3.95
0 | CE350, Tstat Set Up | 4.1683 | 3.889 | 3.863 | 4.5552 | 3.9321 | 3.88
0 | CE360, Undersized System | 4.401 | 4.428 | 4.427 | 4.4554 | 4.432 | 4.44
0 | CE400, Ec. Temp. Ctrl. | 4.0769 | 4.088 | 4.776 | 4.0715 | 0 | 4.05
0 | CE410, Ec. Comp. Lockout | 3.8879 | 3.903 | 3.855 | 0 | 0 | 3.84
0 | CE420, Ec. ODB Limit | 3.7813 | 3.807 | 3.759 | 3.8214 | 0 | 3.94
0 | CE430, Ec. Enthalpy Ctrl. | 3.7813 | 3.805 | 3.759 | 3.7927 | 0 | 3.93
0 | CE440, Ec. Enthalpy Limit | 3.8835 | 3.774 | 3.759 | 3.8018 | 0 | 3.81
0 | CE500, Base w/ 0%OA | 4.2751 | 7.367 | 5.301 | 4.198 | 4.1846 | 4.14
0 | CE510 High PLR | 4.6925 | 7.367 | 5.301 | 4.6847 | 4.6896 | 4.53
0 | CE520, EDB = 15°C | 3.8137 | 4.896 | 4.652 | 3.9377 | 3.8017 | 3.84
0 | CE522, EDB = 20°C | 3.9855 | 6.233 | 5.678 | 4.0424 | 3.9858 | 4
0 | CE525, EDB = 35°C | 4.7178 | 6.325 | 6.031 | 4.704 | 4.6381 | 4.4
0 | CE530, Dry Coil | 4.0061 | 3.981 | 3.85 | 3.925 | 3.84 | 3.88
0 | CE540, Dry, EDB = 15°C | 3.456 | 3.456 | 3.455 | 3.6959 | 3.6667 | 3.69
0 | CE545, Dry, EDB = 35°C | 4.2505 | 4.275 | 4.428 | 4.1661 | 4.1565 | 4.17
0 | Minimum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 2.7931 | 2.798 | 2.801 | 2.7815 | 2.7856 | 2.81
0 | CE310, High Latent | 2.8652 | 2.85 | 2.851 | 2.8927 | 2.8726 | 2.87
0 | CE320, High Infiltration | 2.8252 | 2.801 | 2.805 | 2.8415 | 2.8145 | 2.83
0 | CE330, 100% OA | 2.8252 | 2.798 | 2.801 | 2.8441 | 2.8233 | 2.84
0 | CE340, 50% OA, 50% Infl | 2.8252 | 2.798 | 2.801 | 2.8441 | 2.8233 | 2.84
0 | CE350, Tstat Set Up | 2.7904 | 2.798 | 2.801 | 2.7815 | 2.7859 | 2.81
0 | CE360, Undersized System | 2.8252 | 2.799 | 2.801 | 2.8441 | 2.8233 | 2.84
0 | CE400, Ec. Temp. Ctrl. | 2.7819 | 2.734 | 2.735 | 2.7815 | 0 | 2.81
0 | CE410, Ec. Comp. Lockout | 2.7858 | 2.798 | 2.801 | 0 | 0 | 2.81
0 | CE420, Ec. ODB Limit | 2.7931 | 2.798 | 2.801 | 2.7815 | 0 | 2.81
0 | CE430, Ec. Enthalpy Ctrl. | 2.7711 | 2.734 | 2.735 | 2.7815 | 0 | 2.81
0 | CE440, Ec. Enthalpy Limit | 2.7825 | 2.734 | 2.735 | 2.7815 | 0 | 2.81
0 | CE500, Base w/ 0%OA | 2.6852 | 2.693 | 2.652 | 2.7055 | 2.6665 | 2.71
0 | CE510 High PLR | 2.888 | 2.817 | 2.652 | 2.8653 | 2.8817 | 2.9
0 | CE520, EDB = 15°C | 2.4417 | 2.463 | 2.394 | 2.5316 | 2.3333 | 2.47
0 | CE522, EDB = 20°C | 2.5689 | 2.572 | 2.562 | 2.6134 | 2.4286 | 2.59
0 | CE525, EDB = 35°C | 2.9111 | 2.939 | 2.814 | 2.9396 | 2.8941 | 2.9
0 | CE530, Dry Coil | 2.5013 | 2.495 | 2.498 | 2.532 | 2.4733 | 2.52
0 | CE540, Dry, EDB = 15°C | 2.253 | 2.261 | 2.262 | 2.3828 | 2.1429 | 2.28
0 | CE545, Dry, EDB = 35°C | 2.7325 | 2.72 | 2.722 | 2.66 | 2.692 | 2.72
0 | Maximum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 26.1999 | 25.11 | 25.11 | 25.0025 | 25.05 | 26.19
0 | CE310, High Latent | 27.0778 | 26.89 | 26.72 | 26.4747 | 26.62 | 27.19
0 | CE320, High Infiltration | 32.3604 | 31.61 | 31.5 | 31.7089 | 32.32 | 31.65
0 | CE330, 100% OA | 32.2321 | 31.72 | 32 | 31.0686 | 31.9 | 31.3
0 | CE340, 50% OA, 50% Infl | 32.3066 | 31.61 | 31.56 | 31.4977 | 32.15 | 31.58
0 | CE350, Tstat Set Up | 34.5841 | 34.94 | 34.94 | 35.0021 | 35 | 35
0 | CE360, Undersized System | 33.7585 | 32.78 | 32.56 | 32.5106 | 33 | 33.13
0 | CE400, Ec. Temp. Ctrl. | 27.1148 | 27.56 | 28.83 | 26.9099 | 0 | 26.04
0 | CE410, Ec. Comp. Lockout | 26.8256 | 25.11 | 25.11 | 0 | 0 | 26.19
0 | CE420, Ec. ODB Limit | 26.1999 | 25.11 | 25.11 | 25.0025 | 0 | 26.23
0 | CE430, Ec. Enthalpy Ctrl. | 27.1992 | 25.11 | 25.11 | 25.003 | 0 | 26.45
0 | CE440, Ec. Enthalpy Limit | 27.0452 | 25.11 | 25.11 | 25.003 | 0 | 26.26
0 | CE500, Base w/ 0%OA | 25.8054 | 25.11 | 25.11 | 24.9998 | 25.02 | 25
0 | CE510 High PLR | 26.1003 | 25.11 | 25.11 | 24.9998 | 25.02 | 25
0 | CE520, EDB = 15°C | 16.1232 | 16.11 | 15.94 | 15.0005 | 15.98 | 18.62
0 | CE522, EDB = 20°C | 21.0091 | 20.11 | 20.11 | 20.0004 | 20.05 | 20.93
0 | CE525, EDB = 35°C | 36.08 | 35.06 | 35.06 | 34.9995 | 35 | 35
0 | CE530, Dry Coil | 26.116 | 25.06 | 25.06 | 25.0003 | 25.02 | 25
0 | CE540, Dry, EDB = 15°C | 16.1465 | 15.11 | 15.11 | 15.0005 | 15.05 | 15
0 | CE545, Dry, EDB = 35°C | 35.6715 | 35 | 35 | 35 | 35 | 35
0 | Minimum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 7.93 | 8.89 | 8.83 | 8.7175 | 8 | 6.99
0 | CE310, High Latent | 7.93 | 8.89 | 8.83 | 8.7174 | 8 | 6.99
0 | CE320, High Infiltration | 7.93 | 10.83 | 10.78 | 7.7537 | 8 | 6.99
0 | CE330, 100% OA | 7.93 | 8.89 | 8.83 | 8.716 | 8 | 6.99
0 | CE340, 50% OA, 50% Infl | 7.93 | 8.89 | 8.83 | 8.716 | 8 | 6.99
0 | CE350, Tstat Set Up | 7.93 | 8.89 | 8.83 | 8.7175 | 8 | 6.99
0 | CE360, Undersized System | 7.93 | 8.89 | 8.83 | 8.7177 | 8 | 6.99
0 | CE400, Ec. Temp. Ctrl. | 7.93 | 8.89 | 8.83 | 8.7175 | 0 | 6.99
0 | CE410, Ec. Comp. Lockout | 7.93 | 8.89 | 8.83 | 0 | 0 | 6.99
0 | CE420, Ec. ODB Limit | 7.93 | 8.89 | 8.83 | 8.7175 | 0 | 6.99
0 | CE430, Ec. Enthalpy Ctrl. | 7.93 | 8.89 | 8.83 | 8.7175 | 0 | 6.99
0 | CE440, Ec. Enthalpy Limit | 7.93 | 8.89 | 8.83 | 8.7175 | 0 | 7
0 | CE500, Base w/ 0%OA | 8.427 | 8.17 | 7.94 | 8.9388 | 8.54 | 24.04
0 | CE510 High PLR | 8.427 | 8.17 | 7.94 | 8.9388 | 8.54 | 24.04
0 | CE520, EDB = 15°C | 8.3053 | 8.11 | 7.89 | 8.835 | 8.51 | 13.57
0 | CE522, EDB = 20°C | 8.4141 | 8.17 | 7.94 | 8.8978 | 8.54 | 15.98
0 | CE525, EDB = 35°C | 8.4442 | 8.17 | 7.94 | 9.0147 | 8.54 | 33.01
0 | CE530, Dry Coil | 8.4215 | 8.17 | 7.94 | 8.9381 | 8.54 | 24.04
0 | CE540, Dry, EDB = 15°C | 8.2278 | 8.11 | 7.89 | 8.8327 | 8.51 | 14.95
0 | CE545, Dry, EDB = 35°C | 8.4486 | 8.17 | 7.94 | 9.0132 | 8.54 | 33.01
0 | * ABS[ (Max-Min) / (Mean of Example Simulation Results) ] | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0 | Table B16.5.2-14. Hourly Integrated Maxima and Minima (Zone Humidity Ratio) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Maximum Humidity Ratio | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 0.013284 | 0.0138 | 0.0137 | 0.013626 | 0.013457 | 0.0134
0 | CE310, High Latent | 0.01575 | 0.0188 | 0.0189 | 0.015637 | 0.015432 | 0.0157
0 | CE320, High Infiltration | 0.018017 | 0.0177 | 0.0176 | 0.017807 | 0.017547 | 0.0177
0 | CE330, 100% OA | 0.017651 | 0.0178 | 0.0177 | 0.017934 | 0.017045 | 0.0177
0 | CE340, 50% OA, 50% Infl | 0.017871 | 0.0177 | 0.0174 | 0.017787 | 0.017272 | 0.0177
0 | CE350, Tstat Set Up | 0.016758 | 0.0199 | 0.0199 | 0.01719 | 0.016479 | 0.0166
0 | CE360, Undersized System | 0.013433 | 0.0138 | 0.0137 | 0.01386 | 0.013457 | 0.0134
0 | CE400, Ec. Temp. Ctrl. | 0.016944 | 0.017 | 0.017 | 0.016876 | 0 | 0.0173
0 | CE410, Ec. Comp. Lockout | 0.016835 | 0.0169 | 0.0169 | 0 | 0 | 0.0173
0 | CE420, Ec. ODB Limit | 0.014297 | 0.0147 | 0.0141 | 0.014593 | 0 | 0.0147
0 | CE430, Ec. Enthalpy Ctrl. | 0.016231 | 0.0156 | 0.0156 | 0.016135 | 0 | 0.0158
0 | CE440, Ec. Enthalpy Limit | 0.013313 | 0.0138 | 0.0137 | 0.013626 | 0 | 0.0134
0 | CE500, Base w/ 0%OA | 0.01172 | 0.0119 | 0.0118 | 0.011685 | 0.011713 | 0.0115
0 | CE510 High PLR | 0.011871 | 0.0119 | 0.0119 | 0.011689 | 0.011716 | 0.0115
0 | CE520, EDB = 15°C | 0.0075403 | 0.0077 | 0.0078 | 0.0070236 | 0.007566 | 0.0106
0 | CE522, EDB = 20°C | 0.0094264 | 0.0095 | 0.0138 | 0.009111 | 0.009398 | 0.0107
0 | CE525, EDB = 35°C | 0.017932 | 0.018 | 0.018 | 0.018486 | 0.017626 | 0.0173
0 | CE530, Dry Coil | 0.0069892 | 0.0081 | 0.0081 | 0.0067755 | 0.005491 | 0.00677
0 | CE540, Dry, EDB = 15°C | 0.006084 | 0.005 | 0.0063 | 0.0067755 | 0.003256 | 0.00634
0 | CE545, Dry, EDB = 35°C | 0.0069892 | 0.0122 | 0.0122 | 0.0067755 | 0.006689 | 0.00763
0 | Minimum Humidity Ratio | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0.001968 | 0.00197
0 | CE310, High Latent | 0.0018769 | 0.0017 | 0.0017 | 0.0019433 | 0.002019 | 0.00196
0 | CE320, High Infiltration | 0.0018769 | 0.0017 | 0.0017 | 0.0019336 | 0.001968 | 0.00197
0 | CE330, 100% OA | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0.001968 | 0.00197
0 | CE340, 50% OA, 50% Infl | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0.001968 | 0.00197
0 | CE350, Tstat Set Up | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0.001968 | 0.00197
0 | CE360, Undersized System | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0.001968 | 0.00197
0 | CE400, Ec. Temp. Ctrl. | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0 | 0.00197
0 | CE410, Ec. Comp. Lockout | 0.0018769 | 0.0017 | 0.0017 | 0 | 0 | 0.00197
0 | CE420, Ec. ODB Limit | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0 | 0.00197
0 | CE430, Ec. Enthalpy Ctrl. | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0 | 0.00197
0 | CE440, Ec. Enthalpy Limit | 0.0018769 | 0.0017 | 0.0017 | 0.0019277 | 0 | 0.00197
0 | CE500, Base w/ 0%OA | 0.0068276 | 0 | 0 | 0.0070048 | 0.006908 | 0.0103
0 | CE510 High PLR | 0.0068276 | 0 | 0 | 0.0070048 | 0.006908 | 0.0105
0 | CE520, EDB = 15°C | 0.006103 | 0 | 0 | 0.0065213 | 0.006525 | 0.00657
0 | CE522, EDB = 20°C | 0.0068215 | 0 | 0 | 0.0069847 | 0.006908 | 0.00783
0 | CE525, EDB = 35°C | 0.0068356 | 0 | 0 | 0.0070421 | 0.006909 | 0.0154
0 | CE530, Dry Coil | 0.006208 | 0 | 0 | 0.0067348 | 0.005454 | 0.00663
0 | CE540, Dry, EDB = 15°C | 0.0041096 | 0 | 0 | 0.0038186 | 0.003253 | 0.0042
0 | CE545, Dry, EDB = 35°C | 0.006208 | 0 | 0 | 0.0067755 | 0.006685 | 0.007
0 | Maximum Relative Humidity | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 68.7892 | 69.35 | 68.85 | 68.3673 | 68 | 67.44
0 | CE310, High Latent | 77.7029 | 100.18 | 100.7 | 78.6439 | 77 | 78.19
0 | CE320, High Infiltration | 81.8358 | 83.41 | 83.67 | 82.9666 | 83 | 81.88
0 | CE330, 100% OA | 76.6591 | 78.46 | 77.94 | 76.8755 | 76 | 78.7
0 | CE340, 50% OA, 50% Infl | 79.9293 | 81.37 | 81.26 | 80.796 | 80 | 80.25
0 | CE350, Tstat Set Up | 68.7892 | 81.12 | 81.12 | 68.3673 | 70 | 72.65
0 | CE360, Undersized System | 68.7892 | 69.35 | 68.85 | 68.3671 | 68 | 67.44
0 | CE400, Ec. Temp. Ctrl. | 83.7534 | 85.57 | 85.57 | 84.6363 | 0 | 86.31
0 | CE410, Ec. Comp. Lockout | 83.2247 | 84.79 | 84.79 | 0 | 0 | 86.18
0 | CE420, Ec. ODB Limit | 70.8411 | 74.51 | 71.53 | 73.284 | 0 | 73.85
0 | CE430, Ec. Enthalpy Ctrl. | 80.7087 | 78.43 | 78.43 | 80.7427 | 0 | 78.94
0 | CE440, Ec. Enthalpy Limit | 68.7242 | 69.35 | 68.85 | 68.3673 | 0 | 67.51
0 | CE500, Base w/ 0%OA | 100 | 0 | 0 | 100 | 100 | 60.08
0 | CE510 High PLR | 100 | 0 | 0 | 100 | 100 | 57.51
0 | CE520, EDB = 15°C | 90.2299 | 0 | 0 | 93.8137 | 95 | 71.77
0 | CE522, EDB = 20°C | 100 | 0 | 0 | 100 | 100 | 71.32
0 | CE525, EDB = 35°C | 100 | 0 | 0 | 100 | 100 | 51.12
0 | CE530, Dry Coil | 91.0445 | 0 | 0 | 96.1602 | 79 | 36.01
0 | CE540, Dry, EDB = 15°C | 61.275 | 0 | 0 | 55.1794 | 47 | 39.96
0 | CE545, Dry, EDB = 35°C | 90.8772 | 0 | 0 | 96.2348 | 97 | 24.14
0 | Minimum Relative Humidity | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
0 | Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
0 | CE300 Base, 15% OA | 13.3312 | 11.97 | 11.97 | 14.4023 | 15 | 14.94
0 | CE310, High Latent | 13.3898 | 11.97 | 11.97 | 15.5023 | 16 | 15.93
0 | CE320, High Infiltration | 13.3312 | 11.97 | 11.97 | 14.6416 | 15 | 12.92
0 | CE330, 100% OA | 13.3312 | 11.97 | 11.97 | 14.4025 | 15 | 14.94
0 | CE340, 50% OA, 50% Infl | 13.3312 | 11.97 | 11.97 | 14.4025 | 15 | 14.94
0 | CE350, Tstat Set Up | 13.3312 | 11.97 | 11.97 | 14.4023 | 15 | 14.94
0 | CE360, Undersized System | 13.3312 | 11.97 | 11.97 | 14.4023 | 15 | 14.94
0 | CE400, Ec. Temp. Ctrl. | 13.209 | 11.97 | 11.97 | 13.9256 | 0 | 14.57
0 | CE410, Ec. Comp. Lockout | 13.2091 | 11.97 | 11.97 | 0 | 0 | 14.58
0 | CE420, Ec. ODB Limit | 13.2099 | 11.97 | 11.97 | 13.9257 | 0 | 14.59
0 | CE430, Ec. Enthalpy Ctrl. | 13.2078 | 11.97 | 11.97 | 13.9256 | 0 | 14.58
0 | CE440, Ec. Enthalpy Limit | 13.2069 | 11.97 | 11.97 | 13.9256 | 0 | 14.54
0 | CE500, Base w/ 0%OA | 53.4054 | 0 | 0 | 55.1668 | 54 | 52.83
0 | CE510 High PLR | 52.0879 | 0 | 0 | 55.2884 | 54 | 53.15
0 | CE520, EDB = 15°C | 61.2679 | 0 | 0 | 61.7266 | 61 | 61.9
0 | CE522, EDB = 20°C | 58.5054 | 0 | 0 | 59.1798 | 60 | 57.97
0 | CE525, EDB = 35°C | 45.5284 | 0 | 0 | 47.8518 | 44 | 44.4
0 | CE530, Dry Coil | 29.5934 | 0 | 0 | 34.0277 | 28 | 33.68
0 | CE540, Dry, EDB = 15°C | 36.4749 | 0 | 0 | 36.0017 | 31 | 39.74
0 | CE545, Dry, EDB = 35°C | 17.1244 | 0 | 0 | 19.227 | 19 | 20.14

## Sdata
Energy Consumption
Compressor + OD fan | [7 empty] | Condenser (OD) fan | [6 empty] | Compressor
Hour | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg | Hour | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
1 | 2312.3023 | 2134 | 2131 | 2118.6889 | 2123 | 2183.748 | #N/A | 256.5326 | 237 | 237 |  | 237 | 240.938 | #N/A | 1 | 2055.7697 | 1897 | 1894 |  | 1886 | 1942.81 | #N/A
2 | 2310.1977 | 2181 | 2182 | 2131.2588 | 2208 | 2191.634 | #N/A | 256.5271 | 240 | 241 |  | 244 | 241.104 | #N/A | 2 | 2053.6706 | 1941 | 1941 |  | 1964 | 1950.53 | #N/A
3 | 2311.0279 | 2134 | 2131 | 2112.6225 | 2117 | 2139.18 | #N/A | 256.5356 | 237 | 237 |  | 236 | 236.85 | #N/A | 3 | 2054.4923 | 1897 | 1894 |  | 1881 | 1902.33 | #N/A
4 | 2059.6681 | 2128 | 2126 | 2074.7396 | 2114 | 2076.548 | #N/A | 229.5857 | 237 | 236 |  | 236 | 231.118 | #N/A | 4 | 1830.0824 | 1891 | 1890 |  | 1878 | 1845.43 | #N/A
5 | 2285.7366 | 1912 | 1909 | 1997.2205 | 1980 | 2153.147 | #N/A | 256.394 | 215 | 215 |  | 224 | 238.687 | #N/A | 5 | 2029.3426 | 1697 | 1694 |  | 1756 | 1914.46 | #N/A
6 | 2068.9914 | 2385 | 2392 | 2141.5966 | 2328 | 2799.158 | #N/A | 229.5597 | 259 | 259 |  | 253 | 292.588 | #N/A | 6 | 1839.4317 | 2126 | 2133 |  | 2075 | 2506.57 | #N/A
7 | 2975.789 | 3550 | 3576 | 2869.5781 | 3369 | 3513.919 | #N/A | 308.5446 | 352 | 353 |  | 334 | 342.969 | #N/A | 7 | 2667.2444 | 3198 | 3223 |  | 3035 | 3170.95 | #N/A
8 | 3936.764 | 3467 | 3480 | 3498.5394 | 3655 | 3794.558 | #N/A | 384.0455 | 332 | 335 |  | 352 | 360.598 | #N/A | 8 | 3552.7185 | 3135 | 3145 |  | 3303 | 3433.96 | #N/A
9 | 4822.8773 | 4997 | 4993 | 4681.7762 | 4946 | 4949.938 | #N/A | 458.1014 | 469 | 467 |  | 463 | 460.788 | #N/A | 9 | 4364.7758 | 4528 | 4526 |  | 4483 | 4489.15 | #N/A
10 | 4899.0565 | 5130 | 5133 | 4947.6011 | 5066 | 5342.735 | #N/A | 457.9932 | 479 | 478 |  | 472 | 489.455 | #N/A | 10 | 4441.0633 | 4651 | 4655 |  | 4594 | 4853.28 | #N/A
11 | 5505.8995 | 5971 | 5992 | 5406.6429 | 5754 | 5672.438 | #N/A | 506.3045 | 537 | 536 |  | 516 | 508.218 | #N/A | 11 | 4999.595 | 5434 | 5456 |  | 5238 | 5164.22 | #N/A
12 | 5846.136 | 5517 | 5513 | 5632.385 | 5570 | 5501.464 | #N/A | 529.3648 | 498 | 498 |  | 504 | 496.504 | #N/A | 12 | 5316.7711 | 5019 | 5015 |  | 5066 | 5004.96 | #N/A
13 | 6805.1571 | 6637 | 6636 | 7132.8035 | 7084 | 7093.864 | #N/A | 616.6094 | 597 | 600 |  | 642 | 639.274 | #N/A | 13 | 6188.5477 | 6040 | 6036 |  | 6442 | 6454.59 | #N/A
14 | 6827.0535 | 7053 | 7064 | 6983.3064 | 7168 | 7143.353 | #N/A | 616.1242 | 633 | 635 |  | 645 | 639.953 | #N/A | 14 | 6210.9293 | 6420 | 6429 |  | 6523 | 6503.4 | #N/A
15 | 8703.455 | 8422 | 8437 | 8572.0438 | 8785 | 8825.455 | #N/A | 781.0016 | 751 | 754 |  | 785 | 784.905 | #N/A | 15 | 7922.4534 | 7671 | 7683 |  | 8000 | 8040.55 | #N/A
16 | 8745.8354 | 8990 | 9025 | 8732.6963 | 8968 | 8927.2 | #N/A | 781.0124 | 800 | 803 |  | 799 | 793.61 | #N/A | 16 | 7964.823 | 8190 | 8222 |  | 8169 | 8133.59 | #N/A
17 | 5950.276 | 6276 | 6252 | 5718.3243 | 5825 | 5721.371 | #N/A | 529.4985 | 561 | 556 |  | 519 | 509.581 | #N/A | 17 | 5420.7775 | 5715 | 5696 |  | 5306 | 5211.79 | #N/A
18 | 5939.3653 | 6080 | 6072 | 5880.5828 | 5909 | 5629.246 | #N/A | 529.3784 | 544 | 541 |  | 528 | 506.956 | #N/A | 18 | 5409.9868 | 5536 | 5531 |  | 5381 | 5122.29 | #N/A
19 | 5789.2634 | 5192 | 5168 | 5555.1112 | 5283 | 5324.69 | #N/A | 529.2289 | 481 | 479 |  | 492 | 492.97 | #N/A | 19 | 5260.0345 | 4711 | 4689 |  | 4791 | 4831.72 | #N/A
20 | 5386.5635 | 5363 | 5358 | 5259.2137 | 5307 | 5376.089 | #N/A | 506.2207 | 504 | 503 |  | 498 | 501.239 | #N/A | 20 | 4880.3429 | 4859 | 4855 |  | 4809 | 4874.85 | #N/A
21 | 4347.7986 | 4318 | 4324 | 4325.7083 | 4347 | 4341.163 | #N/A | 409.0843 | 405 | 406 |  | 408 | 405.543 | #N/A | 21 | 3938.7143 | 3913 | 3918 |  | 3939 | 3935.62 | #N/A
22 | 4333.4889 | 4224 | 4222 | 4278.8801 | 4254 | 4243.269 | #N/A | 409.5326 | 399 | 399 |  | 402 | 398.939 | #N/A | 22 | 3923.9563 | 3825 | 3823 |  | 3852 | 3844.33 | #N/A
23 | 4556.4267 | 4145 | 4142 | 4172.5901 | 4147 | 4204.735 | #N/A | 433.8551 | 395 | 394 |  | 395 | 397.275 | #N/A | 23 | 4122.5716 | 3750 | 3748 |  | 3752 | 3807.46 | #N/A
24 | 4286.9653 | 4287 | 4287 | 4151.9737 | 4193 | 4049.81 | #N/A | 409.5808 | 407 | 407 |  | 399 | 385.64 | #N/A | 24 | 3877.3845 | 3880 | 3880 |  | 3794 | 3664.17 | #N/A
Coil Load, Total (kWh,thermal)
Sensible | [7 empty] | Latent
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
1 | 6189.34 | 5889.2583 | 5886.9135 | 5810.748 | 5788 | 5870.06 | #N/A | 1942.39 | 1663.0494 | 1658.0667 | 1660.9695 | 1684 | 1797.5 | #N/A
2 | 6201.56 | 6069.8079 | 6067.17 | 5853.1492 | 5961 | 5871.7 | #N/A | 1914.24 | 1560.4644 | 1559.8782 | 1641.261 | 1747 | 1802.77 | #N/A
3 | 6194.38 | 5881.3446 | 5878.1205 | 5809.4072 | 5788 | 5782.88 | #N/A | 1933.51 | 1668.9114 | 1668.0321 | 1637.1772 | 1657 | 1745.07 | #N/A
4 | 5548.55 | 5878.1205 | 5873.4309 | 5743.5733 | 5788 | 5683.06 | #N/A | 1675.6 | 1655.7219 | 1654.8426 | 1588.4261 | 1644 | 1634.17 | #N/A
5 | 6318.9 | 5675.2953 | 5671.7781 | 5614.133 | 5580 | 5955.01 | #N/A | 1785.95 | 1122.573 | 1081.2459 | 1476.8894 | 1420 | 1559.34 | #N/A
6 | 5686.24 | 6438.5277 | 6438.5277 | 6015.0762 | 6341 | 7311.79 | #N/A | 1444.63 | 1697.6352 | 1746.5829 | 1409.9863 | 1574 | 1911.15 | #N/A
7 | 7596.88 | 8342.2122 | 8347.7811 | 7532.4754 | 8277 | 8646.87 | #N/A | 2114.5 | 2733.7437 | 2884.9833 | 1683.5246 | 2173 | 2122.59 | #N/A
8 | 9558.23 | 9069.9795 | 9069.1002 | 8756.6552 | 9038 | 9298.63 | #N/A | 2563.08 | 1220.7615 | 1202.5893 | 1852.7556 | 1775 | 1887.81 | #N/A
9 | 11757.9 | 11872.6017 | 11875.2396 | 11767.1681 | 11971 | 11923.2 | #N/A | 2797.72 | 2913.1209 | 2968.8099 | 2265.1778 | 2660 | 2821.19 | #N/A
10 | 11506.4 | 12039.0825 | 12041.1342 | 11996.3298 | 11971 | 12287.1 | #N/A | 3132.98 | 3300.8922 | 3351.5985 | 2781.3597 | 3128 | 3595.03 | #N/A
11 | 12342.2 | 12811.9872 | 12817.5561 | 12488.0938 | 12731 | 12561.8 | #N/A | 4031.89 | 4643.2902 | 4787.4954 | 3417.3158 | 3991 | 4052.76 | #N/A
12 | 12810 | 12612.093 | 12610.9206 | 12670.959 | 12559 | 12561.3 | #N/A | 4438.4 | 3603.0783 | 3576.6993 | 3850.9165 | 3699 | 3468.23 | #N/A
13 | 16816.1 | 17139.0225 | 17135.2122 | 17401.2828 | 17422 | 17430.7 | #N/A | 3682.11 | 2583.9696 | 2485.7811 | 4187.139 | 3669 | 3749.01 | #N/A
14 | 17283.5 | 17638.1718 | 17639.0511 | 17591.92 | 17629 | 17608.6 | #N/A | 2950.56 | 3170.1696 | 3180.135 | 3085.9376 | 3438 | 3446.79 | #N/A
15 | 22882.4 | 22196.463 | 22196.7561 | 22480.6555 | 22491 | 22350.4 | #N/A | 3804.88 | 3190.6866 | 3195.9624 | 3652.3342 | 4145 | 4719.45 | #N/A
16 | 22284.7 | 22527.9591 | 22533.2349 | 22557.3408 | 22491 | 22292 | #N/A | 4437.98 | 5053.044 | 5187.87 | 4107.284 | 4925 | 5331.25 | #N/A
17 | 13048.3 | 13599.2538 | 13600.1331 | 13061.4841 | 12939 | 12739.1 | #N/A | 4183.03 | 4605.4803 | 4644.4626 | 3283.1293 | 3763 | 3811.95 | #N/A
18 | 12720.6 | 12829.8663 | 12831.6249 | 12869.5918 | 12729 | 12180.9 | #N/A | 4785.28 | 5103.4572 | 5146.2498 | 4323.8131 | 4582 | 4648.77 | #N/A
19 | 12490.8 | 11875.5327 | 11871.1362 | 12169.8539 | 11761 | 11540.7 | #N/A | 5170.89 | 4136.5203 | 4043.3145 | 4707.7678 | 4470 | 5094.59 | #N/A
20 | 11655.3 | 11532.3126 | 11534.0712 | 11555.6363 | 11381 | 11359.2 | #N/A | 5334.51 | 5549.8485 | 5586.1929 | 4980.857 | 5486 | 5771.92 | #N/A
21 | 8882.19 | 9302.4078 | 9302.7009 | 9062.7383 | 9036 | 8931.39 | #N/A | 4657.75 | 4133.0031 | 4142.3823 | 4382.6766 | 4447 | 4593.42 | #N/A
22 | 8880.28 | 8973.5496 | 8973.8427 | 8952.5422 | 8864 | 8747.22 | #N/A | 4684.26 | 4306.8114 | 4311.2079 | 4433.9592 | 4459 | 4608.6 | #N/A
23 | 9449.35 | 8787.4311 | 8787.4311 | 8753.473 | 8656 | 8646.75 | #N/A | 5081.99 | 4404.4137 | 4404.7068 | 4437.0933 | 4482 | 4696.56 | #N/A
24 | 8806.54 | 8799.1551 | 8799.7413 | 8673.9655 | 8656 | 8359.6 | #N/A | 4885.22 | 4925.2524 | 4954.5624 | 4522.2365 | 4666 | 4613.06 | #N/A
HumRat
0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
1 | 0.0090778 | 0.0094 | 0.0094 | 0.0094054 | 0.009276 | 0.0092502 | #N/A
2 | 0.0090138 | 0.0093 | 0.0093 | 0.0093664 | 0.009302 | 0.0092582 | #N/A
3 | 0.0090644 | 0.0094 | 0.0094 | 0.0093723 | 0.009239 | 0.0092068 | #N/A
4 | 0.0089864 | 0.0094 | 0.0094 | 0.0093141 | 0.009201 | 0.0091047 | #N/A
5 | 0.0088405 | 0.0089 | 0.009 | 0.0091917 | 0.008969 | 0.0089519 | #N/A
6 | 0.0086578 | 0.0092 | 0.0092 | 0.0090454 | 0.009012 | 0.0091583 | #N/A
7 | 0.0091531 | 0.01 | 0.0098 | 0.0093227 | 0.00949 | 0.0094778 | #N/A
8 | 0.0095303 | 0.0094 | 0.0094 | 0.0096417 | 0.009314 | 0.0093737 | #N/A
9 | 0.0096727 | 0.0099 | 0.0099 | 0.0098152 | 0.009708 | 0.0097161 | #N/A
10 | 0.010058 | 0.0103 | 0.0102 | 0.010197 | 0.010041 | 0.010237 | #N/A
11 | 0.010408 | 0.0109 | 0.0107 | 0.010626 | 0.010588 | 0.010622 | #N/A
12 | 0.010684 | 0.0108 | 0.0108 | 0.010942 | 0.01058 | 0.010433 | #N/A
13 | 0.010087 | 0.0101 | 0.0102 | 0.010387 | 0.009975 | 0.0099715 | #N/A
14 | 0.0097987 | 0.01 | 0.01 | 0.0099642 | 0.009778 | 0.0097436 | #N/A
15 | 0.0095792 | 0.0098 | 0.0098 | 0.0098097 | 0.009579 | 0.0097834 | #N/A
16 | 0.0096663 | 0.01 | 0.0098 | 0.0099222 | 0.009733 | 0.0098255 | #N/A
17 | 0.01077 | 0.0107 | 0.0107 | 0.010633 | 0.01044 | 0.010257 | #N/A
18 | 0.011184 | 0.0112 | 0.0112 | 0.011174 | 0.010912 | 0.010859 | #N/A
19 | 0.011131 | 0.011 | 0.0111 | 0.011312 | 0.010914 | 0.011024 | #N/A
20 | 0.010991 | 0.0114 | 0.0113 | 0.011348 | 0.011269 | 0.011357 | #N/A
21 | 0.01114 | 0.0113 | 0.0113 | 0.011561 | 0.011348 | 0.011378 | #N/A
22 | 0.011177 | 0.0114 | 0.0114 | 0.0116 | 0.011383 | 0.011398 | #N/A
23 | 0.011176 | 0.0115 | 0.0115 | 0.011611 | 0.011416 | 0.01145 | #N/A
24 | 0.011275 | 0.0117 | 0.0117 | 0.011664 | 0.011507 | 0.011462 | #N/A
COP2
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
1 | 3.5167 | 3.539 | 3.5406 | 3.5266 | 3.5195 | 3.5112 | #N/A
2 | 3.513 | 3.4985 | 3.4954 | 3.5164 | 3.4905 | 3.5017 | #N/A
3 | 3.517 | 3.5381 | 3.5411 | 3.5248 | 3.5168 | 3.5191 | #N/A
4 | 3.5074 | 3.5403 | 3.5411 | 3.5339 | 3.5156 | 3.5238 | #N/A
5 | 3.5458 | 3.5554 | 3.5375 | 3.5504 | 3.5354 | 3.4899 | #N/A
6 | 3.4465 | 3.4114 | 3.4219 | 3.4671 | 3.3999 | 3.2949 | #N/A
7 | 3.2635 | 3.12 | 3.1412 | 3.2116 | 3.1018 | 3.0648 | #N/A
8 | 3.079 | 2.9682 | 2.9516 | 3.0325 | 2.9584 | 2.948 | #N/A
9 | 3.018 | 2.9589 | 2.973 | 2.9972 | 2.9581 | 2.9787 | #N/A
10 | 2.9882 | 2.9902 | 2.9988 | 2.9868 | 2.9805 | 2.9726 | #N/A
11 | 2.9739 | 2.9233 | 2.9381 | 2.9418 | 2.9062 | 2.929 | #N/A
12 | 2.9504 | 2.9391 | 2.9363 | 2.9334 | 2.9189 | 2.9137 | #N/A
13 | 3.0122 | 2.9717 | 2.9568 | 3.0266 | 2.9771 | 2.9856 | #N/A
14 | 2.9638 | 2.9503 | 2.9472 | 2.961 | 2.939 | 2.9476 | #N/A
15 | 3.0663 | 3.0144 | 3.0097 | 3.0486 | 3.032 | 3.0672 | #N/A
16 | 3.0555 | 3.068 | 3.0716 | 3.0534 | 3.0571 | 3.0943 | #N/A
17 | 2.8959 | 2.9007 | 2.9182 | 2.8583 | 2.8673 | 2.8928 | #N/A
18 | 2.9474 | 2.9496 | 2.9608 | 2.9238 | 2.9298 | 2.9897 | #N/A
19 | 3.0508 | 3.084 | 3.0794 | 3.0382 | 3.0725 | 3.1242 | #N/A
20 | 3.1541 | 3.1852 | 3.1953 | 3.1443 | 3.1783 | 3.1865 | #N/A
21 | 3.1142 | 3.1115 | 3.1094 | 3.1083 | 3.1019 | 3.1155 | #N/A
22 | 3.1302 | 3.144 | 3.1466 | 3.1285 | 3.1316 | 3.1475 | #N/A
23 | 3.1892 | 3.1826 | 3.185 | 3.1612 | 3.1683 | 3.1734 | #N/A
24 | 3.1938 | 3.2014 | 3.2084 | 3.1783 | 3.1774 | 3.2033 | #N/A
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
ODB (°C) | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
1 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8 | #N/A
2 | 18.05 | 18.3333 | 18.3333 | 18.1125 | 18.3 | 18.3 | #N/A
3 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8 | #N/A
4 | 17.8 | 17.7778 | 17.7778 | 17.8 | 17.8 | 17.8 | #N/A
5 | 17.5 | 17.2222 | 17.2222 | 17.425 | 17.2 | 17.2 | #N/A
6 | 18.3 | 19.4444 | 19.4444 | 18.575 | 19.4 | 19.4 | #N/A
7 | 22.2 | 25 | 25 | 22.9 | 25 | 25 | #N/A
8 | 26.1 | 27.2222 | 27.2222 | 26.375 | 27.2 | 27.2 | #N/A
9 | 28.05 | 28.8889 | 28.8889 | 28.2625 | 28.9 | 28.9 | #N/A
10 | 28.9 | 28.8889 | 28.8889 | 28.9 | 28.9 | 28.9 | #N/A
11 | 30 | 31.1111 | 31.1111 | 30.275 | 31.1 | 31.1 | #N/A
12 | 30.85 | 30.5556 | 30.5556 | 30.7875 | 30.6 | 30.6 | #N/A
13 | 30.85 | 31.1111 | 31.1111 | 30.9125 | 31.1 | 31.1 | #N/A
14 | 31.4 | 31.6667 | 31.6667 | 31.475 | 31.7 | 31.7 | #N/A
15 | 31.95 | 32.2222 | 32.2222 | 32.0125 | 32.2 | 32.2 | #N/A
16 | 32.2 | 32.2222 | 32.2222 | 32.2 | 32.2 | 32.2 | #N/A
17 | 31.95 | 31.6667 | 31.6667 | 31.8875 | 31.7 | 31.7 | #N/A
18 | 31.4 | 31.1111 | 31.1111 | 31.325 | 31.1 | 31.1 | #N/A
19 | 29.7 | 28.3333 | 28.3333 | 29.35 | 28.3 | 28.3 | #N/A
20 | 27.75 | 27.2222 | 27.2222 | 27.6125 | 27.2 | 27.2 | #N/A
21 | 27.2 | 27.2222 | 27.2222 | 27.2 | 27.2 | 27.2 | #N/A
22 | 26.95 | 26.6667 | 26.6667 | 26.8875 | 26.7 | 26.7 | #N/A
23 | 26.4 | 26.1111 | 26.1111 | 26.325 | 26.1 | 26.1 | #N/A
24 | 26.1 | 26.1111 | 26.1111 | 26.1 | 26.1 | 26.1 | #N/A
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
EDB (°C) | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EWB
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
1 | 23.4068 | 23.8333 | 23.8333 | 23.9453 | 23.92 | 23.9367 | #N/A | 16.9641 | 17.34 | 17.34 |  | 17.155 | 17.3042 | #N/A
2 | 23.3748 | 23.9444 | 23.9444 | 23.9638 | 24 | 23.9367 | #N/A | 16.9046 | 17.29 | 17.29 |  | 17.238 | 17.31 | #N/A
3 | 23.3833 | 23.8333 | 23.8333 | 23.9453 | 23.92 | 23.8958 | #N/A | 16.9418 | 17.34 | 17.37 |  | 17.12 | 17.2367 | #N/A
4 | 23.3739 | 23.8333 | 23.8333 | 23.9171 | 23.92 | 23.8375 | #N/A | 16.8619 | 17.34 | 17.37 |  | 17.102 | 17.0785 | #N/A
5 | 23.3503 | 23.7778 | 23.7778 | 23.8615 | 23.83 | 23.9757 | #N/A | 16.6966 | 16.85 | 16.94 |  | 16.787 | 17.0075 | #N/A
6 | 23.4171 | 24.1111 | 24.1111 | 24.0337 | 24.16 | 24.5756 | #N/A | 16.5734 | 17.3 | 17.3 |  | 17.032 | 17.5412 | #N/A
7 | 24.0395 | 24.9444 | 24.9444 | 24.6841 | 25 | 25.1643 | #N/A | 17.3192 | 18.39 | 18.23 |  | 17.911 | 17.9926 | #N/A
8 | 24.5724 | 25.2778 | 25.2778 | 25.2076 | 25.33 | 25.4533 | #N/A | 17.7945 | 17.78 | 17.78 |  | 17.646 | 17.9591 | #N/A
9 | 25.0937 | 25.5556 | 25.5556 | 25.4902 | 25.59 | 25.5785 | #N/A | 17.973 | 18.36 | 18.28 |  | 18.118 | 18.3251 | #N/A
10 | 25.2815 | 25.5556 | 25.5556 | 25.5859 | 25.59 | 25.7393 | #N/A | 18.3972 | 18.68 | 18.6 |  | 18.442 | 18.8543 | #N/A
11 | 25.3592 | 25.8889 | 25.8889 | 25.7944 | 25.91 | 25.8631 | #N/A | 18.8246 | 19.48 | 19.33 |  | 19.142 | 19.1876 | #N/A
12 | 25.5877 | 25.8333 | 25.8333 | 25.8706 | 25.84 | 25.8628 | #N/A | 19.1202 | 19.23 | 19.23 |  | 18.935 | 18.8671 | #N/A
13 | 26.53 | 25.9444 | 25.9444 | 25.8841 | 25.91 | 25.9424 | #N/A | 18.8377 | 18.56 | 18.64 |  | 18.326 | 18.518 | #N/A
14 | 26.5617 | 26.0556 | 26.0556 | 25.9682 | 26 | 26.022 | #N/A | 18.5548 | 18.6 | 18.6 |  | 18.269 | 18.4421 | #N/A
15 | 26.7812 | 26.1111 | 26.1111 | 26.0506 | 26.08 | 26.1296 | #N/A | 18.5486 | 18.46 | 18.46 |  | 18.239 | 18.6471 | #N/A
16 | 26.5632 | 26.1667 | 26.1667 | 26.0819 | 26.08 | 26.0323 | #N/A | 18.673 | 18.84 | 18.76 |  | 18.557 | 18.7965 | #N/A
17 | 26.198 | 26.0556 | 26.0556 | 26.0383 | 26 | 25.943 | #N/A | 19.4032 | 19.35 | 19.35 |  | 19.063 | 19.1104 | #N/A
18 | 26.2263 | 25.9444 | 25.9444 | 25.9541 | 25.91 | 25.6955 | #N/A | 19.7724 | 19.75 | 19.68 |  | 19.458 | 19.3936 | #N/A
19 | 25.7001 | 25.5 | 25.5 | 25.6545 | 25.5 | 25.4093 | #N/A | 19.5753 | 19.32 | 19.4 |  | 19.199 | 19.5323 | #N/A
20 | 25.1673 | 25.3333 | 25.3333 | 25.3924 | 25.33 | 25.3281 | #N/A | 19.3718 | 19.76 | 19.76 |  | 19.65 | 19.7431 | #N/A
21 | 24.6544 | 25.3333 | 25.3333 | 25.332 | 25.33 | 25.291 | #N/A | 19.438 | 19.76 | 19.76 |  | 19.706 | 19.7437 | #N/A
22 | 24.7445 | 25.2222 | 25.2222 | 25.2853 | 25.25 | 25.2092 | #N/A | 19.4846 | 19.8 | 19.8 |  | 19.697 | 19.7887 | #N/A
23 | 24.6707 | 25.1111 | 25.1111 | 25.2003 | 25.16 | 25.1645 | #N/A | 19.4693 | 19.84 | 19.84 |  | 19.694 | 19.8355 | #N/A
24 | 24.7257 | 25.1111 | 25.1111 | 25.1665 | 25.16 | 25.0374 | #N/A | 19.5725 | 20.14 | 20.06 |  | 19.805 | 19.7678 | #N/A
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
OHR (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
1 | 0.011255 | 0.0114 | 0.0114 | 0.011192 | 0.0111 | 0.011072 | #N/A
2 | 0.011255 | 0.0112 | 0.0112 | 0.011286 | 0.011462 | 0.011432 | #N/A
3 | 0.011255 | 0.0114 | 0.0114 | 0.01119 | 0.0111 | 0.011072 | #N/A
4 | 0.011075 | 0.0114 | 0.0114 | 0.011051 | 0.0111 | 0.011072 | #N/A
5 | 0.01061 | 0.0103 | 0.0103 | 0.010479 | 0.01018 | 0.010155 | #N/A
6 | 0.010568 | 0.0113 | 0.0113 | 0.010637 | 0.011001 | 0.01097 | #N/A
7 | 0.012071 | 0.0133 | 0.0133 | 0.012265 | 0.01314 | 0.013099 | #N/A
8 | 0.012173 | 0.0109 | 0.0109 | 0.011777 | 0.011075 | 0.011039 | #N/A
9 | 0.011538 | 0.0117 | 0.0117 | 0.011572 | 0.011995 | 0.011957 | #N/A
10 | 0.012388 | 0.0125 | 0.0125 | 0.012393 | 0.01276 | 0.012719 | #N/A
11 | 0.013776 | 0.0148 | 0.0148 | 0.013955 | 0.014809 | 0.014761 | #N/A
12 | 0.014041 | 0.0134 | 0.0134 | 0.013752 | 0.013253 | 0.013211 | #N/A
13 | 0.012315 | 0.0115 | 0.0115 | 0.011978 | 0.011329 | 0.011293 | #N/A
14 | 0.011543 | 0.0121 | 0.0121 | 0.011517 | 0.011729 | 0.011692 | #N/A
15 | 0.012069 | 0.0119 | 0.0119 | 0.012075 | 0.012379 | 0.01234 | #N/A
16 | 0.013324 | 0.0144 | 0.0144 | 0.013479 | 0.014232 | 0.014188 | #N/A
17 | 0.014505 | 0.0146 | 0.0146 | 0.014485 | 0.01473 | 0.014684 | #N/A
18 | 0.015234 | 0.0157 | 0.0157 | 0.015265 | 0.015684 | 0.015634 | #N/A
19 | 0.015134 | 0.0143 | 0.0143 | 0.014908 | 0.014539 | 0.014493 | #N/A
20 | 0.015748 | 0.0164 | 0.0164 | 0.015925 | 0.016878 | 0.016824 | #N/A
21 | 0.016886 | 0.0164 | 0.0164 | 0.016792 | 0.016878 | 0.016824 | #N/A
22 | 0.016863 | 0.0167 | 0.0167 | 0.016752 | 0.016832 | 0.016777 | #N/A
23 | 0.016867 | 0.0169 | 0.0169 | 0.016764 | 0.016889 | 0.016835 | #N/A
24 | 0.017112 | 0.0178 | 0.0178 | 0.017059 | 0.017329 | 0.017273 | #N/A

## Tdata
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.5.2
Example Results for Section 5.3 - HVAC Equipment Performance Tests CE300 through CE545
Table B16.5.2-17. Delta Annual Space Cooling Electricity Consumptions (Total, Compressor) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 4339.6026 | 4629 | 4629 | 4544.7265 | 4543.158 | 4538
CE320-CE300, Infiltration | 4425.8798 | 3995 | 4037 | 4333.4627 | 4424.404 | 4387
CE330-CE300, 100% OA | 5329.5231 | 4958 | 4683 | 5397.736 | 5558.726 | 5260
CE330-CE320, OA-Infl | 903.6433 | 963 | 646 | 1064.2734 | 1134.322 | 873
CE340-CE300, 50/50 OA/inf | 4985.5179 | 4608 | 4510 | 5037.381 | 5088.85 | 4877
CE330-CE340, OA-50/50 | 344.0053 | 350 | 173 | 360.355 | 469.876 | 383
CE350-CE300, Tstat Set Up | -3396.7978 | -4203 | -4207 | -3600.5239 | -3389.819 | -3328
(CE360-CE300)/4, Overload | 4916.2536 | 4828.5 | 4815.25 | 4989.7684 | 4966.7118 | 4999.5 | #VALUE!
CE400-CE300, Ec. T Ctrl | -3588.6237 | -3904 | -3879 | -3732.9566 | 0 | -3657
CE410-CE300, Ec. No Compr. | -3555.3454 | -3082 | -3056 | 0 | 0 | -3567
CE420-CE300, Ec. ODB Lim. | -2246.7696 | -2220 | -1845 | -2010.1329 | 0 | -1862
CE430-CE300, Ec. Enth Ctrl | -3095.7459 | -2818 | -2944 | -2973.2406 | 0 | -3252
CE440-CE300, Ec. Enth Lim | -1942.4562 | -1718 | -1782 | -1713.9923 | 0 | -1822
(CE500-CE300)/2, 0%OA | -6647.9451 | -5966.5 | -5966.5 | -5855.5147 | -6326.729 | -5966 | #VALUE!
(CE510-CE500)/4, PLR | 4304.4811 | 4524.75 | 4525 | 4434.0932 | 4353.525 | 4448.5 | #VALUE!
CE525-CE520, EDB | -4665.708 | -4981 | -4969 | -4315.6173 | -4889.357 | -4458
CE530-CE500, Dry Coil | -5056.616 | -5277 | -5285 | -5292.6649 | -4880.485 | -5263
CE545-CE540, EDB (Dry) | -3743.2989 | -4076 | -4083 | -2425.3866 | -3745.491 | -3825
Compressor (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 3986.0911 | 4244 | 4244 | 0 | 4166.82 | 4177
CE320-CE300, Infiltration | 4079.6031 | 3681 | 3721 | 0 | 4076.025 | 4036
CE330-CE300, 100% OA | 4946.1978 | 4603 | 4352 | 0 | 5157.732 | 4899
CE330-CE320, OA-Infl | 866.5947 | 922 | 631 | 0 | 1081.707 | 863
CE340-CE300, 50/50 OA/inf | 4609.403 | 4260 | 4172 | 0 | 4702.789 | 4524
CE330-CE340, OA-50/50 | 336.7947 | 343 | 180 | 0 | 454.943 | 375
CE350-CE300, Tstat Set Up | -3036.6939 | -3767 | -3772 | 0 | -3031.946 | -2985
(CE360-CE300)/4, Overload | 4438.0764 | 4357.5 | 4345.5 | 0 | 4481.7903 | 4516.25 | #VALUE!
CE400-CE300, Ec. T Ctrl | -3174.5856 | -3463 | -3442 | 0 | 0 | -3247
CE410-CE300, Ec. No Compr. | -3149.0399 | -2746 | -2723 | 0 | 0 | -3191
CE420-CE300, Ec. ODB Lim. | -1994.9489 | -1973 | -1639 | 0 | 0 | -1662
CE430-CE300, Ec. Enth Ctrl | -2754.9132 | -2510 | -2622 | 0 | 0 | -2910
CE440-CE300, Ec. Enth Lim | -1724.4011 | -1527 | -1584 | 0 | 0 | -1627
(CE500-CE300)/2, 0%OA | -2249.6194 | -1548 | -1547.5 | 0 | -1956.0745 | -1677 | #VALUE!
(CE510-CE500)/4, PLR | 3451.4328 | 3575.75 | 3576 | 0 | 3478.3612 | 3557.5 | #VALUE!
CE525-CE520, EDB | -2963.4018 | -3241 | -3233 | 0 | -3148.17 | -2742
CE530-CE500, Dry Coil | -4197.3004 | -4346 | -4354 | 0 | -4001.924 | -4350
CE545-CE540, EDB (Dry) | -2398.8748 | -2713 | -2720 | 0 | -2413.197 | -2449
Supply Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0 | 0 | 0 | 0 | 0 | 0
CE320-CE300, Infiltration | 0 | 0 | 0 | 0 | 0 | 0
CE330-CE300, 100% OA | 0 | 0 | 0 | 0 | 0 | 0
CE330-CE320, OA-Infl | 0 | 0 | 0 | 0 | 0 | 0
CE340-CE300, 50/50 OA/inf | 0 | 0 | 0 | 0 | 0 | 0
CE330-CE340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300, Overload | 0 | 0 | 0 | 0 | 0 | 0
CE400-CE300, Ec. T Ctrl | 0 | 0 | 0 | 0 | 0 | 0
CE410-CE300, Ec. No Compr. | 0 | 0 | 0 | 0 | 0 | 0
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0
CE430-CE300, Ec. Enth Ctrl | 0 | 0 | 0 | 0 | 0 | 0
CE440-CE300, Ec. Enth Lim | 0 | 0 | 0 | 0 | 0 | 0
CE500-CE300, 0%OA | -8316.0984 | -8511 | -8511 | -8233.7654 | -8326.688 | -8241
CE510-CE500, PLR | 1951.1712 | 2262 | 2262 | 2034.3391 | 2001.783 | 2038
CE525-CE520, EDB | -973.4182 | -988 | -986 | -838.7733 | -995.563 | -979
CE530-CE500, Dry Coil | -491.3766 | -536 | -536 | -538.1091 | -502.376 | -522
CE545-CE540, EDB (Dry) | -768.7729 | -757 | -757 | -438.3434 | -761.749 | -787
Condenser Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 353.5115 | 385 | 385 | 0 | 376.338 | 368
CE320-CE300, Infiltration | 346.2767 | 314 | 316 | 0 | 348.379 | 358
CE330-CE300, 100% OA | 383.3254 | 355 | 331 | 0 | 400.994 | 370
CE330-CE320, OA-Infl | 37.0487 | 41 | 15 | 0 | 52.615 | 12
CE340-CE300, 50/50 OA/inf | 376.1148 | 348 | 338 | 0 | 386.061 | 361
CE330-CE340, OA-50/50 | 7.2105 | 7 | -7 | 0 | 14.933 | 9
CE350-CE300, Tstat Set Up | -360.1038 | -436 | -435 | 0 | -357.873 | -353
(CE360-CE300)/4, Overload | 478.1772 | 471 | 469.75 | 0 | 484.9215 | 487.25 | #VALUE!
CE400-CE300, Ec. T Ctrl | -414.0381 | -441 | -437 | 0 | 0 | -421
CE410-CE300, Ec. No Compr. | -406.3054 | -336 | -333 | 0 | 0 | -387
CE420-CE300, Ec. ODB Lim. | -251.8207 | -247 | -206 | 0 | 0 | -208
CE430-CE300, Ec. Enth Ctrl | -340.8327 | -308 | -322 | 0 | 0 | -353
CE440-CE300, Ec. Enth Lim | -218.0552 | -191 | -198 | 0 | 0 | -203
(CE500-CE300)/2, 0%OA | -240.2766 | -163 | -163.5 | 0 | -207.3105 | -173.5 | #VALUE!
(CE510-CE500)/4, PLR | 365.2555 | 383.5 | 383.5 | 0 | 374.718 | 381.5 | #VALUE!
CE525-CE520, EDB | -728.888 | -752 | -750 | 0 | -745.624 | -733
CE530-CE500, Dry Coil | -367.939 | -395 | -395 | 0 | -376.185 | -391
CE545-CE540, EDB (Dry) | -575.6512 | -606 | -606 | 0 | -570.545 | -589
Table B16.5.2-19. Delta Annual Cooling Coil Loads | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Coil Load (kWh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | -405.371 | 504.132 | 507.9423 | -26.7995 | -24.393 | -108
CE320-CE300, Infiltration | 6197.4569 | 6900.1602 | 6942.0735 | 6791.4957 | 6799.339 | 7543
CE330-CE300, 100% OA | 6421.6281 | 7514.2047 | 7522.9977 | 8526.6982 | 7439.994 | 6631
CE330-CE320, OA-Infl | 224.1712 | 614.0445 | 580.9242 | 1735.2025 | 640.655 | -912
CE340-CE300, 50/50 OA/inf | 6370.8576 | 7256.5698 | 7305.8106 | 7633.8781 | 7171.095 | 6215
CE330-CE340, OA-50/50 | 50.7704 | 257.6349 | 217.1871 | 892.82 | 268.899 | 416
CE350-CE300, Tstat Set Up | -1572.7295 | -2028.1055 | -2032.0623 | -1676.7363 | -1655.1658 | -1605.75 | #VALUE!
(CE360-CE300)/4, Overload | 19578.7717 | 19780.7328 | 19783.7371 | 20008.8096 | 19749.0605 | 19876.5 | #VALUE!
CE400-CE300, Ec. T Ctrl | -14709.3889 | -14377.7274 | -14367.762 | -14564.2107 | 0 | -14010
CE410-CE300, Ec. No Compr. | -10985.1029 | -8138.2146 | -8144.9559 | 0 | 0 | -9606
CE420-CE300, Ec. ODB Lim. | -6271.9238 | -6130.7727 | -5192.5596 | -5728.0295 | 0 | -5207
CE430-CE300, Ec. Enth Ctrl | -8798.4022 | -8065.5258 | -8350.7121 | -8513.3758 | 0 | -9048
CE440-CE300, Ec. Enth Lim | -5785.676 | -5204.2836 | -5312.7306 | -5191.7822 | 0 | -5406
CE500-CE300, 0%OA | -11617.9484 | -8147.0076 | -8158.7316 | -7760.7172 | -10335.24 | -7661
(CE510-CE500)/4, PLR | 10761.5494 | 11427.5293 | 11427.4561 | 11272.6881 | 10762.7085 | 11270.75 | #VALUE!
CE525-CE520, EDB | -130.6037 | -883.9896 | -882.231 | -1056.6213 | -201.619 | -949
CE530-CE500, Dry Coil | 2.048 | -1076.2632 | -1075.9701 | -546.8842 | 0 | -528
CE545-CE540, EDB (Dry) | -130.4955 | -808.6629 | -808.6629 | -676.1559 | -201.642 | -792
Latent Coil Load(kWh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 19320.6351 | 19607.2176 | 19612.2003 | 19156.4402 | 19575.693 | 19111
CE320-CE300, Infiltration | 13167.3536 | 12172.7361 | 12259.2006 | 11974.1143 | 12597.449 | 11157
CE330-CE300, 100% OA | 18164.3759 | 15932.3298 | 16178.5338 | 16366.7125 | 18528.23 | 17119
CE330-CE320, OA-Infl | 4997.0223 | 3759.5937 | 3919.3332 | 4392.5982 | 5930.781 | 5962
CE340-CE300, 50/50 OA/inf | 15930.2538 | 14487.6399 | 14625.3969 | 14756.6878 | 15760.481 | 15279
CE330-CE340, OA-50/50 | 2234.1221 | 1444.6899 | 1553.1369 | 1610.0247 | 2767.749 | 1840
CE350-CE300, Tstat Set Up | -4747.9518 | -5434.6602 | -5529.0384 | -4820.6365 | -4263.749 | -4446
CE360-CE300, Overload | 4232.1084 | 3400.8393 | 3426.9252 | 3895.2567 | 4459.339 | 4403
CE400-CE300, Ec. T Ctrl | 3075.3436 | 2011.8384 | 2100.9408 | 2660.1023 | 0 | 2650
CE410-CE300, Ec. No Compr. | -768.9108 | -2365.6101 | -2303.4729 | 0 | 0 | -2477
CE420-CE300, Ec. ODB Lim. | -1545.6363 | -1541.706 | -1217.2443 | -1240.4535 | 0 | -1212
CE430-CE300, Ec. Enth Ctrl | -1872.1533 | -1577.1711 | -1721.9625 | -1663.2215 | 0 | -2010
CE440-CE300, Ec. Enth Lim | -929.828 | -699.0435 | -798.1113 | -708.8605 | 0 | -823
CE500-CE300, 0%OA | -5451.8128 | -3140.5665 | -3140.8596 | -3986.0493 | -4304.002 | -4983
CE510-CE500, PLR | 17484.6814 | 17615.0169 | 17615.0169 | 17347.6038 | 17488.438 | 17340
CE525-CE520, EDB | 2.0047 | -288.1173 | -288.1173 | -57.8538 | -8.624 | -42
CE530-CE500, Dry Coil | -18313.3062 | -18285.3366 | -18285.6297 | -18079.9419 | -18229.955 | -18084
CE545-CE540, EDB (Dry) | -0.97976 | -81.4818 | -81.4818 | -8.5582 | -3.086 | -2
Table B16.5.2-20. Delta Various Annual Means (COP2, IDB) | 0 | 0 | 0 | 0 | 0 | 0 | 0
COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0.16552 | 0.1798 | 0.18013 | 0.15538 | 0.17086 | 0.15
CE320-CE300, Infiltration | 0.17083 | 0.22029 | 0.21969 | 0.16788 | 0.17958 | 0.16
CE330-CE300, 100% OA | 0.24166 | 0.25649 | 0.29907 | 0.25338 | 0.2709 | 0.23
CE330-CE320, OA-Infl | 0.070831 | 0.036201 | 0.079382 | 0.085508 | 0.091321 | 0.07
CE340-CE300, 50/50 OA/inf | 0.20521 | 0.23966 | 0.25826 | 0.21034 | 0.22316 | 0.19
CE330-CE340, OA-50/50 | 0.036452 | 0.016833 | 0.040815 | 0.043047 | 0.047744 | 0.04
CE350-CE300, Tstat Set Up | -0.00011501 | 0.003096 | -0.0019178 | 0.0063283 | 0.0025325 | 0
CE360-CE300, Overload | 0.41996 | 0.46293 | 0.46845 | 0.4406 | 0.44031 | 0.43
CE400-CE300, Ec. T Ctrl | 0.0012106 | 0.013724 | 0.014548 | 0.0089602 | 0 | 0.03
CE410-CE300, Ec. No Compr. | -0.0095511 | -0.025269 | -0.026661 | 0 | 0 | -0.02
CE420-CE300, Ec. ODB Lim. | -0.023 | -0.022394 | -0.019831 | -0.02108 | 0 | -0.02
CE430-CE300, Ec. Enth Ctrl | -0.02827 | -0.024649 | -0.025889 | -0.026368 | 0 | -0.02
CE440-CE300, Ec. Enth Lim | -0.017725 | -0.015393 | -0.015474 | -0.015876 | 0 | -0.01
CE500-CE300, 0%OA | -0.045013 | -0.010183 | -0.010822 | -0.024005 | -0.034365 | -0.03
CE510-CE500, PLR | 0.40948 | 0.41598 | 0.41577 | 0.40797 | 0.39713 | 0.41
CE525-CE520, EDB | 0.58247 | 0.57414 | 0.57204 | 0.50377 | 0.60629 | 0.49
CE530-CE500, Dry Coil | -0.24223 | -0.25849 | -0.25718 | -0.21398 | -0.27645 | -0.22
CE545-CE540, EDB (Dry) | 0.5601 | 0.55853 | 0.56036 | 0.33359 | 0.54604 | 0.51
IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0.1313 | 0.055556 | 0 | 0.0013565 | 0.0080616 | 0.02
CE320-CE300, Infiltration | 0.27622 | 0.33333 | 0.33333 | 0.16367 | 0.24571 | 0.54
CE330-CE300, 100% OA | 0.25545 | 0.22222 | 0.22222 | 0.18266 | 0.21382 | 0.19
CE330-CE320, OA-Infl | -0.02077 | -0.11111 | -0.11111 | 0.018995 | -0.031885 | -0.35
CE340-CE300, 50/50 OA/inf | 0.25135 | 0.22222 | 0.22222 | 0.20752 | 0.22722 | 0.22
CE330-CE340, OA-50/50 | 0.0041016 | 0 | 0 | -0.024858 | -0.013394 | -0.03
CE350-CE300, Tstat Set Up | 2.0352 | 2.1111 | 2.1111 | 2.1509 | 2.187 | 2.16
CE360-CE300, Overload | 1.7407 | 1.5556 | 1.5 | 1.2324 | 1.3992 | 1.38
CE400-CE300, Ec. T Ctrl | 0.50202 | 0 | 0 | 0.0012363 | 0 | 0
CE410-CE300, Ec. No Compr. | 0.49787 | 0 | 0 | 0 | 0 | 0
CE420-CE300, Ec. ODB Lim. | 0.3019 | 0 | 0 | -9.3106e-05 | 0 | 0
CE430-CE300, Ec. Enth Ctrl | 0.36731 | 0 | 0 | -0.00010336 | 0 | 0
CE440-CE300, Ec. Enth Lim | 0.2875 | 0 | 0 | -5.3781e-05 | 0 | 0
CE500-CE300, 0%OA | -3.3901 | -3.3889 | -3.5 | -3.7113 | -2.9838 | -1.13
CE510-CE500, PLR | 1.2445 | 0.11111 | 0.11111 | -0.022745 | 0 | 0
CE525-CE520, EDB | 13.3272 | 13.6111 | 13.5556 | 13.5272 | 13.6289 | 15.8
CE530-CE500, Dry Coil | -0.20888 | -0.055556 | 0 | 0.20651 | 0 | 0
CE545-CE540, EDB (Dry) | 13.3159 | 13.5556 | 13.5556 | 13.5189 | 13.576 | 15.71
Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0.0020018 | 0.0021 | 0.0021 | 0.0019746 | 0.0019998 | 0.0019
CE320-CE300, Infiltration | 0.00091896 | 0.0009 | 0.0009 | 0.00082797 | 0.00087438 | 0.0007
CE330-CE300, 100% OA | 0.00067186 | 0.0007 | 0.0007 | 0.0006823 | 0.00063678 | 0.0007
CE330-CE320, OA-Infl | -0.00024709 | -0.0002 | -0.0002 | -0.00014568 | -0.00023759 | 0
CE340-CE300, 50/50 OA/inf | 0.00072232 | 0.0007 | 0.0007 | 0.00069759 | 0.00069351 | 0.0007
CE330-CE340, OA-50/50 | -5.0461e-05 | 0 | 0 | -1.5289e-05 | -5.6729e-05 | 0
CE350-CE300, Tstat Set Up | 0.00063685 | 0.0008 | 0.0008 | 0.00063956 | 0.00058373 | 0.00057
CE360-CE300, Overload | -0.0005696 | -0.0005 | -0.0005 | -0.00052024 | -0.00062237 | -0.00062
CE400-CE300, Ec. T Ctrl | 0.00073206 | 0.0008 | 0.0008 | 0.00080072 | 0 | 0.0008
CE410-CE300, Ec. No Compr. | 0.00067139 | 0.0003 | 0.0003 | 0 | 0 | 0.0003
CE420-CE300, Ec. ODB Lim. | 0.00019481 | 0.0002 | 0.0002 | 0.00016242 | 0 | 0.0001
CE430-CE300, Ec. Enth Ctrl | 0.00024119 | 0.0002 | 0.0002 | 0.00020337 | 0 | 0.0002
CE440-CE300, Ec. Enth Lim | 8.8738e-05 | 0.0001 | 0.0001 | 4.8002e-05 | 0 | 0
CE500-CE300, 0%OA | 0.00070622 | 0 | 0 | 8.6686e-05 | 0.0010435 | 0.0015
CE510-CE500, PLR | 0.00037457 | 0 | 0 | 7.3411e-06 | -8.8998e-07 | 0
CE525-CE520, EDB | 0.0070203 | 0 | 0 | 0.0077564 | 0.0069569 | 0.00747
CE530-CE500, Dry Coil | -0.0035488 | 0 | 0 | -0.0026606 | -0.0044208 | -0.00403
CE545-CE540, EDB (Dry) | 0.0017664 | 0 | 0 | 0.0023868 | 0.0028945 | 0.00259
Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 9.7158 | 10.25 | 10.25 | 9.9598 | 10.0148 | 9.87
CE320-CE300, Infiltration | 3.3904 | 2.95 | 2.97 | 3.2494 | 3.2773 | 2.01
CE330-CE300, 100% OA | 2.2296 | 2.32 | 2.37 | 2.5851 | 2.2587 | 2.77
CE330-CE320, OA-Infl | -1.1608 | -0.63 | -0.6 | -0.66425 | -1.0186 | 0.76
CE340-CE300, 50/50 OA/inf | 2.4702 | 2.43 | 2.45 | 2.5566 | 2.4705 | 2.85
CE330-CE340, OA-50/50 | -0.24056 | -0.11 | -0.08 | 0.028551 | -0.21187 | -0.08
CE350-CE300, Tstat Set Up | -3.1309 | -2.81 | -2.73 | -3.4182 | -3.5099 | -3.37
CE360-CE300, Overload | -7.5814 | -6.77 | -6.79 | -6.2219 | -6.9551 | -6.72
CE400-CE300, Ec. T Ctrl | 2.156 | 3.95 | 3.97 | 3.9572 | 0 | 4.08
CE410-CE300, Ec. No Compr. | 1.8822 | 1.39 | 1.35 | 0 | 0 | 1.82
CE420-CE300, Ec. ODB Lim. | 0.16451 | 0.88 | 0.69 | 0.80676 | 0 | 0.83
CE430-CE300, Ec. Enth Ctrl | 0.20708 | 0.91 | 1.02 | 1.0089 | 0 | 1.24
CE440-CE300, Ec. Enth Lim | -0.28509 | 0.2 | 0.29 | 0.23749 | 0 | 0.3
CE500-CE300, 0%OA | 17.9113 | 0 | 0 | 10.6062 | 18.1158 | 15.8
CE510-CE500, PLR | -2.3476 | 0 | 0 | 0.11417 | -0.010621 | 0.11
CE525-CE520, EDB | -8.4071 | 0 | 0 | -6.4105 | -10.0881 | -14.8
CE530-CE500, Dry Coil | -19.7962 | 0 | 0 | -10.2243 | -24.4903 | -24.13
CE545-CE540, EDB (Dry) | -11.8961 | 0 | 0 | -7.6766 | -3.1763 | -14.62
Table B16.5.2-22. Delta Hourly Integrated Maximum Total Consumptions | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Consumption (Wh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 968.3645 | 1019 | 993 | 640.9591 | 721 | 614
CE320-CE300, Infiltration | 1402.1615 | 1352 | 1379 | 1054.567 | 1172 | 1327
CE330-CE300, 100% OA | 1720.664 | 1648 | 1805 | 1414.2502 | 1535 | 1787
CE330-CE320, OA-Infl | 318.5024 | 296 | 426 | 359.6832 | 363 | 460
CE340-CE300, 50/50 OA/inf | 1554.8648 | 1594 | 1588 | 1234.3106 | 1345 | 1553
CE330-CE340, OA-50/50 | 165.7992 | 54 | 217 | 179.9396 | 190 | 234
CE350-CE300, Tstat Set Up | 0.85194 | 90 | 0 | 0.0021837 | 0 | -2
CE360-CE300, Overload | 1143.4651 | 1172 | 1124 | 844.4186 | 931 | 1214
CE400-CE300, Ec. T Ctrl | 1.8307 | 0 | 75 | -1.7556e-06 | 0 | -29
CE410-CE300, Ec. No Compr. | 1.8307 | 0 | 0 | 0 | 0 | 1
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0
CE430-CE300, Ec. Enth Ctrl | 0 | 0 | 0 | -1.0004e-10 | 0 | 0
CE440-CE300, Ec. Enth Lim | 0 | 0 | 0 | 0 | 0 | -87
CE500-CE300, 0%OA | -1459.5539 | -1133 | -1177 | -1501.1724 | -1755 | -1274
CE510-CE500, PLR | 1038.4136 | 1159 | 1162 | 1011.1162 | 1009 | 1070
CE525-CE520, EDB | -1668.6417 | -1451 | -1483 | -1530.9547 | -1625 | -1099
CE530-CE500, Dry Coil | -2138.1546 | -2372 | -2370 | -2227.6394 | -2185 | -2185
CE545-CE540, EDB (Dry) | -1494.1291 | -1593 | -1593 | -914.6465 | -1495 | -1514
Sensible + Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 5153.95 | 5349 | 5578 | 4393.2239 | 4759 | 4919
CE320-CE300, Infiltration | 8143.55 | 22412 | 22368 | 7031.9273 | 7402 | 7848
CE330-CE300, 100% OA | 11317.95 | 12227 | 33117 | 10711.8252 | 11476 | 10343
CE330-CE320, OA-Infl | 3174.4 | -10185 | 10749 | 3679.898 | 4074 | 2495
CE340-CE300, 50/50 OA/inf | 9477.65 | 19418 | 28094 | 8595.018 | 8864 | 9060
CE330-CE340, OA-50/50 | 1840.3 | -7191 | 5023 | 2116.8072 | 2612 | 1283
CE350-CE300, Tstat Set Up | -82.32 | 0 | -1 | 0.0093743 | 0 | 5
CE360-CE300, Overload | 6683.11 | 9212 | 9564 | 5726.4726 | 5820 | 6379
CE400-CE300, Ec. T Ctrl | 9004.55 | 9142 | 18383 | 7994.8866 | 0 | 8702
CE410-CE300, Ec. No Compr. | -82.32 | 0 | 0 | 0 | 0 | 1
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0
CE430-CE300, Ec. Enth Ctrl | 0 | 0 | 0 | -5.5297e-10 | 0 | 0
CE440-CE300, Ec. Enth Lim | 0 | 0 | 0 | -2.7649e-10 | 0 | -295
CE500-CE300, 0%OA | -4688.54 | -3694 | -3749 | -5086.83 | -5935 | -4517
CE510-CE500, PLR | 3107.54 | 3481 | 3482 | 3531.3254 | 3381 | 3542
CE525-CE520, EDB | 410.17 | -412 | -412 | -76.1817 | 8 | -881
CE530-CE500, Dry Coil | -7651.41 | -8131 | -8131 | -8007.6599 | -7791 | -7929
CE545-CE540, EDB (Dry) | 500.2 | -291 | -292 | -186.6119 | -30 | -302
Sensible Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | -183.1 | -123 | -86 | -254.3484 | -379 | -259
CE320-CE300, Infiltration | 8038.2 | 7916 | 7867 | 8441.2775 | 7677 | 8059
CE330-CE300, 100% OA | 9948.7 | 10207 | 11285 | 11233.9719 | 10540 | 10513
CE330-CE320, OA-Infl | 1910.5 | 2291 | 3418 | 2792.6945 | 2863 | 2454
CE340-CE300, 50/50 OA/inf | 9551.5 | 8883 | 8881 | 9356.9768 | 9483 | 9272
CE330-CE340, OA-50/50 | 397.2 | 1324 | 2404 | 1876.9952 | 1057 | 1241
CE350-CE300, Tstat Set Up | 0.1 | 0 | 0 | -0.00037974 | 0 | -32
CE360-CE300, Overload | 8783.3 | 8908 | 8860 | 9090.1056 | 8524 | 9271
CE400-CE300, Ec. T Ctrl | 0.1 | 0 | 0 | -7.3683e-06 | 0 | -31
CE410-CE300, Ec. No Compr. | -11.7 | 0 | 0 | 0 | 0 | -15
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | -2.9104e-11 | 0 | -15
CE430-CE300, Ec. Enth Ctrl | 0 | 0 | 0 | -4.1473e-10 | 0 | -15
CE440-CE300, Ec. Enth Lim | 0 | 0 | 0 | -1.6371e-10 | 0 | -33
CE500-CE300, 0%OA | -3728.2 | -3194 | -3197 | -3681.5174 | -4681 | -3090
CE510-CE500, PLR | 2180 | 2504 | 2505 | 2441.0216 | 2345 | 2451
CE525-CE520, EDB | 286.8 | -309 | -304 | -335.6215 | -210 | -717
CE530-CE500, Dry Coil | 284.9 | -433 | -433 | -210.5244 | 0 | -192
CE545-CE540, EDB (Dry) | 500.2 | -291 | -292 | -186.6119 | -35 | -302
Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 6271.3 | 5835 | 5876 | 6040.0162 | 5737 | 5685
CE320-CE300, Infiltration | 13511.6 | 22193 | 22109 | 11960.6494 | 11322 | 11537
CE330-CE300, 100% OA | 18189.5 | 17637 | 31415 | 16899.4932 | 17809 | 17096
CE330-CE320, OA-Infl | 4677.9 | -4556 | 9306 | 4938.8437 | 6487 | 5559
CE340-CE300, 50/50 OA/inf | 15212.6 | 21147 | 26617 | 13676.4198 | 13850 | 13402
CE330-CE340, OA-50/50 | 2976.9 | -3510 | 4798 | 3223.0734 | 3959 | 3694
CE350-CE300, Tstat Set Up | 115.56 | -1 | -1 | 0.53144 | 380 | 1211
CE360-CE300, Overload | -360.54 | 722 | 942 | -1714.5041 | -1516 | -1458
CE400-CE300, Ec. T Ctrl | 17439.6 | 16274 | 23002 | 16082.4601 | 0 | 16253
CE410-CE300, Ec. No Compr. | 1503.2 | 0 | -3 | 0 | 0 | -15
CE420-CE300, Ec. ODB Lim. | 115.34 | 0 | 0 | -5.6389e-11 | 0 | 2
CE430-CE300, Ec. Enth Ctrl | 0 | 1801 | 1707 | 838.9522 | 0 | 2
CE440-CE300, Ec. Enth Lim | 0 | 0 | -3 | -2.9104e-11 | 0 | -253
CE500-CE300, 0%OA | -1670.24 | -1571 | -1661 | -2396.1014 | -2570 | -2630
CE510-CE500, PLR | 927.1 | 990 | 990 | 1116.0715 | 1045 | 1112
CE525-CE520, EDB | 123.37 | -122 | -122 | 248.8578 | 212 | -144
CE530-CE500, Dry Coil | -7965.46 | -7733 | -7733 | -7837.6616 | -7626 | -7726.1
CE545-CE540, EDB (Dry) | -627.186 | 0 | 0 | -1654.9514 | -841 | -1181
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Table B16.5.2-25. Delta Hourly Integrated Maximum and Minimum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | -0.025037 | 0.272 | 0.271 | 0.2477 | 0.25703 | 0.24
CE320-CE300, Infiltration | 0 | 1.274 | 1.11 | 0.014298 | 0.072694 | 0.5
CE330-CE300, 100% OA | 0 | 0.24 | 1.738 | 0.14626 | 0.25134 | 0.17
CE330-CE320, OA-Infl | 0 | -1.034 | 0.628 | 0.13196 | 0.17864 | -0.33
CE340-CE300, 50/50 OA/inf | 0 | 0.752 | 1.482 | 0.061376 | 0.14655 | 0.07
CE330-CE340, OA-50/50 | 0 | -0.512 | 0.256 | 0.084885 | 0.10479 | 0.1
CE350-CE300, Tstat Set Up | 0 | 0.02 | 0.006 | 0.63002 | 0.061488 | 0
CE360-CE300, Overload | 0.23263 | 0.559 | 0.57 | 0.53014 | 0.5614 | 0.56
CE400-CE300, Ec. T Ctrl | -0.091398 | 0.219 | 0.919 | 0.14625 | 0 | 0.17
CE410-CE300, Ec. No Compr. | -0.28043 | 0.034 | -0.002 | 0 | 0 | -0.04
CE420-CE300, Ec. ODB Lim. | -0.38705 | -0.062 | -0.098 | -0.10384 | 0 | 0.06
CE430-CE300, Ec. Enth Ctrl | -0.38705 | -0.064 | -0.098 | -0.13253 | 0 | 0.05
CE440-CE300, Ec. Enth Lim | -0.28486 | -0.095 | -0.098 | -0.12338 | 0 | -0.07
CE500-CE300, 0%OA | 0.1068 | 3.498 | 1.444 | 0.27276 | 0.31401 | 0.26
CE510-CE500, PLR | 0.4174 | 0 | 0 | 0.48669 | 0.50496 | 0.39
CE525-CE520, EDB | 0.90402 | 1.429 | 1.379 | 0.76636 | 0.83633 | 0.56
CE530-CE500, Dry Coil | -0.26907 | -3.386 | -1.451 | -0.27296 | -0.34458 | -0.26
CE545-CE540, EDB (Dry) | 0.79448 | 0.819 | 0.973 | 0.47021 | 0.48982 | 0.48
Minimum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0.072169 | 0.052 | 0.05 | 0.11113 | 0.087015 | 0.06
CE320-CE300, Infiltration | 0.032137 | 0.003 | 0.004 | 0.059984 | 0.028893 | 0.02
CE330-CE300, 100% OA | 0.032137 | 0 | 0 | 0.062559 | 0.037696 | 0.03
CE330-CE320, OA-Infl | 0 | -0.003 | -0.004 | 0.0025756 | 0.0088028 | 0.01
CE340-CE300, 50/50 OA/inf | 0.032137 | 0 | 0 | 0.062559 | 0.037696 | 0.03
CE330-CE340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300, Tstat Set Up | -0.0026372 | 0 | 0 | -4.2544e-07 | 0.00027963 | 0
CE360-CE300, Overload | 0.032137 | 0.001 | 0 | 0.062561 | 0.037696 | 0.03
CE400-CE300, Ec. T Ctrl | -0.011155 | -0.064 | -0.066 | -3.9918e-07 | 0 | 0
CE410-CE300, Ec. No Compr. | -0.0072339 | 0 | 0 | 0 | 0 | 0
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0
CE430-CE300, Ec. Enth Ctrl | -0.021929 | -0.064 | -0.066 | 0 | 0 | 0
CE440-CE300, Ec. Enth Lim | -0.010585 | -0.064 | -0.066 | -4.885e-15 | 0 | 0
CE500-CE300, 0%OA | -0.10787 | -0.105 | -0.149 | -0.076073 | -0.11916 | -0.1
CE510-CE500, PLR | 0.20276 | 0.124 | 0 | 0.15983 | 0.21527 | 0.19
CE525-CE520, EDB | 0.46939 | 0.476 | 0.42 | 0.40795 | 0.56074 | 0.43
CE530-CE500, Dry Coil | -0.18393 | -0.198 | -0.154 | -0.1735 | -0.19318 | -0.19
CE545-CE540, EDB (Dry) | 0.4795 | 0.459 | 0.46 | 0.27714 | 0.54916 | 0.44
Table B16.5.2-26. Delta Hourly Integrated Maximum and Minimum IDB | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0.8779 | 1.78 | 1.61 | 1.4722 | 1.57 | 1
CE320-CE300, Infiltration | 6.1605 | 6.5 | 6.39 | 6.7065 | 7.27 | 5.46
CE330-CE300, 100% OA | 6.0322 | 6.61 | 6.89 | 6.0662 | 6.85 | 5.11
CE330-CE320, OA-Infl | -0.1283 | 0.11 | 0.5 | -0.64028 | -0.42 | -0.35
CE340-CE300, 50/50 OA/inf | 6.1067 | 6.5 | 6.45 | 6.4953 | 7.1 | 5.39
CE330-CE340, OA-50/50 | -0.0745 | 0.11 | 0.44 | -0.4291 | -0.25 | -0.28
CE350-CE300, Tstat Set Up | 8.3842 | 9.83 | 9.83 | 9.9997 | 9.95 | 8.81
CE360-CE300, Overload | 7.5586 | 7.67 | 7.45 | 7.5081 | 7.95 | 6.94
CE400-CE300, Ec. T Ctrl | 0.9149 | 2.45 | 3.72 | 1.9074 | 0 | -0.15
CE410-CE300, Ec. No Compr. | 0.6257 | 0 | 0 | 0 | 0 | 0
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | -1.5401e-11 | 0 | 0.04
CE430-CE300, Ec. Enth Ctrl | 0.9993 | 0 | 0 | 0.00056794 | 0 | 0.26
CE440-CE300, Ec. Enth Lim | 0.8453 | 0 | 0 | 0.00049509 | 0 | 0.07
CE500-CE300, 0%OA | -0.3945 | 0 | 0 | -0.0026447 | -0.03 | -1.19
CE510-CE500, PLR | 0.2949 | 0 | 0 | -2.2958e-08 | 0 | 0
CE525-CE520, EDB | 19.9568 | 18.95 | 19.12 | 19.999 | 19.02 | 16.38
CE530-CE500, Dry Coil | 0.3106 | -0.05 | -0.05 | 0.00043309 | 0 | 0
CE545-CE540, EDB (Dry) | 19.525 | 19.89 | 19.89 | 19.9995 | 19.95 | 20
Minimum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0 | 0 | 0 | -0.00012889 | 0 | 0
CE320-CE300, Infiltration | 0 | 1.94 | 1.95 | -0.9638 | 0 | 0
CE330-CE300, 100% OA | 0 | 0 | 0 | -0.0015681 | 0 | 0
CE330-CE320, OA-Infl | 0 | -1.94 | -1.95 | 0.96224 | 0 | 0
CE340-CE300, 50/50 OA/inf | 0 | 0 | 0 | -0.0015681 | 0 | 0
CE330-CE340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300, Overload | 0 | 0 | 0 | 0.00017983 | 0 | 0
CE400-CE300, Ec. T Ctrl | 0 | 0 | 0 | -3.0198e-14 | 0 | 0
CE410-CE300, Ec. No Compr. | 0 | 0 | 0 | 0 | 0 | 0
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | -3.0198e-14 | 0 | 0
CE430-CE300, Ec. Enth Ctrl | 0 | 0 | 0 | -3.0198e-14 | 0 | 0
CE440-CE300, Ec. Enth Lim | 0 | 0 | 0 | -3.0198e-14 | 0 | 0.01
CE500-CE300, 0%OA | 0.49703 | -0.72 | -0.89 | 0.22125 | 0.54 | 17.05
CE510-CE500, PLR | 0 | 0 | 0 | 1.2601e-08 | 0 | 0
CE525-CE520, EDB | 0.13889 | 0.06 | 0.05 | 0.17974 | 0.03 | 19.44
CE530-CE500, Dry Coil | -0.00551 | 0 | 0 | -0.00068516 | 0 | 0
CE545-CE540, EDB (Dry) | 0.22078 | 0.06 | 0.05 | 0.18049 | 0.03 | 18.06
Table B16.5.2-27. Delta Hourly Integrated Maximum and Minimum Zone Humidity Ratio | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0.0024658 | 0.005 | 0.0052 | 0.0020112 | 0.001975 | 0.0023
CE320-CE300, Infiltration | 0.0047326 | 0.0039 | 0.0039 | 0.0041811 | 0.00409 | 0.0043
CE330-CE300, 100% OA | 0.0043671 | 0.004 | 0.004 | 0.0043074 | 0.003588 | 0.0043
CE330-CE320, OA-Infl | -0.0003655 | 0.0001 | 0.0001 | 0.00012627 | -0.000502 | 0
CE340-CE300, 50/50 OA/inf | 0.0045871 | 0.0039 | 0.0037 | 0.0041608 | 0.003815 | 0.0043
CE330-CE340, OA-50/50 | -0.00022 | 0.0001 | 0.0003 | 0.00014662 | -0.000227 | 0
CE350-CE300, Tstat Set Up | 0.0034739 | 0.0061 | 0.0062 | 0.0035636 | 0.003022 | 0.0032
CE360-CE300, Overload | 0.0001491 | 0 | 0 | 0.00023399 | 0 | 0
CE400-CE300, Ec. T Ctrl | 0.0036593 | 0.0032 | 0.0033 | 0.00325 | 0 | 0.0039
CE410-CE300, Ec. No Compr. | 0.0035512 | 0.0031 | 0.0032 | 0 | 0 | 0.0039
CE420-CE300, Ec. ODB Lim. | 0.0010125 | 0.0009 | 0.0004 | 0.00096639 | 0 | 0.0013
CE430-CE300, Ec. Enth Ctrl | 0.0029463 | 0.0018 | 0.0019 | 0.0025083 | 0 | 0.0024
CE440-CE300, Ec. Enth Lim | 2.85e-05 | 0 | 0 | 1.3697e-12 | 0 | 0
CE500-CE300, 0%OA | -0.0015646 | -0.0019 | -0.0019 | -0.0019411 | -0.001744 | -0.0019
CE510-CE500, PLR | 0.0001517 | 0 | 0.0001 | 3.4061e-06 | 3e-06 | 0
CE525-CE520, EDB | 0.010392 | 0.0103 | 0.0102 | 0.011462 | 0.01006 | 0.0067
CE530-CE500, Dry Coil | -0.0047305 | -0.0038 | -0.0037 | -0.0049096 | -0.006222 | -0.00473
CE545-CE540, EDB (Dry) | 0.0009051 | 0.0072 | 0.0059 | 1.8956e-13 | 0.003433 | 0.00129
Minimum Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 1e-08 | 0 | 0 | 1.5608e-05 | 5.1e-05 | -1e-05
CE320-CE300, Infiltration | 0 | 0 | 0 | 5.8672e-06 | 0 | 0
CE330-CE300, 100% OA | 0 | 0 | 0 | -1.7036e-08 | 0 | 0
CE330-CE320, OA-Infl | 0 | 0 | 0 | -5.8842e-06 | 0 | 0
CE340-CE300, 50/50 OA/inf | 0 | 0 | 0 | -1.7036e-08 | 0 | 0
CE330-CE340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300, Overload | 0 | 0 | 0 | -2.2318e-11 | 0 | 0
CE400-CE300, Ec. T Ctrl | 0 | 0 | 0 | 2.2054e-12 | 0 | 0
CE410-CE300, Ec. No Compr. | 0 | 0 | 0 | 0 | 0 | 0
CE420-CE300, Ec. ODB Lim. | 0 | 0 | 0 | -1.2812e-12 | 0 | 0
CE430-CE300, Ec. Enth Ctrl | 0 | 0 | 0 | 2.2054e-12 | 0 | 0
CE440-CE300, Ec. Enth Lim | 0 | 0 | 0 | -1.7443e-12 | 0 | 0
CE500-CE300, 0%OA | 0.0049507 | 0 | 0 | 0.0050771 | 0.00494 | 0.00833
CE510-CE500, PLR | 0 | 0 | 0 | 6.179e-12 | 0 | 0.0002
CE525-CE520, EDB | 0.00073266 | 0 | 0 | 0.00052082 | 0.000384 | 0.00883
CE530-CE500, Dry Coil | -0.00061959 | 0 | 0 | -0.00027005 | -0.001454 | -0.00367
CE545-CE540, EDB (Dry) | 0.0020983 | 0 | 0 | 0.002957 | 0.003432 | 0.0028
Table B16.5.2-28. Delta Hourly Integrated Maximum and Minimum Zone Relative Humidity | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 8.9137 | 30.83 | 31.85 | 10.2766 | 9 | 10.75
CE320-CE300, Infiltration | 13.0466 | 14.06 | 14.82 | 14.5993 | 15 | 14.44
CE330-CE300, 100% OA | 7.8699 | 9.11 | 9.09 | 8.5081 | 8 | 11.26
CE330-CE320, OA-Infl | -5.1767 | -4.95 | -5.73 | -6.0911 | -7 | -3.18
CE340-CE300, 50/50 OA/inf | 11.1401 | 12.02 | 12.41 | 12.4287 | 12 | 12.81
CE330-CE340, OA-50/50 | -3.2702 | -2.91 | -3.32 | -3.9205 | -4 | -1.55
CE350-CE300, Tstat Set Up | 0 | 11.77 | 12.27 | 4.9738e-13 | 2 | 5.21
CE360-CE300, Overload | 0 | 0 | 0 | -0.00016648 | 0 | 0
CE400-CE300, Ec. T Ctrl | 14.9642 | 16.22 | 16.72 | 16.269 | 0 | 18.87
CE410-CE300, Ec. No Compr. | 14.4355 | 15.44 | 15.94 | 0 | 0 | 18.74
CE420-CE300, Ec. ODB Lim. | 2.0519 | 5.16 | 2.68 | 4.9167 | 0 | 6.41
CE430-CE300, Ec. Enth Ctrl | 11.9195 | 9.08 | 9.58 | 12.3754 | 0 | 11.5
CE440-CE300, Ec. Enth Lim | -0.065 | 0 | 0 | 6.6574e-09 | 0 | 0.07
CE500-CE300, 0%OA | 31.2108 | 0 | 0 | 31.6327 | 32 | -7.36
CE510-CE500, PLR | 0 | 0 | 0 | 0 | 0 | -2.57
CE525-CE520, EDB | 9.7701 | 0 | 0 | 6.1863 | 5 | -20.65
CE530-CE500, Dry Coil | -8.9555 | 0 | 0 | -3.8398 | -21 | -24.07
CE545-CE540, EDB (Dry) | 29.6022 | 0 | 0 | 41.0554 | 50 | -15.82
Minimum Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | EnergyPlus | CODYRUN | HOT3000 | Tested Prg
Case | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | EnergyPlus/GARD | CODYRUN/UR | HOT3000/NRCan | Tested Prg
CE310-CE300, Latent Gains | 0.0586 | 0 | 0 | 1.1 | 1 | 0.99
CE320-CE300, Infiltration | 0 | 0 | 0 | 0.23921 | 0 | -2.02
CE330-CE300, 100% OA | 0 | 0 | 0 | 0.00010511 | 0 | 0
CE330-CE320, OA-Infl | 0 | 0 | 0 | -0.23911 | 0 | 2.02
CE340-CE300, 50/50 OA/inf | 0 | 0 | 0 | 0.00010511 | 0 | 0
CE330-CE340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0
CE350-CE300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0
CE360-CE300, Overload | 0 | 0 | 0 | -5.7187e-05 | 0 | 0
CE400-CE300, Ec. T Ctrl | -0.1222 | 0 | 0 | -0.47678 | 0 | -0.37
CE410-CE300, Ec. No Compr. | -0.1221 | 0 | 0 | 0 | 0 | -0.36
CE420-CE300, Ec. ODB Lim. | -0.1213 | 0 | 0 | -0.47665 | 0 | -0.35
CE430-CE300, Ec. Enth Ctrl | -0.1234 | 0 | 0 | -0.47678 | 0 | -0.36
CE440-CE300, Ec. Enth Lim | -0.1243 | 0 | 0 | -0.47678 | 0 | -0.4
CE500-CE300, 0%OA | 40.0742 | 0 | 0 | 40.7644 | 39 | 37.89
CE510-CE500, PLR | -1.3175 | 0 | 0 | 0.12165 | 0 | 0.32
CE525-CE520, EDB | -15.7395 | 0 | 0 | -13.8748 | -17 | -17.5
CE530-CE500, Dry Coil | -23.812 | 0 | 0 | -21.139 | -26 | -19.15
CE545-CE540, EDB (Dry) | -19.3505 | 0 | 0 | -16.7748 | -12 | -19.6
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ] | 0 | 0 | 0 | 0 | 0 | 0 | 0

## TRNSYS-TUD
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
TRNSYS-TUD, received 19 Feb 2003 with revs by jn 20 Feb 2003, and for 5 Apr 2003 results as noted below
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
TRNSYS-TUD, received 19 Feb 2003 with revs by jn 20 Feb 2003, and for 5 Apr 2003 results as noted below
• deleted column J (other COP2 calcs by Thoi), 20 Feb 2003
• column i: recalc COP2 based on spec (annual sum total coil load)/(annual sum compressor + OD fan energy) [previously TUD used average of hourly calculated COP2 when compressor operating; was only slight difference from spec definition]. 20 Feb 2003
• E440 updated for corrected IP to SI psychrometric enthalpy conversion, for 5 Apr 2003 results
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 35633.7773 | 22353.5343 | 2400.3229 | 10879.92 | 80426.8675 | 56661.7484 | 23765.119 | 3.2491 | 23.6243 | 0.0090691 | 48.6149 | 19.9145 | 0.011643 | E300 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9635.7 | 03-Sep | 16 | 32174.05 | 08-Jul | 15 | 34.7 | 20-Jul | 15 | 0.021878 | 02-Oct | 9
E310 | 39973.3798 | 26339.6254 | 2753.8345 | 10879.92 | 99342.1316 | 56256.3775 | 43085.7541 | 3.4146 | 23.7556 | 0.011071 | 58.3307 |  |  | E310 | 12594.4016 | 20-Jul | 15 | 23094.3 | 10-Sep | 15 | 15907 | 03-Sep | 15 | 37328 | 03-Sep | 15
E320 | 40059.657 | 26433.1374 | 2746.5996 | 10879.92 | 99791.678 | 62859.2053 | 36932.4726 | 3.4199 | 23.9005 | 0.009988 | 52.0053 |  |  | E320 | 13028.1986 | 20-Jul | 15 | 31315.6 | 24-Apr | 16 | 23147.3 | 02-Oct | 10 | 40317.6 | 03-Sep | 16
E330 | 40963.3004 | 27299.7321 | 2783.6483 | 10879.92 | 105012.8715 | 63083.3765 | 41929.495 | 3.4907 | 23.8797 | 0.0097409 | 50.8445 |  |  | E330 | 13346.701 | 20-Jul | 15 | 33226.1 | 14-Jun | 14 | 27825.2 | 18-Sep | 16 | 43492 | 02-Oct | 9
E340 | 40619.2951 | 26962.9373 | 2776.4378 | 10879.92 | 102727.9789 | 63032.6061 | 39695.3729 | 3.4543 | 23.8756 | 0.0097914 | 51.085 |  |  | E340 | 13180.9018 | 20-Jul | 15 | 32828.9 | 24-Apr | 15 | 24848.3 | 02-Oct | 9 | 41651.7 | 02-Oct | 10
E350 | 32236.9795 | 19316.8404 | 2040.2191 | 10879.92 | 69387.9976 | 50370.8304 | 19017.1672 | 3.2489 | 25.6595 | 0.0097059 | 45.484 |  |  | E350 | 11626.889 | 20-Jul | 15 | 23277.5 | 29-Jul | 15 | 9751.26 | 01-Oct | 13 | 32091.73 | 08-Jul | 15
E360 | 55298.7917 | 40105.8399 | 4313.0318 | 10879.92 | 162974.0626 | 134976.8351 | 27997.2274 | 3.669 | 25.3649 | 0.0084995 | 41.0335 |  |  | E360 | 12769.5022 | 20-Jul | 15 | 32060.7 | 24-Apr | 16 | 9275.16 | 02-Oct | 10 | 38857.16 | 02-Oct | 10
E400 | 32045.1536 | 19178.9487 | 1986.2848 | 10879.92 | 68792.8221 | 41952.3595 | 26840.4626 | 3.2503 | 24.1263 | 0.0098011 | 50.7709 |  |  | E400 | 11627.8677 | 20-Jul | 15 | 23277.5 | 29-Jul | 15 | 27075.3 | 16-Sep | 15 | 41178.6 | 16-Sep | 15
E410 | 32078.4319 | 19204.4944 | 1994.0175 | 10879.92 | 68672.8538 | 45676.6456 | 22996.2083 | 3.2395 | 24.1221 | 0.0097405 | 50.4971 |  |  | E410 | 11627.8677 | 20-Jul | 15 | 23265.7 | 10-Sep | 16 | 11138.9 | 16-Sep | 15 | 32091.73 | 08-Jul | 15
E420 | 33387.0076 | 20358.5854 | 2148.5022 | 10879.92 | 72609.3074 | 50389.8247 | 22219.4827 | 3.2261 | 23.9262 | 0.0092639 | 48.7794 |  |  | E420 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9751.04 | 01-Oct | 13 | 32174.05 | 08-Jul | 15
E430 | 32538.0313 | 19598.6211 | 2059.4903 | 10879.92 | 69756.312 | 47863.3462 | 21892.9657 | 3.2208 | 23.9916 | 0.0093103 | 48.8219 |  |  | E430 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9635.7 | 03-Sep | 16 | 32174.05 | 08-Jul | 15
E440 | 33691.321 | 20629.1333 | 2182.2678 | 10879.92 | 73711.3635 | 50876.0725 | 22835.291 | 3.2313 | 23.9118 | 0.0091578 | 48.3298 |  |  | E440 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9635.7 | 03-Sep | 16 | 32174.05 | 08-Jul | 15
E500 | 22337.887 | 17854.2956 | 1919.7698 | 2563.8216 | 63357.1063 | 45043.8 | 18313.3062 | 3.2041 | 20.2342 | 0.0097753 | 66.5261 |  |  | E500 | 10166.4831 | 20-Jul | 15 | 19549.2 | 28-Oct | 15 | 7965.46 | 06-Oct | 15 | 27485.51 | 28-Oct | 15
E500 May-Sep | 17390.8511 | 13942.1479 | 1476.6547 | 1972.0485 | 48443.4308 | 34443.2344 | 14000.1964 | 3.1418 | 24.5723 | 0.011021 | 57.0476 |  |  | E510 | 11204.8968 | 20-Jul | 15 | 21729.2 | 29-Apr | 19 | 8892.56 | 15-Sep | 11 | 30593.05 | 29-Apr | 19
E510 May-Sep | 34608.7754 | 27747.879 | 2937.6766 | 3923.2198 | 108974.3099 | 77489.4321 | 31484.8778 | 3.5513 | 25.8168 | 0.011395 | 54.7001 |  |  | E520 | 11035.3898 | 20-Jul | 15 | 19415.9 | 28-Sep | 15 | 7913.7 | 28-Sep | 15 | 27329.6 | 28-Sep | 15
E520 | 24986.582 | 19521.2767 | 2340.1169 | 3125.1884 | 63421.5444 | 45109.6141 | 18311.9303 | 2.9011 | 13.5171 | 0.0066924 | 69.8745 |  |  | E522 | 10430.7791 | 20-Jul | 15 | 19488.8 | 12-Mai | 15 | 7906.7 | 02-Mai | 15 | 27383.59 | 12-Mai | 15
E522 | 23544.1607 | 18620.3108 | 2108.2783 | 2815.5716 | 63389.2228 | 45076.0312 | 18313.1916 | 3.0581 | 16.9456 | 0.0081904 | 68.6774 |  |  | E525 | 9366.7481 | 20-Jul | 15 | 19702.7 | 26-Jul | 16 | 8037.07 | 26-Jul | 16 | 27739.77 | 26-Jul | 16
E525 | 20320.874 | 16557.8748 | 1611.2289 | 2151.7702 | 63292.9454 | 44979.0103 | 18313.9351 | 3.4835 | 26.8443 | 0.013713 | 61.4674 |  |  | E530 | 8028.3285 | 20-Jul | 15 | 19834.1 | 29-Mai | 15 | 1.6431e-11 | 18-Jun | 16 | 19834.1 | 29-Mai | 15
E530 | 17281.271 | 13656.9951 | 1551.8309 | 2072.4451 | 45045.848 | 45045.848 | 0 | 2.9618 | 20.0253 | 0.0062265 | 46.7299 |  |  | E540 | 8698.9562 | 20-Jul | 15 | 19575 | 30-Aug | 16 | 627.186 | 11-Mar | 10 | 19575 | 30-Aug | 16
E540 | 19430.3785 | 15020.7433 | 1888.1035 | 2521.5317 | 45112.827 | 45111.8473 | 0.97976 | 2.668 | 13.2893 | 0.0044601 | 48.521 |  |  | E545 | 7204.827 | 20-Jul | 15 | 20075.2 | 17-Jun | 16 | 1.8119e-11 | 01-Jul | 16 | 20075.2 | 17-Jun | 16
E545 | 15687.0796 | 12621.8685 | 1312.4522 | 1752.7588 | 44981.3517 | 44981.3517 | 0 | 3.2281 | 26.6052 | 0.0062265 | 36.6249
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [10 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum*
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2055.7697 | 256.5326 | 8131.73 | 6189.34 | 1942.39 | 0.0090778 | 3.5167 | 18.05 | 23.4068 | 16.9641 | 0.011255 |  |  | E300 | 4.1683 | 16-Apr | 3 | 2.7931 | 24-Apr | 17 | 26.1999 | 07-Jul | 15 | 7.93 | 06-Jan | 6 | 0.013284 | 16-Nov | 17 | 0.0018769 | 11-Jan | 3 | 68.7892 | 16-Nov | 17 | 13.3312 | 06-Nov | 5
2 | 2053.6706 | 256.5271 | 8115.8 | 6201.56 | 1914.24 | 0.0090138 | 3.513 | 18.05 | 23.3748 | 16.9046 | 0.011255 |  |  | E310 | 4.1433 | 30-Apr | 15 | 2.8652 | 01-Dec | 15 | 27.0778 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.01575 | 01-Oct | 23 | 0.0018769 | 11-Jan | 3 | 77.7029 | 02-Oct | 4 | 13.3898 | 06-Nov | 6
3 | 2054.4923 | 256.5356 | 8127.89 | 6194.38 | 1933.51 | 0.0090644 | 3.517 | 18.05 | 23.3833 | 16.9418 | 0.011255 |  |  | E320 | 4.1683 | 16-Apr | 3 | 2.8252 | 31-Mar | 14 | 32.3604 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.018017 | 10-Jul | 13 | 0.0018769 | 11-Jan | 3 | 81.8358 | 18-Sep | 10 | 13.3312 | 06-Nov | 5
4 | 1830.0824 | 229.5857 | 7224.15 | 5548.55 | 1675.6 | 0.0089864 | 3.5074 | 17.8 | 23.3739 | 16.8619 | 0.011075 |  |  | E330 | 4.1683 | 16-Apr | 3 | 2.8252 | 31-Mar | 14 | 32.2321 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.017651 | 10-Jul | 12 | 0.0018769 | 11-Jan | 3 | 76.6591 | 22-Sep | 20 | 13.3312 | 06-Nov | 5
5 | 2029.3426 | 256.394 | 8104.85 | 6318.9 | 1785.95 | 0.0088405 | 3.5458 | 17.5 | 23.3503 | 16.6966 | 0.01061 |  |  | E340 | 4.1683 | 16-Apr | 3 | 2.8252 | 31-Mar | 14 | 32.3066 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.017871 | 10-Jul | 13 | 0.0018769 | 11-Jan | 3 | 79.9293 | 18-Sep | 10 | 13.3312 | 06-Nov | 5
6 | 1839.4317 | 229.5597 | 7130.87 | 5686.24 | 1444.63 | 0.0086578 | 3.4465 | 18.3 | 23.4171 | 16.5734 | 0.010568 |  |  | E350 | 4.1683 | 16-Apr | 3 | 2.7904 | 24-Apr | 17 | 34.5841 | 01-Oct | 24 | 7.93 | 06-Jan | 6 | 0.016758 | 01-Oct | 24 | 0.0018769 | 11-Jan | 3 | 68.7892 | 16-Nov | 17 | 13.3312 | 06-Nov | 5
7 | 2667.2444 | 308.5446 | 9711.38 | 7596.88 | 2114.5 | 0.0091531 | 3.2635 | 22.2 | 24.0395 | 17.3192 | 0.012071 |  |  | E360 | 4.401 | 05-Oct | 1 | 2.8252 | 31-Mar | 14 | 33.7585 | 10-Jul | 13 | 7.93 | 06-Jan | 6 | 0.013433 | 10-Jul | 13 | 0.0018769 | 11-Jan | 3 | 68.7892 | 16-Nov | 17 | 13.3312 | 06-Nov | 5
8 | 3552.7185 | 384.0455 | 12121.31 | 9558.23 | 2563.08 | 0.0095303 | 3.079 | 26.1 | 24.5724 | 17.7945 | 0.012173 |  |  | E400 | 4.0769 | 16-Sep | 15 | 2.7819 | 31-Mar | 19 | 27.1148 | 16-Sep | 15 | 7.93 | 06-Jan | 6 | 0.016944 | 05-Apr | 22 | 0.0018769 | 11-Jan | 3 | 83.7534 | 05-Apr | 22 | 13.209 | 06-Nov | 5
9 | 4364.7758 | 458.1014 | 14555.62 | 11757.9 | 2797.72 | 0.0096727 | 3.018 | 28.05 | 25.0937 | 17.973 | 0.011538 |  |  | E410 | 3.8879 | 30-Apr | 15 | 2.7858 | 24-Apr | 17 | 26.8256 | 23-Oct | 15 | 7.93 | 06-Jan | 6 | 0.016835 | 05-Apr | 22 | 0.0018769 | 11-Jan | 3 | 83.2247 | 05-Apr | 22 | 13.2091 | 06-Nov | 5
10 | 4441.0633 | 457.9932 | 14639.38 | 11506.4 | 3132.98 | 0.010058 | 2.9882 | 28.9 | 25.2815 | 18.3972 | 0.012388 |  |  | E420 | 3.7813 | 27-Sep | 16 | 2.7931 | 24-Apr | 17 | 26.1999 | 07-Jul | 15 | 7.93 | 06-Jan | 6 | 0.014297 | 02-Apr | 10 | 0.0018769 | 11-Jan | 3 | 70.8411 | 02-Apr | 10 | 13.2099 | 06-Nov | 5
11 | 4999.595 | 506.3045 | 16374.09 | 12342.2 | 4031.89 | 0.010408 | 2.9739 | 30 | 25.3592 | 18.8246 | 0.013776 |  |  | E430 | 3.7813 | 27-Sep | 16 | 2.7711 | 30-Mar | 19 | 27.1992 | 01-Nov | 16 | 7.93 | 06-Jan | 6 | 0.016231 | 02-Apr | 5 | 0.0018769 | 11-Jan | 3 | 80.7087 | 02-Apr | 5 | 13.2078 | 06-Nov | 5
12 | 5316.7711 | 529.3648 | 17248.4 | 12810 | 4438.4 | 0.010684 | 2.9504 | 30.85 | 25.5877 | 19.1202 | 0.014041 |  |  | E440 | 3.8835 | 12-Dez | 7 | 2.7825 | 31-Mar | 19 | 27.0452 | 28-Apr | 15 | 7.93 | 06-Jan | 6 | 0.013313 | 16-Nov | 17 | 0.0018769 | 11-Jan | 3 | 68.7242 | 16-Nov | 17 | 13.2069 | 06-Nov | 5
13 | 6188.5477 | 616.6094 | 20498.21 | 16816.1 | 3682.11 | 0.010087 | 3.0122 | 30.85 | 26.53 | 18.8377 | 0.012315 |  |  | E500 | 4.2751 | 13-Oct | 1 | 2.6852 | 30-Jul | 12 | 25.8054 | 30-Apr | 15 | 8.427 | 20-Dec | 22 | 0.01172 | 11-Jul | 15 | 0.0068276 | 20-Dec | 22 | 100 | 21-Nov | 24 | 53.4054 | 30-Apr | 15
14 | 6210.9293 | 616.1242 | 20234.06 | 17283.5 | 2950.56 | 0.0097987 | 2.9638 | 31.4 | 26.5617 | 18.5548 | 0.011543 |  |  | E510 | 4.6925 | 05-Oct | 1 | 2.888 | 31-Mar | 15 | 26.1003 | 09-Jul | 15 | 8.427 | 20-Dec | 22 | 0.011871 | 07-Sep | 15 | 0.0068276 | 20-Dec | 22 | 100 | 21-Nov | 24 | 52.0879 | 04-Oct | 23
15 | 7922.4534 | 781.0016 | 26687.28 | 22882.4 | 3804.88 | 0.0095792 | 3.0663 | 31.95 | 26.7812 | 18.5486 | 0.012069 |  |  | E520 | 3.8137 | 30-Apr | 15 | 2.4417 | 30-Jul | 12 | 16.1232 | 15-Aug | 15 | 8.3053 | 20-Dec | 22 | 0.0075403 | 07-Sep | 15 | 0.006103 | 26-Nov | 2 | 90.2299 | 20-Dec | 22 | 61.2679 | 25-Nov | 24
16 | 7964.823 | 781.0124 | 26722.68 | 22284.7 | 4437.98 | 0.0096663 | 3.0555 | 32.2 | 26.5632 | 18.673 | 0.013324 |  |  | E522 | 3.9855 | 16-Mar | 10 | 2.5689 | 08-Jul | 17 | 21.0091 | 16-Jul | 15 | 8.4141 | 20-Dec | 22 | 0.0094264 | 20-Jul | 16 | 0.0068215 | 20-Dec | 22 | 100 | 18-Dec | 8 | 58.5054 | 30-Apr | 15
17 | 5420.7775 | 529.4985 | 17231.33 | 13048.3 | 4183.03 | 0.01077 | 2.8959 | 31.95 | 26.198 | 19.4032 | 0.014505 |  |  | E525 | 4.7178 | 13-Oct | 1 | 2.9111 | 14-Jul | 17 | 36.08 | 10-Mai | 16 | 8.4442 | 20-Dec | 22 | 0.017932 | 10-Mai | 16 | 0.0068356 | 20-Dec | 22 | 100 | 12-Nov | 20 | 45.5284 | 30-Apr | 15
18 | 5409.9868 | 529.3784 | 17505.88 | 12720.6 | 4785.28 | 0.011184 | 2.9474 | 31.4 | 26.2263 | 19.7724 | 0.015234 |  |  | E530 | 4.0061 | 02-Nov | 1 | 2.5013 | 30-Jul | 12 | 26.116 | 04-Jun | 15 | 8.4215 | 20-Dec | 22 | 0.0069892 | 01-Jan | 1 | 0.006208 | 01-Apr | 1 | 91.0445 | 20-Dec | 22 | 29.5934 | 04-Jun | 15
19 | 5260.0345 | 529.2289 | 17661.69 | 12490.8 | 5170.89 | 0.011131 | 3.0508 | 29.7 | 25.7001 | 19.5753 | 0.015134 |  |  | E540 | 3.456 | 30-Apr | 15 | 2.253 | 30-Jul | 12 | 16.1465 | 21-Sep | 16 | 8.2278 | 20-Dec | 22 | 0.006084 | 01-Jan | 1 | 0.0041096 | 05-Oct | 3 | 61.275 | 20-Dec | 22 | 36.4749 | 21-Sep | 16
20 | 4880.3429 | 506.2207 | 16989.81 | 11655.3 | 5334.51 | 0.010991 | 3.1541 | 27.75 | 25.1673 | 19.3718 | 0.015748 |  |  | E545 | 4.2505 | 16-Mar | 10 | 2.7325 | 14-Jul | 17 | 35.6715 | 20-Jul | 15 | 8.4486 | 20-Dec | 22 | 0.0069892 | 01-Jan | 1 | 0.006208 | 01-Apr | 1 | 90.8772 | 20-Dec | 22 | 17.1244 | 20-Jul | 15
21 | 3938.7143 | 409.0843 | 13539.94 | 8882.19 | 4657.75 | 0.01114 | 3.1142 | 27.2 | 24.6544 | 19.438 | 0.016886 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 3923.9563 | 409.5326 | 13564.54 | 8880.28 | 4684.26 | 0.011177 | 3.1302 | 26.95 | 24.7445 | 19.4846 | 0.016863
23 | 4122.5716 | 433.8551 | 14531.34 | 9449.35 | 5081.99 | 0.011176 | 3.1892 | 26.4 | 24.6707 | 19.4693 | 0.016867
24 | 3877.3845 | 409.5808 | 13691.76 | 8806.54 | 4885.22 | 0.011275 | 3.1938 | 26.1 | 24.7257 | 19.5725 | 0.017112
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3892.9389 | 3014.619 | 376.0762 | 502.2437 | 13185.6871 | 9374.7971 | 3810.89 | 0.010675 | 3.8448 | 16.7917 | 24.6411
June 25 | 5044.9219 | 4083.8829 | 411.4946 | 549.5444 | 13188.0504 | 9377.6867 | 3810.3637 | 0.011168 | 2.9313 | 29.5167 | 24.5478
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3022.7732 | 2311.4724 | 304.5625 | 406.7383 | 9353.1633 | 9353.1633 | -5.4771e-13 | 0.006208 | 3.5431 | 16.7917 | 24.365
June 25 | 3894.1233 | 3118.0954 | 332.2771 | 443.7507 | 9376.2963 | 9376.2963 | 7.2905e-13 | 0.006208 | 2.7197 | 29.5167 | 24.3537

## DOE22
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
DOE-2.2 NT42j; 16 Jun 2004 rev for FLOOR-WEIGHT = 0.74 (zone air mass)
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34750 | 21569 | 2301 | 10880 | 77283.4356 | 55796.8608 | 21486.5748 | 3.2377 | 24.0556 | 0.0092 | 48.26 | 19.8889 | 0.0116 | E300 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15 | 35 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 | 39379 | 25813 | 2686 | 10880 | 97394.7852 | 56300.9928 | 41093.7924 | 3.4175 | 24.1111 | 0.0113 | 58.51 | ODB, OHR |  | E310 | 12583 | 2002-07-20 | 15 | 23080 | 2004-09-10 | 16 | 15139 | 2001-09-03 | 15 | 36750 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 | 38745 | 25250 | 2615 | 10880 | 96356.3319 | 62697.021 | 33659.3109 | 3.458 | 24.3889 | 0.0101 | 51.21 | from E500 |  | E320 | 12916 | 2002-07-20 | 15 | 31119 | 2004-04-24 | 16 | 31497 | 2002-10-02 | 9 | 53813 | 2002-10-02 | 9
E330 | 39708 | 26172 | 2656 | 10880 | 100729.9701 | 63311.0655 | 37418.9046 | 3.4942 | 24.2778 | 0.0099 | 50.58 |  |  | E330 | 13212 | 2002-07-20 | 15 | 33410 | 2002-06-14 | 14 | 26941 | 2003-09-18 | 15 | 43628 | 2002-10-02 | 9
E340 | 39358 | 25829 | 2649 | 10880 | 99027.6453 | 63053.4306 | 35974.2147 | 3.4773 | 24.2778 | 0.0099 | 50.69 |  |  | E340 | 13158 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 30451 | 2002-10-02 | 9 | 50819 | 2002-10-02 | 9
E350 | 30547 | 17802 | 1865 | 10880 | 63736.3536 | 47684.439 | 16051.9146 | 3.2408 | 26.1667 | 0.01 | 45.45 |  |  | E350 | 11654 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9303 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E360 | 54064 | 38999 | 4185 | 10880 | 159807.2061 | 134919.792 | 24887.4141 | 3.7006 | 25.6111 | 0.0087 | 41.49 |  |  | E360 | 12736 | 2002-07-20 | 15 | 32111 | 2003-04-24 | 16 | 10026 | 2002-10-02 | 9 | 40613 | 2002-10-02 | 9
E400 | 30846 | 18106 | 1860 | 10880 | 64917.5466 | 41419.1334 | 23498.4132 | 3.2514 | 24.0556 | 0.01 | 52.21 |  |  | E400 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 25578 | 2002-09-18 | 14 | 40543 | 2002-09-18 | 14
E410 | 31668 | 18823 | 1965 | 10880 | 66779.6109 | 47658.6462 | 19120.9647 | 3.2124 | 24.0556 | 0.0095 | 49.65 |  |  | E410 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E420 | 32530 | 19596 | 2054 | 10880 | 69610.9569 | 49666.0881 | 19944.8688 | 3.2153 | 24.0556 | 0.0094 | 49.14 |  |  | E420 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E430 | 31932 | 19059 | 1993 | 10880 | 67640.7387 | 47731.335 | 19909.4037 | 3.213 | 24.0556 | 0.0094 | 49.17 |  |  | E430 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 11105 | 2004-10-24 | 14 | 31401 | 2001-07-20 | 15
E440 | 33032 | 20042 | 2110 | 10880 | 71380.1085 | 50592.5772 | 20787.5313 | 3.2223 | 24.0556 | 0.0093 | 48.46 |  |  | E440 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E500 | 22817 | 18473 | 1975 | 2369 | 65995.8615 | 47649.8532 | 18346.0083 | 3.2275 | 20.6667 |  |  |  |  | E500 | 10431 | 2002-07-20 | 15 | 20009 | 2003-06-04 | 16 | 7733 | 2001-09-03 | 15 | 27707 | 2001-08-16 | 16
E500 May-Sep | 17872 | 14508 | 1527 | 1837 | 50692.8174 | 36595.5867 | 14097.2307 | 3.1614 | 25 | 0.0114 | 57.47 |  |  | E510 | 11590 | 2002-07-20 | 15 | 22513 | 2002-07-11 | 15 | 8723 | 2002-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep | 35971 | 28811 | 3061 | 4099 | 114017.9517 | 82305.7041 | 31712.2476 | 3.5774 | 25.1111 | 0.0114 | 57.36 |  |  | E520 | 10989 | 2002-07-20 | 15 | 20159 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-08-14 | 16
E520 | 25389 | 20121 | 2394 | 2874 | 66571.2168 | 48101.5203 | 18469.6965 | 2.9567 | 13.7778 |  |  |  |  | E522 | 10972 | 2002-07-20 | 15 | 20137 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27868 | 2002-08-16 | 16
E522 | 24293 | 19407 | 2182 | 2704 | 66373.0812 | 47962.2978 | 18410.7834 | 3.0744 | 17.2778 |  |  |  |  | E525 | 9538 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 | 20408 | 16880 | 1642 | 1886 | 65399.1099 | 47217.5307 | 18181.5792 | 3.5309 | 27.3889 |  |  |  |  | E530 | 8059 | 2002-07-20 | 15 | 19576 | 2002-04-24 | 16 | 0 | 0 | 0 | 19576 | 2002-04-24 | 16
E530 | 17540 | 14127 | 1580 | 1833 | 46634.2617 | 46573.59 | 60.6717 | 2.969 | 20.6111 |  |  |  |  | E540 | 8943 | 2002-07-20 | 15 | 19766 | 2002-04-24 | 16 | 0 | 0 | 0 | 19766 | 2002-04-24 | 16
E540 | 19878 | 15680 | 1940 | 2258 | 47129.8938 | 47022.9123 | 106.9815 | 2.6748 | 13.7778 |  |  |  |  | E545 | 7350 | 2002-07-20 | 15 | 19475 | 2002-04-24 | 16 | 0 | 0 | 0 | 19475 | 2002-04-24 | 16
E545 | 15802 | 12967 | 1334 | 1501 | 46239.7491 | 46214.2494 | 25.4997 | 3.2333 | 27.3333
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
[10 empty] | ewb from hvac2kit |  | OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) | (kg/kg) | (Pa) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1897 | 237 | 7552.3077 | 5889.2583 | 1663.0494 | 0.0094 | 3.539 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101254.8653 | E300 | 3.869 | 2002-04-30 | 16 | 2.798 | 2002-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
2 | 1941 | 240 | 7630.2723 | 6069.8079 | 1560.4644 | 0.0093 | 3.4985 | 18.3333 | 23.9444 | 17.29 | 0.0112 | 0.0096 | 101254.8653 | E310 | 4.141 | 2002-04-30 | 16 | 2.85 | 2002-12-01 | 14 | 26.89 | 2004-07-20 | 16 | 8.89 | 2001-01-06 | 6 | 0.0188 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.18 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4
3 | 1897 | 237 | 7550.256 | 5881.3446 | 1668.9114 | 0.0094 | 3.5381 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E320 | 5.143 | 2002-10-02 | 9 | 2.801 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 10.83 | 2001-01-06 | 7 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.41 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
4 | 1891 | 237 | 7533.8424 | 5878.1205 | 1655.7219 | 0.0094 | 3.5403 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E330 | 4.109 | 2003-06-17 | 16 | 2.798 | 2002-12-01 | 14 | 31.72 | 2004-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0178 | 2003-10-02 | 9 | 0.0017 | 2001-01-04 | 24 | 78.46 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
5 | 1697 | 215 | 6797.8683 | 5675.2953 | 1122.573 | 0.0089 | 3.5554 | 17.2222 | 23.7778 | 16.85 | 0.0103 | 0.0091 | 101593.5104 | E340 | 4.621 | 2002-10-02 | 9 | 2.798 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.37 | 2004-09-18 | 9 | 11.97 | 2002-11-06 | 4
6 | 2126 | 259 | 8136.1629 | 6438.5277 | 1697.6352 | 0.0092 | 3.4114 | 19.4444 | 24.1111 | 17.3 | 0.0113 | 0.0095 | 101593.5104 | E350 | 3.889 | 2003-04-27 | 5 | 2.798 | 2004-12-01 | 14 | 34.94 | 2003-06-23 | 24 | 8.89 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4
7 | 3198 | 352 | 11075.9559 | 8342.2122 | 2733.7437 | 0.01 | 3.12 | 25 | 24.9444 | 18.39 | 0.0133 | 0.0105 | 101593.5104 | E360 | 4.428 | 2002-10-04 | 24 | 2.799 | 2002-12-01 | 14 | 32.78 | 2002-07-20 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
8 | 3135 | 332 | 10290.741 | 9069.9795 | 1220.7615 | 0.0094 | 2.9682 | 27.2222 | 25.2778 | 17.78 | 0.0109 | 0.0096 | 101593.5104 | E400 | 4.088 | 2003-06-17 | 16 | 2.734 | 2002-12-03 | 15 | 27.56 | 2003-09-16 | 16 | 8.89 | 2001-01-06 | 6 | 0.017 | 2002-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2002-04-05 | 21 | 11.97 | 2002-11-06 | 4
9 | 4528 | 469 | 14785.7226 | 11872.6017 | 2913.1209 | 0.0099 | 2.9589 | 28.8889 | 25.5556 | 18.36 | 0.0117 | 0.0102 | 101593.5104 | E410 | 3.903 | 2002-04-30 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4
10 | 4651 | 479 | 15339.9747 | 12039.0825 | 3300.8922 | 0.0103 | 2.9902 | 28.8889 | 25.5556 | 18.68 | 0.0125 | 0.0106 | 101593.5104 | E420 | 3.807 | 2003-05-21 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0147 | 2003-04-01 | 21 | 0.0017 | 2001-01-04 | 24 | 74.51 | 2003-04-17 | 7 | 11.97 | 2002-11-06 | 4
11 | 5434 | 537 | 17455.2774 | 12811.9872 | 4643.2902 | 0.0109 | 2.9233 | 31.1111 | 25.8889 | 19.48 | 0.0148 | 0.0115 | 101593.5104 | E430 | 3.805 | 2003-10-24 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0156 | 2002-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2002-04-02 | 4 | 11.97 | 2002-11-06 | 4
12 | 5019 | 498 | 16215.1713 | 12612.093 | 3603.0783 | 0.0108 | 2.9391 | 30.5556 | 25.8333 | 19.23 | 0.0134 | 0.0112 | 101593.5104 | E440 | 3.774 | 2002-09-27 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
13 | 6040 | 597 | 19722.9921 | 17139.0225 | 2583.9696 | 0.0101 | 2.9717 | 31.1111 | 25.9444 | 18.56 | 0.0115 | 0.0103 | 101593.5104 | E500 | 7.367 | 2004-03-11 | 10 | 2.693 | 2002-07-29 | 12 | 25.11 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
14 | 6420 | 633 | 20808.3414 | 17638.1718 | 3170.1696 | 0.01 | 2.9503 | 31.6667 | 26.0556 | 18.6 | 0.0121 | 0.0103 | 101593.5104 | E510 | 7.367 | 2004-03-11 | 10 | 2.817 | 2004-04-05 | 17 | 25.11 | 2001-04-21 | 3 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
15 | 7671 | 751 | 25387.1496 | 22196.463 | 3190.6866 | 0.0098 | 3.0144 | 32.2222 | 26.1111 | 18.46 | 0.0119 | 0.0101 | 101593.5104 | E520 | 4.896 | 2004-03-16 | 10 | 2.463 | 2004-04-05 | 17 | 16.11 | 2002-08-16 | 16 | 8.11 | 2004-12-20 | 12 | 0.0077 | 2004-07-10 | 16 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
16 | 8190 | 800 | 27581.0031 | 22527.9591 | 5053.044 | 0.01 | 3.068 | 32.2222 | 26.1667 | 18.84 | 0.0144 | 0.0106 | 101254.8653 | E522 | 6.233 | 2004-03-11 | 10 | 2.572 | 2002-07-29 | 12 | 20.11 | 2001-04-21 | 15 | 8.17 | 2004-12-20 | 12 | 0.0095 | 2003-06-04 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
17 | 5715 | 561 | 18204.7341 | 13599.2538 | 4605.4803 | 0.0107 | 2.9007 | 31.6667 | 26.0556 | 19.35 | 0.0146 | 0.0113 | 101254.8653 | E525 | 6.325 | 2004-04-12 | 9 | 2.939 | 2003-07-30 | 12 | 35.06 | 2003-04-21 | 16 | 8.17 | 2004-12-20 | 13 | 0.018 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
18 | 5536 | 544 | 17933.3235 | 12829.8663 | 5103.4572 | 0.0112 | 2.9496 | 31.1111 | 25.9444 | 19.75 | 0.0157 | 0.0119 | 101254.8653 | E530 | 3.981 | 2004-03-11 | 10 | 2.495 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0081 | 2001-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
19 | 4711 | 481 | 16012.053 | 11875.5327 | 4136.5203 | 0.011 | 3.084 | 28.3333 | 25.5 | 19.32 | 0.0143 | 0.0115 | 101254.8653 | E540 | 3.456 | 2004-04-30 | 16 | 2.261 | 2003-07-29 | 12 | 15.11 | 2004-05-31 | 16 | 8.11 | 2004-12-20 | 12 | 0.005 | 2003-06-04 | 13 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
20 | 4859 | 504 | 17082.1611 | 11532.3126 | 5549.8485 | 0.0114 | 3.1852 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104 | E545 | 4.275 | 2004-03-16 | 10 | 2.72 | 2003-07-29 | 12 | 35 | 2003-04-21 | 15 | 8.17 | 2004-12-20 | 13 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
21 | 3913 | 405 | 13435.4109 | 9302.4078 | 4133.0031 | 0.0113 | 3.1115 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104
22 | 3825 | 399 | 13280.361 | 8973.5496 | 4306.8114 | 0.0114 | 3.144 | 26.6667 | 25.2222 | 19.8 | 0.0167 | 0.0122 | 101593.5104
23 | 3750 | 395 | 13191.8448 | 8787.4311 | 4404.4137 | 0.0115 | 3.1826 | 26.1111 | 25.1111 | 19.84 | 0.0169 | 0.0123 | 101593.5104
24 | 3880 | 407 | 13724.4075 | 8799.1551 | 4925.2524 | 0.0117 | 3.2014 | 26.1111 | 25.1111 | 20.14 | 0.0178 | 0.0127 | 101593.5104
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3975.4583 | 3119.8333 | 389.125 | 466.5 | 13732.6998 | 9924.8179 | 3807.8819 | 0.011 | 3.9136 | 16.8333 | 24.9444
June 25 | 5204.3333 | 4263.5417 | 426.3333 | 514.4583 | 13837.5319 | 9981.2396 | 3856.2923 | 0.0115 | 2.9505 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3062 | 2390.0417 | 311.1667 | 360.7917 | 9721.15 | 9721.15 | 0 | 0.0071 | 3.5988 | 16.8333 | 24.9444
June 25 | 3978.2083 | 3243 | 339.625 | 395.5833 | 9760.7918 | 9760.7674 | 0.024425 | 0.0078 | 2.7245 | 29.5 | 24.9444
DOE-2.2 NT42j, 17 Nov 2003
enter raw doe2 results below
bold entries not changed
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s; ODB Date: E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor |  | ODB Date: Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Compr + Both Fans Wh: Energy Consumption; Sensible Hour: E v a p o r a t o r C o i l L o a d s
Cases | Total | Compr+cond | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans Wh: Compr + Both Fans; Sensible Date: Sensible; Latent Date: Latent; Sensible + Latent Wh: Sensible + Latent; ODB Date: ODB; Outdoor Humidity Ratio kg/kg: Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (Btu) | (Btu) | (Btu) |  | (°F) | (kg/kg) | (%) | (°F) | (kg/kg) |  | Wh | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | °F | Date | Hour | kg/kg | Date | Hour
E300 |  | 23870 | 2301 | 10880 | 263676 |  | 73308 | 3.2377 | 75.3 | 0.0092 | 48.26 | 67.8 | 0.0116 | E300 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15 | 95 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 |  | 28499 | 2686 | 10880 | 332292 |  | 140204 | 3.4175 | 75.4 | 0.0113 | 58.51 |  |  | E310 | 12583 | 2002-07-20 | 15 | 23080 | 2004-09-10 | 16 | 15139 | 2001-09-03 | 15 | 36750 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 |  | 27865 | 2615 | 10880 | 328749 |  | 114839 | 3.458 | 75.9 | 0.0101 | 51.21 |  |  | E320 | 12916 | 2002-07-20 | 15 | 31119 | 2004-04-24 | 16 | 31497 | 2002-10-02 | 9 | 53813 | 2002-10-02 | 9
E330 |  | 28828 | 2656 | 10880 | 343671 |  | 127666 | 3.4942 | 75.7 | 0.0099 | 50.58 |  |  | E330 | 13212 | 2002-07-20 | 15 | 33410 | 2002-06-14 | 14 | 26941 | 2003-09-18 | 15 | 43628 | 2002-10-02 | 9
E340 |  | 28478 | 2649 | 10880 | 337863 |  | 122737 | 3.4773 | 75.7 | 0.0099 | 50.69 |  |  | E340 | 13158 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 30451 | 2002-10-02 | 9 | 50819 | 2002-10-02 | 9
E350 |  | 19667 | 1865 | 10880 | 217456 |  | 54766 | 3.2408 | 79.1 | 0.01 | 45.45 |  |  | E350 | 11654 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9303 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E360 |  | 43184 | 4185 | 10880 | 545231 |  | 84911 | 3.7006 | 78.1 | 0.0087 | 41.49 |  |  | E360 | 12736 | 2002-07-20 | 15 | 32111 | 2003-04-24 | 16 | 10026 | 2002-10-02 | 9 | 40613 | 2002-10-02 | 9
E400 |  | 19966 | 1860 | 10880 | 221486 |  | 80172 | 3.2514 | 75.3 | 0.01 | 52.21 |  |  | E400 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 25578 | 2002-09-18 | 14 | 40543 | 2002-09-18 | 14
E410 |  | 20788 | 1965 | 10880 | 227839 |  | 65237 | 3.2124 | 75.3 | 0.0095 | 49.65 |  |  | E410 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E420 |  | 21650 | 2054 | 10880 | 237499 |  | 68048 | 3.2153 | 75.3 | 0.0094 | 49.14 |  |  | E420 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E430 |  | 21052 | 1993 | 10880 | 230777 |  | 67927 | 3.213 | 75.3 | 0.0094 | 49.17 |  |  | E430 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 11105 | 2004-10-24 | 14 | 31401 | 2001-07-20 | 15
E440 |  | 22152 | 2110 | 10880 | 243535 |  | 70923 | 3.2223 | 75.3 | 0.0093 | 48.46 |  |  | E440 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E500 |  | 20448 | 1975 | 2369 | 225165 |  | 62593 | 3.2275 | 69.2 |  |  |  |  | E500 | 10431 | 2002-07-20 | 15 | 20009 | 2003-06-04 | 16 | 7733 | 2001-09-03 | 15 | 27707 | 2001-08-16 | 16
E500 May-Sep |  | 16035 | 1527 | 1837 | 172954 |  | 48097 | 3.1614 | 77 | 0.0114 | 57.47 |  |  | E510 | 11590 | 2002-07-20 | 15 | 22513 | 2002-07-11 | 15 | 8723 | 2002-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep |  | 31872 | 3061 | 4099 | 389007 |  | 108196 | 3.5774 | 77.2 | 0.0114 | 57.36 |  |  | E520 | 10989 | 2002-07-20 | 15 | 20159 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-08-14 | 16
E520 |  | 22515 | 2394 | 2874 | 227128 |  | 63015 | 2.9567 | 56.8 |  |  |  |  | E522 | 10972 | 2002-07-20 | 15 | 20137 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27868 | 2002-08-16 | 16
E522 |  | 21589 | 2182 | 2704 | 226452 |  | 62814 | 3.0744 | 63.1 |  |  |  |  | E525 | 9538 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 |  | 18522 | 1642 | 1886 | 223129 |  | 62032 | 3.5309 | 81.3 |  |  |  |  | E530 | Compr + Both Fans Wh: 8059; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19576; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19576; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E530 |  | 15707 | 1580 | 1833 | 159107 |  | 207 | 2.969 | 69.1 |  |  |  |  | E540 | Compr + Both Fans Wh: 8943; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19766; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19766; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E540 |  | 17620 | 1940 | 2258 | 160798 |  | 365 | 2.6748 | 56.8 |  |  |  |  | E545 | Compr + Both Fans Wh: 7350; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19475; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19475; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E545 |  | 14301 | 1334 | 1501 | 157761 |  | 87 | 3.2333 | 81.2
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh/h: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compr+cond | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Btu/h) | (Btu/h) | (Btu/h) | (kg/kg) |  | (°F) | (°F) | (°F) | (kg/kg) | (kg/kg) | (in Hg) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2134 | 237 | 25767 |  | 5674 | 0.0094 | 3.539 | 64 | 74.9 | 63.212 | 0.0114 | 0.0097 | 29.9 | E300 | 3.869 | 2002-04-30 | 16 | 2.798 | 2002-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
2 | 2181 | 240 | 26033 |  | 5324 | 0.0093 | 3.4985 | 65 | 75.1 | enter | 0.0112 | 0.0096 | 29.9 | E310 | 4.141 | 2002-04-30 | 16 | 2.85 | 2002-12-01 | 14 | 26.89 | 2004-07-20 | 16 | 8.89 | 2001-01-06 | 6 | 0.0188 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.18 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4
3 | 2134 | 237 | 25760 |  | 5694 | 0.0094 | 3.5381 | 64 | 74.9 | above | 0.0114 | 0.0097 | 30 | E320 | 5.143 | 2002-10-02 | 9 | 2.801 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 10.83 | 2001-01-06 | 7 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.41 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
4 | 2128 | 237 | 25704 |  | 5649 | 0.0094 | 3.5403 | 64 | 74.9 |  | 0.0114 | 0.0097 | 30 | E330 | 4.109 | 2003-06-17 | 16 | 2.798 | 2002-12-01 | 14 | 31.72 | 2004-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0178 | 2003-10-02 | 9 | 0.0017 | 2001-01-04 | 24 | 78.46 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
5 | 1912 | 215 | 23193 |  | 3830 | 0.0089 | 3.5554 | 63 | 74.8 |  | 0.0103 | 0.0091 | 30 | E340 | 4.621 | 2002-10-02 | 9 | 2.798 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.37 | 2004-09-18 | 9 | 11.97 | 2002-11-06 | 4
6 | 2385 | 259 | 27759 |  | 5792 | 0.0092 | 3.4114 | 67 | 75.4 |  | 0.0113 | 0.0095 | 30 | E350 | 3.889 | 2003-04-27 | 5 | 2.798 | 2004-12-01 | 14 | 34.94 | 2003-06-23 | 24 | 8.89 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4
7 | 3550 | 352 | 37789 |  | 9327 | 0.01 | 3.12 | 77 | 76.9 |  | 0.0133 | 0.0105 | 30 | E360 | 4.428 | 2002-10-04 | 24 | 2.799 | 2002-12-01 | 14 | 32.78 | 2002-07-20 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
8 | 3467 | 332 | 35110 |  | 4165 | 0.0094 | 2.9682 | 81 | 77.5 |  | 0.0109 | 0.0096 | 30 | E400 | 4.088 | 2003-06-17 | 16 | 2.734 | 2002-12-03 | 15 | 27.56 | 2003-09-16 | 16 | 8.89 | 2001-01-06 | 6 | 0.017 | 2002-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2002-04-05 | 21 | 11.97 | 2002-11-06 | 4
9 | 4997 | 469 | 50446 |  | 9939 | 0.0099 | 2.9589 | 84 | 78 |  | 0.0117 | 0.0102 | 30 | E410 | 3.903 | 2002-04-30 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4
10 | 5130 | 479 | 52337 |  | 11262 | 0.0103 | 2.9902 | 84 | 78 |  | 0.0125 | 0.0106 | 30 | E420 | 3.807 | 2003-05-21 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0147 | 2003-04-01 | 21 | 0.0017 | 2001-01-04 | 24 | 74.51 | 2003-04-17 | 7 | 11.97 | 2002-11-06 | 4
11 | 5971 | 537 | 59554 |  | 15842 | 0.0109 | 2.9233 | 88 | 78.6 |  | 0.0148 | 0.0115 | 30 | E430 | 3.805 | 2003-10-24 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0156 | 2002-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2002-04-02 | 4 | 11.97 | 2002-11-06 | 4
12 | 5517 | 498 | 55323 |  | 12293 | 0.0108 | 2.9391 | 87 | 78.5 |  | 0.0134 | 0.0112 | 30 | E440 | 3.774 | 2002-09-27 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
13 | 6637 | 597 | 67291 |  | 8816 | 0.0101 | 2.9717 | 88 | 78.7 |  | 0.0115 | 0.0103 | 30 | E500 | 7.367 | 2004-03-11 | 10 | 2.693 | 2002-07-29 | 12 | 25.11 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
14 | 7053 | 633 | 70994 |  | 10816 | 0.01 | 2.9503 | 89 | 78.9 |  | 0.0121 | 0.0103 | 30 | E510 | 7.367 | 2004-03-11 | 10 | 2.817 | 2004-04-05 | 17 | 25.11 | 2001-04-21 | 3 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
15 | 8422 | 751 | 86616 |  | 10886 | 0.0098 | 3.0144 | 90 | 79 |  | 0.0119 | 0.0101 | 30 | E520 | 4.896 | 2004-03-16 | 10 | 2.463 | 2004-04-05 | 17 | 16.11 | 2002-08-16 | 16 | 8.11 | 2004-12-20 | 12 | 0.0077 | 2004-07-10 | 16 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
16 | 8990 | 800 | 94101 |  | 17240 | 0.01 | 3.068 | 90 | 79.1 |  | 0.0144 | 0.0106 | 29.9 | E522 | 6.233 | 2004-03-11 | 10 | 2.572 | 2002-07-29 | 12 | 20.11 | 2001-04-21 | 15 | 8.17 | 2004-12-20 | 12 | 0.0095 | 2003-06-04 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
17 | 6276 | 561 | 62111 |  | 15713 | 0.0107 | 2.9007 | 89 | 78.9 |  | 0.0146 | 0.0113 | 29.9 | E525 | 6.325 | 2004-04-12 | 9 | 2.939 | 2003-07-30 | 12 | 35.06 | 2003-04-21 | 16 | 8.17 | 2004-12-20 | 13 | 0.018 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
18 | 6080 | 544 | 61185 |  | 17412 | 0.0112 | 2.9496 | 88 | 78.7 |  | 0.0157 | 0.0119 | 29.9 | E530 | 3.981 | 2004-03-11 | 10 | 2.495 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0081 | 2001-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
19 | 5192 | 481 | 54630 |  | 14113 | 0.011 | 3.084 | 83 | 77.9 |  | 0.0143 | 0.0115 | 29.9 | E540 | 3.456 | 2004-04-30 | 16 | 2.261 | 2003-07-29 | 12 | 15.11 | 2004-05-31 | 16 | 8.11 | 2004-12-20 | 12 | 0.005 | 2003-06-04 | 13 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
20 | 5363 | 504 | 58281 |  | 18935 | 0.0114 | 3.1852 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | E545 | 4.275 | 2004-03-16 | 10 | 2.72 | 2003-07-29 | 12 | 35 | 2003-04-21 | 15 | 8.17 | 2004-12-20 | 13 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
21 | 4318 | 405 | 45839 |  | 14101 | 0.0113 | 3.1115 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30
22 | 4224 | 399 | 45310 |  | 14694 | 0.0114 | 3.144 | 80 | 77.4 |  | 0.0167 | 0.0122 | 30
23 | 4145 | 395 | 45008 |  | 15027 | 0.0115 | 3.1826 | 79 | 77.2 |  | 0.0169 | 0.0123 | 30
24 | 4287 | 407 | 46825 |  | 16804 | 0.0117 | 3.2014 | 79 | 77.2 |  | 0.0178 | 0.0127 | 30
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 84215 | 9339 | 11196 | 1124479 |  | 311802 | 0.011 | 3.9136 | 62.3 | 76.9
June 25 |  | 112557 | 10232 | 12347 | 1133063 |  | 315766 | 0.0115 | 2.9505 | 85.1 | 77
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 64829 | 7468 | 8659 | 796000 |  | 0 | 0.0071 | 3.5988 | 62.3 | 76.9
June 25 |  | 85983 | 8151 | 9494 | 799246 |  | 2 | 0.0078 | 2.7245 | 85.1 | 76.9

## DOE21E
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
DOE-2.1E ESTSC 120, 20 Oct 2003, using COIL-BF-FPLR default curve; input revs: 11/11/03 for TAVE and correct OUTSIDE-FAN-ELEC, 06/16/04 FLOOR-WEIGHT = 0.74 (zone air mass)
E300OUT2.XLS, Mar 20, 2002
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34755 | 21573 | 2302 | 10880 | 77291.9355 | 55804.7745 | 21487.161 | 3.2374 | 24.0556 | 0.0092 | 48.28 | 19.8889 | 0.0116 | E300 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2001-09-03 | 15 | 31455 | 2001-07-20 | 15 | 35 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 | 39384 | 25817 | 2687 | 10880 | 97412.0781 | 56312.7168 | 41099.3613 | 3.4175 | 24.0556 | 0.0113 | 58.53 | ODB, OHR |  | E310 | 12595 | 2002-07-20 | 15 | 23119 | 2004-06-04 | 16 | 15270 | 2001-09-03 | 15 | 37033 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 | 38792 | 25294 | 2618 | 10880 | 96493.2096 | 62746.848 | 33746.3616 | 3.4571 | 24.3889 | 0.0101 | 51.25 | from E500 |  | E320 | 12981 | 2002-07-20 | 15 | 31072 | 2002-04-24 | 16 | 31503 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9
E330 | 39438 | 25925 | 2633 | 10880 | 100993.467 | 63327.7722 | 37665.6948 | 3.5364 | 24.2778 | 0.0099 | 50.65 |  |  | E330 | 13407 | 2002-07-20 | 15 | 34490 | 2002-06-14 | 15 | 40809 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9
E340 | 39265 | 25745 | 2640 | 10880 | 99223.143 | 63110.5851 | 36112.5579 | 3.4956 | 24.2778 | 0.0099 | 50.73 |  |  | E340 | 13190 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 36011 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9
E350 | 30548 | 17801 | 1867 | 10880 | 63634.6479 | 47676.5253 | 15958.1226 | 3.2354 | 26.1667 | 0.01 | 45.55 |  |  | E350 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9393 | 2001-09-03 | 15 | 31454 | 2001-07-20 | 15
E360 | 54016 | 38955 | 4181 | 10880 | 159853.809 | 134939.7228 | 24914.0862 | 3.7058 | 25.5556 | 0.0087 | 41.49 |  |  | E360 | 12726 | 2002-07-20 | 15 | 32065 | 2004-04-24 | 16 | 10336 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9
E400 | 30876 | 18131 | 1865 | 10880 | 65025.1143 | 41437.0125 | 23588.1018 | 3.2519 | 24.0556 | 0.01 | 52.25 |  |  | E400 | 11677 | 2004-09-18 | 15 | 23205 | 2002-07-20 | 15 | 32396 | 2003-09-18 | 15 | 49838 | 2003-09-18 | 15
E410 | 31699 | 18850 | 1969 | 10880 | 66843.5067 | 47659.8186 | 19183.6881 | 3.2107 | 24.0556 | 0.0095 | 49.63 |  |  | E410 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E420 | 32910 | 19934 | 2096 | 10880 | 70882.1316 | 50612.2149 | 20269.9167 | 3.2175 | 24.0556 | 0.0094 | 48.97 |  |  | E420 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E430 | 31811 | 18951 | 1980 | 10880 | 67219.2609 | 47454.0624 | 19765.1985 | 3.2115 | 24.0556 | 0.0094 | 49.3 |  |  | E430 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 11101 | 2003-05-21 | 15 | 31455 | 2001-07-20 | 15
E440 | 32973 | 19989 | 2104 | 10880 | 71181.0936 | 50492.0439 | 20689.0497 | 3.2219 | 24.0556 | 0.0093 | 48.57 |  |  | E440 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2003-07-20 | 15
E500 | 22822 | 18478 | 1975 | 2369 | 65992.3443 | 47646.0429 | 18346.3014 | 3.2265 | 20.5556 |  |  |  |  | E500 | 10425 | 2002-07-20 | 15 | 20008 | 2002-09-10 | 16 | 7733 | 2001-09-03 | 15 | 27706 | 2001-08-16 | 16
E500 May-Sep | 17870 | 14506 | 1527 | 1837 | 50690.4726 | 36593.2419 | 14097.2307 | 3.1616 | 25 | 0.0114 | 57.47 |  |  | E510 | 11587 | 2002-07-20 | 15 | 22513 | 2003-07-11 | 15 | 8723 | 2003-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep | 35970 | 28810 | 3061 | 4099 | 114015.3138 | 82303.0662 | 31712.2476 | 3.5774 | 25.1111 | 0.0114 | 57.36 |  |  | E520 | 11014 | 2002-07-20 | 15 | 20154 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-07-23 | 16
E520 | 25390 | 20126 | 2393 | 2871 | 66565.3548 | 48095.6583 | 18469.6965 | 2.956 | 13.7222 |  |  |  |  | E522 | 10966 | 2002-07-20 | 15 | 20135 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27866 | 2002-08-16 | 16
E522 | 24307 | 19418 | 2182 | 2707 | 66371.9088 | 47961.4185 | 18410.4903 | 3.0728 | 17.2222 |  |  |  |  | E525 | 9531 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 | 20421 | 16893 | 1643 | 1885 | 65395.0065 | 47213.4273 | 18181.5792 | 3.528 | 27.2778 |  |  |  |  | E530 | 8055 | 2002-07-20 | 15 | 19575 | 2002-04-24 | 16 | 0 | 0 | 0 | 19575 | 2002-04-24 | 16
E530 | 17537 | 14124 | 1580 | 1833 | 46630.7445 | 46570.0728 | 60.6717 | 2.9694 | 20.5556 |  |  |  |  | E540 | 8939 | 2002-07-20 | 15 | 19766 | 2002-04-24 | 16 | 0 | 0 | 0 | 19766 | 2002-04-24 | 16
E540 | 19874 | 15677 | 1939 | 2258 | 47126.0835 | 47019.102 | 106.9815 | 2.6752 | 13.7222 |  |  |  |  | E545 | 7346 | 2002-07-20 | 15 | 19474 | 2002-04-24 | 16 | 0 | 0 | 0 | 19474 | 2002-04-24 | 16
E545 | 15791 | 12957 | 1333 | 1501 | 46235.9388 | 46210.4391 | 25.4997 | 3.2355 | 27.2778
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
[10 empty] | ewb from hvac2kit |  | OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) | (kg/kg) | (Pa) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1894 | 237 | 7544.9802 | 5886.9135 | 1658.0667 | 0.0094 | 3.5406 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101254.8653 | E300 | 3.857 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4
2 | 1941 | 241 | 7627.0482 | 6067.17 | 1559.8782 | 0.0093 | 3.4954 | 18.3333 | 23.9444 | 17.29 | 0.0112 | 0.0096 | 101254.8653 | E310 | 4.128 | 2002-04-30 | 16 | 2.851 | 2002-12-01 | 12 | 26.72 | 2002-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0189 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.7 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4
3 | 1894 | 237 | 7546.1526 | 5878.1205 | 1668.0321 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114 | 0.0097 | 101593.5104 | E320 | 4.967 | 2002-10-02 | 9 | 2.805 | 2003-12-01 | 15 | 31.5 | 2003-07-08 | 16 | 10.78 | 2001-01-06 | 7 | 0.0176 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.67 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4
4 | 1890 | 236 | 7528.2735 | 5873.4309 | 1654.8426 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114 | 0.0097 | 101593.5104 | E330 | 5.595 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 32 | 2003-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 13 | 0.0017 | 2001-01-04 | 24 | 77.94 | 2003-09-18 | 9 | 11.97 | 2002-11-06 | 4
5 | 1694 | 215 | 6753.024 | 5671.7781 | 1081.2459 | 0.009 | 3.5375 | 17.2222 | 23.7778 | 16.94 | 0.0103 | 0.0092 | 101593.5104 | E340 | 5.339 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 31.56 | 2003-07-08 | 16 | 8.83 | 2001-01-06 | 6 | 0.0174 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.26 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4
6 | 2133 | 259 | 8185.1106 | 6438.5277 | 1746.5829 | 0.0092 | 3.4219 | 19.4444 | 24.1111 | 17.3 | 0.0113 | 0.0095 | 101593.5104 | E350 | 3.863 | 2004-10-05 | 3 | 2.801 | 2003-12-01 | 12 | 34.94 | 2004-06-24 | 24 | 8.83 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4
7 | 3223 | 353 | 11232.7644 | 8347.7811 | 2884.9833 | 0.0098 | 3.1412 | 25 | 24.9444 | 18.23 | 0.0133 | 0.0103 | 101593.5104 | E360 | 4.427 | 2002-10-04 | 24 | 2.801 | 2003-12-01 | 12 | 32.56 | 2004-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4
8 | 3145 | 335 | 10271.6895 | 9069.1002 | 1202.5893 | 0.0094 | 2.9516 | 27.2222 | 25.2778 | 17.78 | 0.0109 | 0.0096 | 101593.5104 | E400 | 4.776 | 2003-09-18 | 15 | 2.735 | 2003-12-03 | 13 | 28.83 | 2002-09-18 | 16 | 8.83 | 2001-01-06 | 6 | 0.017 | 2003-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2003-04-05 | 21 | 11.97 | 2002-11-06 | 4
9 | 4526 | 467 | 14844.0495 | 11875.2396 | 2968.8099 | 0.0099 | 2.973 | 28.8889 | 25.5556 | 18.28 | 0.0117 | 0.0101 | 101593.5104 | E410 | 3.855 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4
10 | 4655 | 478 | 15392.7327 | 12041.1342 | 3351.5985 | 0.0102 | 2.9988 | 28.8889 | 25.5556 | 18.6 | 0.0125 | 0.0105 | 101593.5104 | E420 | 3.759 | 2003-09-27 | 15 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0141 | 2002-04-17 | 3 | 0.0017 | 2001-01-04 | 24 | 71.53 | 2002-04-17 | 3 | 11.97 | 2002-11-06 | 4
11 | 5456 | 536 | 17605.0515 | 12817.5561 | 4787.4954 | 0.0107 | 2.9381 | 31.1111 | 25.8889 | 19.33 | 0.0148 | 0.0113 | 101593.5104 | E430 | 3.759 | 2003-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0156 | 2003-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2003-04-02 | 4 | 11.97 | 2002-11-06 | 4
12 | 5015 | 498 | 16187.6199 | 12610.9206 | 3576.6993 | 0.0108 | 2.9363 | 30.5556 | 25.8333 | 19.23 | 0.0134 | 0.0112 | 101593.5104 | E440 | 3.759 | 2002-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4
13 | 6036 | 600 | 19620.9933 | 17135.2122 | 2485.7811 | 0.0102 | 2.9568 | 31.1111 | 25.9444 | 18.64 | 0.0115 | 0.0104 | 101593.5104 | E500 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0118 | 2004-04-06 | 10 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
14 | 6429 | 635 | 20819.1861 | 17639.0511 | 3180.135 | 0.01 | 2.9472 | 31.6667 | 26.0556 | 18.6 | 0.0121 | 0.0103 | 101593.5104 | E510 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 3 | 7.94 | 2003-12-20 | 11 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
15 | 7683 | 754 | 25392.7185 | 22196.7561 | 3195.9624 | 0.0098 | 3.0097 | 32.2222 | 26.1111 | 18.46 | 0.0119 | 0.0101 | 101593.5104 | E520 | 4.652 | 2003-03-16 | 10 | 2.394 | 2004-04-05 | 17 | 15.94 | 2004-07-10 | 16 | 7.89 | 2003-12-20 | 12 | 0.0078 | 2004-03-29 | 10 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
16 | 8222 | 803 | 27721.1049 | 22533.2349 | 5187.87 | 0.0098 | 3.0716 | 32.2222 | 26.1667 | 18.76 | 0.0144 | 0.0105 | 101254.8653 | E522 | 5.678 | 2004-03-11 | 10 | 2.562 | 2004-03-31 | 17 | 20.11 | 2003-04-21 | 15 | 7.94 | 2003-12-20 | 11 | 0.0138 | 2004-04-06 | 10 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
17 | 5696 | 556 | 18244.5957 | 13600.1331 | 4644.4626 | 0.0107 | 2.9182 | 31.6667 | 26.0556 | 19.35 | 0.0146 | 0.0113 | 101254.8653 | E525 | 6.031 | 2004-03-16 | 10 | 2.814 | 2004-03-31 | 17 | 35.06 | 2003-04-21 | 16 | 7.94 | 2003-12-20 | 12 | 0.018 | 2002-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
18 | 5531 | 541 | 17977.8747 | 12831.6249 | 5146.2498 | 0.0112 | 2.9608 | 31.1111 | 25.9444 | 19.68 | 0.0157 | 0.0118 | 101254.8653 | E530 | 3.85 | 2004-10-13 | 9 | 2.498 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0081 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
19 | 4689 | 479 | 15914.4507 | 11871.1362 | 4043.3145 | 0.0111 | 3.0794 | 28.3333 | 25.5 | 19.4 | 0.0143 | 0.0116 | 101254.8653 | E540 | 3.455 | 2004-04-30 | 16 | 2.262 | 2012-07-30 | 12 | 15.11 | 2004-05-31 | 16 | 7.89 | 2003-12-20 | 12 | 0.0063 | 2004-04-08 | 8 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
20 | 4855 | 503 | 17120.2641 | 11534.0712 | 5586.1929 | 0.0113 | 3.1953 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104 | E545 | 4.428 | 2004-03-16 | 10 | 2.722 | 2002-07-30 | 12 | 35 | 2004-04-21 | 15 | 7.94 | 2003-12-20 | 12 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
21 | 3918 | 406 | 13445.0832 | 9302.7009 | 4142.3823 | 0.0113 | 3.1094 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104
22 | 3823 | 399 | 13285.0506 | 8973.8427 | 4311.2079 | 0.0114 | 3.1466 | 26.6667 | 25.2222 | 19.8 | 0.0167 | 0.0122 | 101593.5104
23 | 3748 | 394 | 13192.1379 | 8787.4311 | 4404.7068 | 0.0115 | 3.185 | 26.1111 | 25.1111 | 19.84 | 0.0169 | 0.0123 | 101593.5104
24 | 3880 | 407 | 13754.3037 | 8799.7413 | 4954.5624 | 0.0117 | 3.2084 | 26.1111 | 25.1111 | 20.06 | 0.0178 | 0.0126 | 101593.5104
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3975.1667 | 3119.6667 | 389.0833 | 466.4167 | 13732.9074 | 9925.0255 | 3807.8819 | 0.011 | 3.9139 | 16.8333 | 24.9444
June 25 | 5204.0833 | 4263.4167 | 426.3333 | 514.3333 | 13837.3853 | 9981.0931 | 3856.2923 | 0.0115 | 2.9506 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3061.7917 | 2389.9167 | 311.125 | 360.75 | 9721.3943 | 9721.3943 | 0 | 0.0071 | 3.5991 | 16.8333 | 24.6667
June 25 | 3978.0833 | 3242.9583 | 339.625 | 395.5 | 9760.6941 | 9760.6697 | 0.024425 | 0.0078 | 2.7245 | 29.5 | 24.9444
enter raw doe2 results below
bold entries not changed
tk variable for compr ON
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s; ODB Date: E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor |  | ODB Date: Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Compr + Both Fans Wh: Energy Consumption; Sensible Hour: E v a p o r a t o r C o i l L o a d s
Cases | Total | Compr+cond | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans Wh: Compr + Both Fans; Sensible Date: Sensible; Latent Date: Latent; Sensible + Latent Wh: Sensible + Latent; ODB Date: ODB; Outdoor Humidity Ratio kg/kg: Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (Btu) | (Btu) | (Btu) |  | (°F) | (kg/kg) | (%) | (°F) | (kg/kg) |  | Wh | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | °F | Date | Hour | kg/kg | Date | Hour
E300 |  | 23875 | 2302 | 10880 | 263705 |  | 73310 | 3.2374 | 75.3 | 0.0092 | 48.28 | 67.8 | 0.0116 | E300 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2001-09-03 | 15 | 31455 | 2001-07-20 | 15 | 95 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 |  | 28504 | 2687 | 10880 | 332351 |  | 140223 | 3.4175 | 75.3 | 0.0113 | 58.53 |  |  | E310 | 12595 | 2002-07-20 | 15 | 23119 | 2004-06-04 | 16 | 15270 | 2001-09-03 | 15 | 37033 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 |  | 27912 | 2618 | 10880 | 329216 |  | 115136 | 3.4571 | 75.9 | 0.0101 | 51.25 |  |  | E320 | 12981 | 2002-07-20 | 15 | 31072 | 2002-04-24 | 16 | 31503 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9
E330 |  | 28558 | 2633 | 10880 | 344570 |  | 128508 | 3.5364 | 75.7 | 0.0099 | 50.65 |  |  | E330 | 13407 | 2002-07-20 | 15 | 34490 | 2002-06-14 | 15 | 40809 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9
E340 |  | 28385 | 2640 | 10880 | 338530 |  | 123209 | 3.4956 | 75.7 | 0.0099 | 50.73 |  |  | E340 | 13190 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 36011 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9
E350 |  | 19668 | 1867 | 10880 | 217109 |  | 54446 | 3.2354 | 79.1 | 0.01 | 45.55 |  |  | E350 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9393 | 2001-09-03 | 15 | 31454 | 2001-07-20 | 15
E360 |  | 43136 | 4181 | 10880 | 545390 |  | 85002 | 3.7058 | 78 | 0.0087 | 41.49 |  |  | E360 | 12726 | 2002-07-20 | 15 | 32065 | 2004-04-24 | 16 | 10336 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9
E400 |  | 19996 | 1865 | 10880 | 221853 |  | 80478 | 3.2519 | 75.3 | 0.01 | 52.25 |  |  | E400 | 11677 | 2004-09-18 | 15 | 23205 | 2002-07-20 | 15 | 32396 | 2003-09-18 | 15 | 49838 | 2003-09-18 | 15
E410 |  | 20819 | 1969 | 10880 | 228057 |  | 65451 | 3.2107 | 75.3 | 0.0095 | 49.63 |  |  | E410 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E420 |  | 22030 | 2096 | 10880 | 241836 |  | 69157 | 3.2175 | 75.3 | 0.0094 | 48.97 |  |  | E420 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E430 |  | 20931 | 1980 | 10880 | 229339 |  | 67435 | 3.2115 | 75.3 | 0.0094 | 49.3 |  |  | E430 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 11101 | 2003-05-21 | 15 | 31455 | 2001-07-20 | 15
E440 |  | 22093 | 2104 | 10880 | 242856 |  | 70587 | 3.2219 | 75.3 | 0.0093 | 48.57 |  |  | E440 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2003-07-20 | 15
E500 |  | 20453 | 1975 | 2369 | 225153 |  | 62594 | 3.2265 | 69 |  |  |  |  | E500 | 10425 | 2002-07-20 | 15 | 20008 | 2002-09-10 | 16 | 7733 | 2001-09-03 | 15 | 27706 | 2001-08-16 | 16
E500 May-Sep |  | 16033 | 1527 | 1837 | 172946 |  | 48097 | 3.1616 | 77 | 0.0114 | 57.47 |  |  | E510 | 11587 | 2002-07-20 | 15 | 22513 | 2003-07-11 | 15 | 8723 | 2003-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep |  | 31871 | 3061 | 4099 | 388998 |  | 108196 | 3.5774 | 77.2 | 0.0114 | 57.36 |  |  | E520 | 11014 | 2002-07-20 | 15 | 20154 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-07-23 | 16
E520 |  | 22519 | 2393 | 2871 | 227108 |  | 63015 | 2.956 | 56.7 |  |  |  |  | E522 | 10966 | 2002-07-20 | 15 | 20135 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27866 | 2002-08-16 | 16
E522 |  | 21600 | 2182 | 2707 | 226448 |  | 62813 | 3.0728 | 63 |  |  |  |  | E525 | 9531 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 |  | 18536 | 1643 | 1885 | 223115 |  | 62032 | 3.528 | 81.1 |  |  |  |  | E530 | Compr + Both Fans Wh: 8055; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19575; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19575; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E530 |  | 15704 | 1580 | 1833 | 159095 |  | 207 | 2.9694 | 69 |  |  |  |  | E540 | Compr + Both Fans Wh: 8939; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19766; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19766; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E540 |  | 17616 | 1939 | 2258 | 160785 |  | 365 | 2.6752 | 56.7 |  |  |  |  | E545 | Compr + Both Fans Wh: 7346; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19474; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19474; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E545 |  | 14290 | 1333 | 1501 | 157748 |  | 87 | 3.2355 | 81.1
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh/h: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compr+cond | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Btu/h) | (Btu/h) | (Btu/h) | (kg/kg) |  | (°F) | (°F) | (°F) | (kg/kg) | (kg/kg) | (in Hg) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2131 | 237 | 25742 |  | 5657 | 0.0094 | 3.5406 | 64 | 74.9 | 63.212 | 0.0114 | 0.0097 | 29.9 | E300 | 3.857 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4 | E300
2 | 2182 | 241 | 26022 |  | 5322 | 0.0093 | 3.4954 | 65 | 75.1 | enter | 0.0112 | 0.0096 | 29.9 | E310 | 4.128 | 2002-04-30 | 16 | 2.851 | 2002-12-01 | 12 | 26.72 | 2002-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0189 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.7 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4 | E310
3 | 2131 | 237 | 25746 |  | 5691 | 0.0094 | 3.5411 | 64 | 74.9 | above | 0.0114 | 0.0097 | 30 | E320 | 4.967 | 2002-10-02 | 9 | 2.805 | 2003-12-01 | 15 | 31.5 | 2003-07-08 | 16 | 10.78 | 2001-01-06 | 7 | 0.0176 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.67 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4 | E320
4 | 2126 | 236 | 25685 |  | 5646 | 0.0094 | 3.5411 | 64 | 74.9 |  | 0.0114 | 0.0097 | 30 | E330 | 5.595 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 32 | 2003-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 13 | 0.0017 | 2001-01-04 | 24 | 77.94 | 2003-09-18 | 9 | 11.97 | 2002-11-06 | 4 | E330
5 | 1909 | 215 | 23040 |  | 3689 | 0.009 | 3.5375 | 63 | 74.8 |  | 0.0103 | 0.0092 | 30 | E340 | 5.339 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 31.56 | 2003-07-08 | 16 | 8.83 | 2001-01-06 | 6 | 0.0174 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.26 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4 | E340
6 | 2392 | 259 | 27926 |  | 5959 | 0.0092 | 3.4219 | 67 | 75.4 |  | 0.0113 | 0.0095 | 30 | E350 | 3.863 | 2004-10-05 | 3 | 2.801 | 2003-12-01 | 12 | 34.94 | 2004-06-24 | 24 | 8.83 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4 | E350
7 | 3576 | 353 | 38324 |  | 9843 | 0.0098 | 3.1412 | 77 | 76.9 |  | 0.0133 | 0.0103 | 30 | E360 | 4.427 | 2002-10-04 | 24 | 2.801 | 2003-12-01 | 12 | 32.56 | 2004-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4 | E360
8 | 3480 | 335 | 35045 |  | 4103 | 0.0094 | 2.9516 | 81 | 77.5 |  | 0.0109 | 0.0096 | 30 | E400 | 4.776 | 2003-09-18 | 15 | 2.735 | 2003-12-03 | 13 | 28.83 | 2002-09-18 | 16 | 8.83 | 2001-01-06 | 6 | 0.017 | 2003-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2003-04-05 | 21 | 11.97 | 2002-11-06 | 4 | E400
9 | 4993 | 467 | 50645 |  | 10129 | 0.0099 | 2.973 | 84 | 78 |  | 0.0117 | 0.0101 | 30 | E410 | 3.855 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4 | E410
10 | 5133 | 478 | 52517 |  | 11435 | 0.0102 | 2.9988 | 84 | 78 |  | 0.0125 | 0.0105 | 30 | E420 | 3.759 | 2003-09-27 | 15 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0141 | 2002-04-17 | 3 | 0.0017 | 2001-01-04 | 24 | 71.53 | 2002-04-17 | 3 | 11.97 | 2002-11-06 | 4 | E420
11 | 5992 | 536 | 60065 |  | 16334 | 0.0107 | 2.9381 | 88 | 78.6 |  | 0.0148 | 0.0113 | 30 | E430 | 3.759 | 2003-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0156 | 2003-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2003-04-02 | 4 | 11.97 | 2002-11-06 | 4 | E430
12 | 5513 | 498 | 55229 |  | 12203 | 0.0108 | 2.9363 | 87 | 78.5 |  | 0.0134 | 0.0112 | 30 | E440 | 3.759 | 2002-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4 | E440
13 | 6636 | 600 | 66943 |  | 8481 | 0.0102 | 2.9568 | 88 | 78.7 |  | 0.0115 | 0.0104 | 30 | E500 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0118 | 2004-04-06 | 10 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E500
14 | 7064 | 635 | 71031 |  | 10850 | 0.01 | 2.9472 | 89 | 78.9 |  | 0.0121 | 0.0103 | 30 | E510 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 3 | 7.94 | 2003-12-20 | 11 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E510
15 | 8437 | 754 | 86635 |  | 10904 | 0.0098 | 3.0097 | 90 | 79 |  | 0.0119 | 0.0101 | 30 | E520 | 4.652 | 2003-03-16 | 10 | 2.394 | 2004-04-05 | 17 | 15.94 | 2004-07-10 | 16 | 7.89 | 2003-12-20 | 12 | 0.0078 | 2004-03-29 | 10 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E520
16 | 9025 | 803 | 94579 |  | 17700 | 0.0098 | 3.0716 | 90 | 79.1 |  | 0.0144 | 0.0105 | 29.9 | E522 | 5.678 | 2004-03-11 | 10 | 2.562 | 2004-03-31 | 17 | 20.11 | 2003-04-21 | 15 | 7.94 | 2003-12-20 | 11 | 0.0138 | 2004-04-06 | 10 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E522
17 | 6252 | 556 | 62247 |  | 15846 | 0.0107 | 2.9182 | 89 | 78.9 |  | 0.0146 | 0.0113 | 29.9 | E525 | 6.031 | 2004-03-16 | 10 | 2.814 | 2004-03-31 | 17 | 35.06 | 2003-04-21 | 16 | 7.94 | 2003-12-20 | 12 | 0.018 | 2002-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E525
18 | 6072 | 541 | 61337 |  | 17558 | 0.0112 | 2.9608 | 88 | 78.7 |  | 0.0157 | 0.0118 | 29.9 | E530 | 3.85 | 2004-10-13 | 9 | 2.498 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0081 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E530
19 | 5168 | 479 | 54297 |  | 13795 | 0.0111 | 3.0794 | 83 | 77.9 |  | 0.0143 | 0.0116 | 29.9 | E540 | 3.455 | 2004-04-30 | 16 | 2.262 | 2012-07-30 | 12 | 15.11 | 2004-05-31 | 16 | 7.89 | 2003-12-20 | 12 | 0.0063 | 2004-04-08 | 8 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E540
20 | 5358 | 503 | 58411 |  | 19059 | 0.0113 | 3.1953 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | E545 | 4.428 | 2004-03-16 | 10 | 2.722 | 2002-07-30 | 12 | 35 | 2004-04-21 | 15 | 7.94 | 2003-12-20 | 12 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E545
21 | 4324 | 406 | 45872 |  | 14133 | 0.0113 | 3.1094 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | [19 empty] | note: RH max may occur when system off
22 | 4222 | 399 | 45326 |  | 14709 | 0.0114 | 3.1466 | 80 | 77.4 |  | 0.0167 | 0.0122 | 30
23 | 4142 | 394 | 45009 |  | 15028 | 0.0115 | 3.185 | 79 | 77.2 |  | 0.0169 | 0.0123 | 30
24 | 4287 | 407 | 46927 |  | 16904 | 0.0117 | 3.2084 | 79 | 77.2 |  | 0.0178 | 0.0126 | 30
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 84210 | 9338 | 11194 | 1124496 |  | 311802 | 0.011 | 3.9139 | 62.3 | 76.9
June 25 |  | 112554 | 10232 | 12344 | 1133051 |  | 315766 | 0.0115 | 2.9506 | 85.1 | 77
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 64825 | 7467 | 8658 | 796020 |  | 0 | 0.0071 | 3.5991 | 62.3 | 76.4
June 25 |  | 85982 | 8151 | 9492 | 799238 |  | 2 | 0.0078 | 2.7245 | 85.1 | 76.9

## EnergyPlus1.0
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
ENERGYPLUS received 7/28/03
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
15
| 1999-08-16 |  | 15
Round 5 - Revision 3 - Space Humidity Ratio Algorithm Fix for E500 Cases & Case E440 enthalpy setpoint = 47250 J/kg, changed E530,540,545 max/min end time from 12/1 to 12/31; also changed note at bottom of table
EnergyPlus results with Version 1.1.0.020
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34745.6375 | 23883.5456 |  | 10862.0919 | 77317.9497 | 55251.9574 | 22065.9923 | 3.2373 | 24.0907 | 0.0092861 | 48.5913 | 19.9141 | 0.011593 | E300 | 11899.8597 | 2010-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 | 10234.8217 | 2010-07-10 | 13 | 32733.2556 | 2010-07-20 | 15 | 34.775 | 2010-07-20 | 15 | 0.021842 | 2010-10-02 | 9
E310 | 39290.3641 | 28428.2722 |  | 10862.0919 | 96447.5904 | 55225.158 | 41222.4325 | 3.3927 | 24.0921 | 0.011261 | 58.5512 |  |  | E310 | 12540.8188 | 2010-07-20 | 15 | 23276.4591 | 2010-07-11 | 16 | 16274.8379 | 2010-08-04 | 15 | 37126.4795 | 2010-09-17 | 15
E320 | 39079.1002 | 28217.0083 |  | 10862.0919 | 96083.5597 | 62043.4531 | 34040.1066 | 3.4052 | 24.2544 | 0.010114 | 51.8407 |  |  | E320 | 12954.4267 | 2010-07-20 | 15 | 31972.0849 | 2010-04-24 | 15 | 22195.4712 | 2010-10-02 | 10 | 39765.1828 | 2010-09-03 | 16
E330 | 40143.3736 | 29281.2817 |  | 10862.0919 | 102211.3604 | 63778.6556 | 38432.7048 | 3.4907 | 24.2734 | 0.0099684 | 51.1765 |  |  | E330 | 13314.1099 | 2010-07-20 | 15 | 34764.7794 | 2010-06-14 | 15 | 27134.3149 | 2010-09-18 | 16 | 43445.0808 | 2010-10-02 | 9
E340 | 39783.0185 | 28920.9266 |  | 10862.0919 | 99708.5156 | 62885.8356 | 36822.6801 | 3.4476 | 24.2983 | 0.0099837 | 51.1479 |  |  | E340 | 13134.1703 | 2010-07-20 | 15 | 32887.7843 | 2010-04-24 | 15 | 23911.2415 | 2010-10-02 | 10 | 41328.2736 | 2010-10-02 | 10
E350 | 31145.1136 | 20283.0217 |  | 10862.0919 | 65790.3681 | 48545.0123 | 17245.3558 | 3.2436 | 26.2416 | 0.0099257 | 45.1731 |  |  | E350 | 11899.8619 | 2010-07-20 | 15 | 23530.8071 | 2010-07-20 | 15 | 10235.3532 | 2010-07-10 | 13 | 32733.265 | 2010-07-20 | 15
E360 | 54704.711 | 43842.619 |  | 10862.0919 | 161248.445 | 135287.1959 | 25961.249 | 3.6779 | 25.3232 | 0.0087659 | 42.3695 |  |  | E360 | 12744.2783 | 2010-07-20 | 15 | 32620.9131 | 2010-04-24 | 16 | 8520.3176 | 2010-10-02 | 11 | 38459.7282 | 2010-10-02 | 11
E400 | 31012.681 | 20150.589 |  | 10862.0919 | 65413.8414 | 40687.7468 | 24726.0946 | 3.2462 | 24.092 | 0.010087 | 52.5485 |  |  | E400 | 11899.8597 | 2010-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 | 26317.2818 | 2010-09-16 | 14 | 40728.1422 | 2010-09-16 | 15
E410 | [13 empty] | E410
E420 | 32735.5046 | 21873.4127 |  | 10862.0919 | 70349.4668 | 49523.9279 | 20825.5388 | 3.2162 | 24.0906 | 0.0094486 | 49.3981 |  |  | E420 | 11899.8597 | 2010-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 | 10234.8217 | 2010-07-10 | 13 | 32733.2556 | 2010-07-20 | 15
E430 | 31772.397 | 20910.3051 |  | 10862.0919 | 67141.3524 | 46738.5816 | 20402.7708 | 3.2109 | 24.0906 | 0.0094895 | 49.6002 |  |  | E430 | 11899.8597 | 2010-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 | 11073.7739 | 2010-10-24 | 13 | 32733.2556 | 2010-07-20 | 15
E440 | 33031.6453 | 22169.5533 |  | 10862.0919 | 71417.307 | 50060.1752 | 21357.1318 | 3.2214 | 24.0907 | 0.0093341 | 48.8288 |  |  | E440 | 11899.8597 | 2010-07-20 | 15 | 23530.8075 | 2010-07-20 | 15 | 10234.8217 | 2010-07-10 | 13 | 32733.2556 | 2010-07-20 | 15
E500 | 23034.6081 | 20406.2816 |  | 2628.3265 | 65571.1832 | 47491.2402 | 18079.943 | 3.2133 | 20.3795 | 0.0093728 | 59.1976 |  |  | E500 | 10398.6872 | 2010-07-20 | 15 | 19849.2901 | 2010-07-20 | 15 | 7838.7203 | 2010-06-29 | 16 | 27646.4256 | 2010-06-29 | 16
E500 May-Sep | 17996.1112 | 15967.1478 |  | 2028.9634 | 50354.2901 | 36475.5877 | 13878.7023 | 3.1536 | 24.9823 | 0.011322 | 57.3219 |  |  | E510 | 11409.8034 | 2010-07-20 | 15 | 22290.3117 | 2010-07-20 | 15 | 8954.7918 | 2010-06-17 | 14 | 31177.751 | 2010-06-17 | 14
E510 May-Sep | 35732.4838 | 31669.1814 |  | 4063.3025 | 112792.6463 | 81566.3401 | 31226.3062 | 3.5616 | 24.9596 | 0.011329 | 57.4361 |  |  | E520 | 11100.5253 | 2010-07-20 | 15 | 19999.2936 | 2010-07-20 | 15 | 7698.5342 | 2010-06-29 | 16 | 27652.6954 | 2010-06-29 | 16
E520 | 25017.1776 | 21998.5084 |  | 3018.6693 | 66087.7865 | 47986.359 | 18101.4275 | 3.0042 | 13.5769 | 0.0060452 | 61.4049 |  |  | E522 | 10762.3872 | 2010-07-20 | 15 | 19933.5062 | 2010-07-20 | 15 | 7769.7702 | 2010-06-29 | 16 | 27658.7918 | 2010-06-29 | 16
E522 | 24077.7247 | 21235.1683 |  | 2842.5564 | 65850.6755 | 47757.6997 | 18092.9758 | 3.101 | 16.9966 | 0.0076074 | 60.7524 |  |  | E525 | 9569.5705 | 2010-07-20 | 15 | 19663.6722 | 2010-07-20 | 15 | 7947.3919 | 2010-06-29 | 16 | 27576.5137 | 2010-06-29 | 16
E525 | 20701.5603 | 18521.6644 |  | 2179.8959 | 64973.3114 | 46929.7377 | 18043.5737 | 3.508 | 27.1041 | 0.013802 | 54.9944 |  |  | E530 | 8171.0479 | 2010-07-20 | 15 | 19638.7657 | 2010-07-20 | 15 | 1.0587 | 2010-03-16 | 10 | 19638.7657 | 2010-07-20 | 15
E530 | 17741.9432 | 15651.7258 |  | 2090.2174 | 46944.3571 | 46944.356 | 0.0011462 | 2.9993 | 20.586 | 0.0067122 | 48.9733 |  |  | E540 | 8677.4025 | 2010-07-20 | 15 | 19726.32 | 2010-07-20 | 15 | 1654.9514 | 2010-03-11 | 10 | 19726.32 | 2010-07-20 | 15
E540 | 19061.1125 | 16751.8668 |  | 2309.2457 | 47296.6053 | 47288.0472 | 8.5582 | 2.8234 | 13.7934 | 0.0043466 | 46.3072 |  |  | E545 | 7762.756 | 2010-07-20 | 15 | 19539.7081 | 2010-07-20 | 15 | 8.2784e-12 | 2010-05-23 | 15 | 19539.7081 | 2010-07-20 | 15
E545 | 16635.7259 | 14764.8235 |  | 1870.9023 | 46611.8912 | 46611.8912 | 3.4549e-12 | 3.157 | 27.3123 | 0.0067334 | 38.6306
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [10 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum* |  | Cases
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2118.6889 |  | 7471.7175 | 5810.748 | 1660.9695 | 0.0094054 | 3.5266 | 17.9875 | 23.9453 |  | 0.011192 |  |  | E300 | 3.9252 | 2010-04-30 | 15 | 2.7815 | 2010-06-13 | 17 | 25.0025 | 2010-09-23 | 8 | 8.7175 | 2010-01-06 | 6 | 0.013626 | 2010-11-16 | 17 | 0.0019277 | 2010-01-11 | 3 | 68.3673 | 2010-11-16 | 17 | 14.4023 | 2010-11-06 | 6 | E300
2 | 2131.2588 |  | 7494.4102 | 5853.1492 | 1641.261 | 0.0093664 | 3.5164 | 18.1125 | 23.9638 |  | 0.011286 |  |  | E310 | 4.1729 | 2010-04-30 | 15 | 2.8927 | 2010-12-01 | 15 | 26.4747 | 2010-07-20 | 16 | 8.7174 | 2010-01-06 | 6 | 0.015637 | 2010-10-01 | 8 | 0.0019433 | 2010-01-05 | 7 | 78.6439 | 2010-10-02 | 8 | 15.5023 | 2010-11-06 | 8 | E310
3 | 2112.6225 |  | 7446.5844 | 5809.4072 | 1637.1772 | 0.0093723 | 3.5248 | 17.9875 | 23.9453 |  | 0.01119 |  |  | E320 | 3.9395 | 2010-09-16 | 15 | 2.8415 | 2010-03-31 | 15 | 31.7089 | 2010-07-20 | 15 | 7.7537 | 2010-01-06 | 6 | 0.017807 | 2010-07-10 | 13 | 0.0019336 | 2010-01-11 | 3 | 82.9666 | 2010-09-18 | 10 | 14.6416 | 2010-11-06 | 6 | E320
4 | 2074.7396 |  | 7331.9994 | 5743.5733 | 1588.4261 | 0.0093141 | 3.5339 | 17.8 | 23.9171 |  | 0.011051 |  |  | E330 | 4.0715 | 2010-09-16 | 14 | 2.8441 | 2010-03-31 | 15 | 31.0686 | 2010-07-08 | 16 | 8.716 | 2010-01-06 | 6 | 0.017934 | 2010-07-10 | 12 | 0.0019277 | 2010-01-11 | 3 | 76.8755 | 2010-09-03 | 10 | 14.4025 | 2010-11-06 | 6 | E330
5 | 1997.2205 |  | 7091.0224 | 5614.133 | 1476.8894 | 0.0091917 | 3.5504 | 17.425 | 23.8615 |  | 0.010479 |  |  | E340 | 3.9866 | 2010-09-16 | 15 | 2.8441 | 2010-03-31 | 15 | 31.4977 | 2010-07-20 | 15 | 8.716 | 2010-01-06 | 6 | 0.017787 | 2010-07-10 | 12 | 0.0019277 | 2010-01-11 | 3 | 80.796 | 2010-09-18 | 10 | 14.4025 | 2010-11-06 | 6 | E340
6 | 2141.5966 |  | 7425.0625 | 6015.0762 | 1409.9863 | 0.0090454 | 3.4671 | 18.575 | 24.0337 |  | 0.010637 |  |  | E350 | 4.5552 | 2010-10-13 | 1 | 2.7815 | 2010-06-13 | 17 | 35.0021 | 2010-10-01 | 2 | 8.7175 | 2010-01-06 | 6 | 0.01719 | 2010-10-02 | 1 | 0.0019277 | 2010-01-11 | 3 | 68.3673 | 2010-11-16 | 17 | 14.4023 | 2010-11-06 | 6 | E350
7 | 2869.5781 |  | 9216 | 7532.4754 | 1683.5246 | 0.0093227 | 3.2116 | 22.9 | 24.6841 |  | 0.012265 |  |  | E360 | 4.4554 | 2010-10-04 | 24 | 2.8441 | 2010-03-31 | 15 | 32.5106 | 2010-07-10 | 13 | 8.7177 | 2010-01-06 | 6 | 0.01386 | 2010-07-10 | 13 | 0.0019277 | 2010-01-11 | 3 | 68.3671 | 2010-11-16 | 17 | 14.4023 | 2010-11-06 | 6 | E360
8 | 3498.5394 |  | 10609.4108 | 8756.6552 | 1852.7556 | 0.0096417 | 3.0325 | 26.375 | 25.2076 |  | 0.011777 |  |  | E400 | 4.0715 | 2010-09-16 | 14 | 2.7815 | 2010-06-13 | 17 | 26.9099 | 2010-09-16 | 16 | 8.7175 | 2010-01-06 | 6 | 0.016876 | 2010-04-05 | 22 | 0.0019277 | 2010-01-11 | 3 | 84.6363 | 2010-04-05 | 22 | 13.9256 | 2010-11-06 | 6 | E400
9 | 4681.7762 |  | 14032.3459 | 11767.1681 | 2265.1778 | 0.0098152 | 2.9972 | 28.2625 | 25.4902 |  | 0.011572 |  |  | E410 | [24 empty] | E410
10 | 4947.6011 |  | 14777.6894 | 11996.3298 | 2781.3597 | 0.010197 | 2.9868 | 28.9 | 25.5859 |  | 0.012393 |  |  | E420 | 3.8214 | 2010-05-21 | 15 | 2.7815 | 2010-06-13 | 17 | 25.0025 | 2010-09-23 | 8 | 8.7175 | 2010-01-06 | 6 | 0.014593 | 2010-04-02 | 18 | 0.0019277 | 2010-01-11 | 3 | 73.284 | 2010-04-02 | 18 | 13.9257 | 2010-11-06 | 6 | E420
11 | 5406.6429 |  | 15905.4096 | 12488.0938 | 3417.3158 | 0.010626 | 2.9418 | 30.275 | 25.7944 |  | 0.013955 |  |  | E430 | 3.7927 | 2010-05-21 | 16 | 2.7815 | 2010-06-13 | 17 | 25.003 | 2010-05-18 | 19 | 8.7175 | 2010-01-06 | 6 | 0.016135 | 2010-04-02 | 5 | 0.0019277 | 2010-01-11 | 3 | 80.7427 | 2010-04-02 | 5 | 13.9256 | 2010-11-06 | 6 | E430
12 | 5632.385 |  | 16521.8755 | 12670.959 | 3850.9165 | 0.010942 | 2.9334 | 30.7875 | 25.8706 |  | 0.013752 |  |  | E440 | 3.8018 | 2010-05-21 | 15 | 2.7815 | 2010-06-13 | 17 | 25.003 | 2010-04-24 | 19 | 8.7175 | 2010-01-06 | 6 | 0.013626 | 2010-11-16 | 17 | 0.0019277 | 2010-01-11 | 3 | 68.3673 | 2010-11-16 | 17 | 13.9256 | 2010-11-06 | 6 | E440
13 | 7132.8035 |  | 21588.4217 | 17401.2828 | 4187.139 | 0.010387 | 3.0266 | 30.9125 | 25.8841 |  | 0.011978 |  |  | E500 | 4.198 | 2010-03-16 | 10 | 2.7055 | 2010-07-30 | 12 | 24.9998 | 2010-03-31 | 18 | 8.9388 | 2010-12-21 | 2 | 0.011685 | 2010-07-20 | 15 | 0.0070048 | 2010-12-20 | 12 | 100 | 2010-11-21 | 9 | 55.1668 | 2010-04-30 | 4 | E500
14 | 6983.3064 |  | 20677.8576 | 17591.92 | 3085.9376 | 0.0099642 | 2.961 | 31.475 | 25.9682 |  | 0.011517 |  |  | E510 | 4.6847 | 2010-10-05 | 1 | 2.8653 | 2010-03-31 | 18 | 24.9998 | 2010-03-31 | 18 | 8.9388 | 2010-12-21 | 2 | 0.011689 | 2010-07-20 | 15 | 0.0070048 | 2010-12-20 | 12 | 100 | 2010-11-21 | 9 | 55.2884 | 2010-05-04 | 3 | E510
15 | 8572.0438 |  | 26132.9897 | 22480.6555 | 3652.3342 | 0.0098097 | 3.0486 | 32.0125 | 26.0506 |  | 0.012075 |  |  | E520 | 3.9377 | 2010-04-30 | 15 | 2.5316 | 2010-07-30 | 12 | 15.0005 | 2010-04-16 | 1 | 8.835 | 2010-12-21 | 1 | 0.0070236 | 2010-07-20 | 15 | 0.0065213 | 2010-11-10 | 9 | 93.8137 | 2010-12-20 | 11 | 61.7266 | 2010-11-27 | 24 | E520
16 | 8732.6963 |  | 26664.6248 | 22557.3408 | 4107.284 | 0.0099222 | 3.0534 | 32.2 | 26.0819 |  | 0.013479 |  |  | E522 | 4.0424 | 2010-04-30 | 15 | 2.6134 | 2010-07-30 | 12 | 20.0004 | 2010-04-16 | 20 | 8.8978 | 2010-12-21 | 1 | 0.009111 | 2010-07-20 | 15 | 0.0069847 | 2010-12-20 | 12 | 100 | 2010-12-15 | 22 | 59.1798 | 2010-04-30 | 4 | E522
17 | 5718.3243 |  | 16344.6134 | 13061.4841 | 3283.1293 | 0.010633 | 2.8583 | 31.8875 | 26.0383 |  | 0.014485 |  |  | E525 | 4.704 | 2010-03-16 | 10 | 2.9396 | 2010-07-30 | 12 | 34.9995 | 2010-03-11 | 12 | 9.0147 | 2010-12-21 | 2 | 0.018486 | 2010-07-20 | 15 | 0.0070421 | 2010-12-20 | 12 | 100 | 2010-11-12 | 19 | 47.8518 | 2010-10-05 | 2 | E525
18 | 5880.5828 |  | 17193.4049 | 12869.5918 | 4323.8131 | 0.011174 | 2.9238 | 31.325 | 25.9541 |  | 0.015265 |  |  | E530 | 3.925 | 2010-03-16 | 10 | 2.532 | 2010-07-30 | 12 | 25.0003 | 2010-03-30 | 17 | 8.9381 | 2010-12-21 | 2 | 0.0067755 | 2010-03-11 | 1 | 0.0067348 | 2010-10-18 | 12 | 96.1602 | 2010-12-20 | 11 | 34.0277 | 2010-04-18 | 18 | E530
19 | 5555.1112 |  | 16877.6217 | 12169.8539 | 4707.7678 | 0.011312 | 3.0382 | 29.35 | 25.6545 |  | 0.014908 |  |  | E540 | 3.6959 | 2010-03-16 | 10 | 2.3828 | 2010-07-30 | 12 | 15.0005 | 2010-03-25 | 8 | 8.8327 | 2010-12-21 | 1 | 0.0067755 | 2010-03-11 | 1 | 0.0038186 | 2010-10-18 | 9 | 55.1794 | 2010-12-20 | 11 | 36.0017 | 2010-09-28 | 16 | E540
20 | 5259.2137 |  | 16536.4933 | 11555.6363 | 4980.857 | 0.011348 | 3.1443 | 27.6125 | 25.3924 |  | 0.015925 |  |  | E545 | 4.1661 | 2010-03-16 | 10 | 2.66 | 2010-07-30 | 12 | 35 | 2010-07-09 | 22 | 9.0132 | 2010-12-21 | 2 | 0.0067755 | 2010-12-31 | 7 | 0.0067755 | 2010-04-01 | 2 | 96.2348 | 2010-12-20 | 11 | 19.227 | 2010-04-18 | 17 | E545
21 | 4325.7083 |  | 13445.4149 | 9062.7383 | 4382.6766 | 0.011561 | 3.1083 | 27.2 | 25.332 |  | 0.016792 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 4278.8801 |  | 13386.5014 | 8952.5422 | 4433.9592 | 0.0116 | 3.1285 | 26.8875 | 25.2853 |  | 0.016752
23 | 4172.5901 |  | 13190.5663 | 8753.473 | 4437.0933 | 0.011611 | 3.1612 | 26.325 | 25.2003 |  | 0.016764
24 | 4151.9737 |  | 13196.202 | 8673.9655 | 4522.2365 | 0.011664 | 3.1783 | 26.1 | 25.1665 |  | 0.017059
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 4028.8242 | 3509.8969 |  | 518.9273 | 13655.2659 | 9883.6259 | 3771.64 | 0.010984 | 3.8497 | 16.8146 | 24.9818
June 25 | 5228.78 | 4663.2403 |  | 565.5397 | 13733.0749 | 9952.5713 | 3780.5037 | 0.011459 | 2.9431 | 29.5167 | 24.9828
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3101.4372 | 2689.0399 |  | 412.3973 | 9775.2401 | 9775.2401 | 5.713e-13 | 0.0067531 | 3.4414 | 16.8146 | 25
June 25 | 4028.6999 | 3578.6202 |  | 450.0798 | 9835.1361 | 9835.1361 | 6.6831e-13 | 0.0067531 | 2.7795 | 29.5167 | 25
Note 1 - Condenser fan power included with compressor power; cannot breakout

## CodyRun
E300OUT2.XLS, Mar 20, 2002 | [5 empty] | HVAC BESTEST model Cody-Tau, Neural Network + Linear Extrapolation + rint + Enthalpy
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545 | [5 empty] | Output file Name |  | BESTEST300N2_nn_int.xls
CODYRUN results received 07 May 2003
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [15 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity | Relative |  |  | Energy Consumption |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Humidity | Cases |  | Compr + Both Fans |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) | (%) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34976.411 | 21770.001 | 2326.49 | 10879.92 | 77744.589 | 55209.465 | 22535.143 | 3.2264 | 24.0816 | 0.0091748 | 47.8261 | 19.9145 | 0.011649 | 0.47826 | E300 | 11932 | 1900-07-20 | 15 | 23457 | 1900-07-20 | 15 | 10375 | 1900-09-03 | 15 | 32502 | 1900-07-20 | 15 | 35 | 1900-07-20 | 15 | 0.022406 | 1900-10-02 | 9
E310 | 39519.569 | 25936.821 | 2702.828 | 10879.92 | 97295.866 | 55185.072 | 42110.836 | 3.3972 | 24.0897 | 0.011175 | 57.841 |  |  | 0.57841 | E310 | 12653 | 1900-07-20 | 15 | 23078 | 1900-09-10 | 15 | 16112 | 1900-08-04 | 15 | 37261 | 1900-09-03 | 15
E320 | 39400.815 | 25846.026 | 2674.869 | 10879.92 | 97141.307 | 62008.804 | 35132.592 | 3.406 | 24.3274 | 0.010049 | 51.1034 |  |  | 0.51103 | E320 | 13104 | 1900-07-20 | 15 | 31134 | 1900-06-03 | 16 | 21697 | 1900-09-17 | 12 | 39904 | 1900-09-03 | 16
E330 | 40535.137 | 26927.733 | 2727.484 | 10879.92 | 103712.915 | 62649.459 | 41063.373 | 3.4973 | 24.2955 | 0.0098116 | 50.0848 |  |  | 0.50085 | E330 | 13467 | 1900-07-20 | 15 | 33997 | 1900-04-24 | 16 | 28184 | 1900-09-18 | 15 | 43978 | 1900-10-02 | 9
E340 | 40065.261 | 26472.79 | 2712.551 | 10879.92 | 100676.21 | 62380.56 | 38295.624 | 3.4495 | 24.3089 | 0.0098683 | 50.2967 |  |  | 0.50297 | E340 | 13277 | 1900-07-20 | 15 | 32940 | 1900-04-24 | 16 | 24225 | 1900-09-03 | 17 | 41366 | 1900-09-03 | 15
E350 | 31586.592 | 18738.055 | 1968.617 | 10879.92 | 66860.163 | 48588.802 | 18271.394 | 3.2289 | 26.2686 | 0.0097585 | 44.3162 |  |  | 0.44316 | E350 | 11932 | 1900-07-20 | 15 | 23457 | 1900-07-20 | 15 | 10755 | 1900-10-02 | 8 | 32502 | 1900-07-20 | 15
E360 | 54843.258 | 39697.162 | 4266.176 | 10879.92 | 161200.179 | 134205.707 | 26994.482 | 3.6667 | 25.4809 | 0.0085524 | 40.871 |  |  | 0.40871 | E360 | 12863 | 1900-07-20 | 15 | 31981 | 1900-04-24 | 16 | 8859 | 1900-09-03 | 17 | 38322 | 1900-10-02 | 10
E400 | [14 empty] | E400 | bar: Wh to Sensible + Latent Hour
E410 | [14 empty] | E410 | bar: Wh to Sensible + Latent Hour
E420 | [14 empty] | E420 | bar: Wh to Sensible + Latent Hour
E430 | [14 empty] | E430 | bar: Wh to Sensible + Latent Hour
E440 | [14 empty] | E440 | bar: Wh to Sensible + Latent Hour
E500 | 22322.953 | 17857.852 | 1911.869 | 2553.232 | 63105.366 | 44874.225 | 18231.141 | 3.192 | 21.0978 | 0.010218 | 65.9419 |  |  | 0.65942 | E500 | 10177 | 1900-07-20 | 15 | 18776 | 1900-06-04 | 15 | 7805 | 1900-06-29 | 16 | 26567 | 1900-06-29 | 16
E500 May-Sep | 17434.537 | 13988.512 | 1475.528 | 1970.497 | 48439.57 | 34448.151 | 13991.418 | 3.1324 | 25 | 0.011329 | 57.0722 |  |  | 0.57072 | E510 | 11186 | 1900-07-20 | 15 | 21121 | 1900-06-04 | 13 | 8850 | 1900-06-17 | 14 | 29948 | 1900-06-17 | 14
E510 May-Sep | 34848.637 | 27901.957 | 2974.4 | 3972.28 | 108979.013 | 77498.985 | 31479.856 | 3.5295 | 25 | 0.011328 | 57.0615 |  |  | 0.57062 | E520 | 11044 | 1900-07-20 | 15 | 18969 | 1900-07-20 | 16 | 7726 | 1900-06-30 | 16 | 26675 | 1900-07-20 | 16
E520 | 25131.07 | 19654.972 | 2344.827 | 3131.271 | 63212.102 | 44976.724 | 18235.133 | 2.8733 | 14.1421 | 0.0070234 | 70.2268 |  |  | 0.70227 | E522 | 10639 | 1900-07-20 | 15 | 18785 | 1900-06-04 | 15 | 7743 | 1900-06-29 | 16 | 26514 | 1900-06-29 | 16
E522 | 23619.744 | 18689.799 | 2110.833 | 2819.112 | 63157.03 | 44924.113 | 18233.151 | 3.0363 | 17.729 | 0.0085797 | 68.2314 |  |  | 0.68231 | E525 | 9419 | 1900-07-20 | 15 | 18759 | 1900-06-04 | 15 | 7938 | 1900-06-29 | 16 | 26683 | 1900-06-29 | 16
E525 | 20241.713 | 16506.802 | 1599.203 | 2135.708 | 63001.558 | 44775.105 | 18226.509 | 3.4796 | 27.7709 | 0.01398 | 60.1387 |  |  | 0.60139 | E530 | 7992 | 1900-07-20 | 15 | 18776 | 1900-06-04 | 15 | 179 | 1900-03-11 | 11 | 18776 | 1900-06-04 | 15
E530 | 17442.468 | 13855.928 | 1535.684 | 2050.856 | 44875.414 | 44874.225 | 1.186 | 2.9156 | 21.0978 | 0.0057975 | 41.4516 |  |  | 0.41452 | E540 | 8846 | 1900-07-20 | 15 | 18794 | 1900-06-04 | 15 | 845 | 1900-03-11 | 10 | 18794 | 1900-06-04 | 15
E540 | 19536.572 | 15163.82 | 1872.336 | 2500.416 | 44979.842 | 44976.747 | 3.09 | 2.6403 | 14.1406 | 0.0038546 | 40.0509 |  |  | 0.40051 | E545 | 7351 | 1900-07-20 | 15 | 18759 | 1900-06-04 | 15 | 4 | 1900-07-20 | 15 | 18764 | 1900-07-20 | 15
E545 | 15791.081 | 12750.623 | 1301.791 | 1738.667 | 44775.11 | 44775.105 | 0.004 | 3.1863 | 27.7166 | 0.006749 | 36.8747 |  |  | 0.36875
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [11 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum*
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour | MaxRH | MinRH
1 | 1886 | 237 | 7472 | 5788 | 1684 | 0.009276 | 3.5195 | 17.8 | 23.92 | 17.155 | 0.0111 |  |  |  | E300 | 3.8706 | 1900-04-30 | 16 | 2.7856 | 1900-06-13 | 17 | 25.05 | 1900-02-20 | 17 | 8 | 1900-01-05 | 5 | 0.013457 | 1900-11-16 | 16 | 0.001968 | 1900-01-10 | 3 | 68 | 1900-11-16 | 16 | 15 | 1900-11-06 | 5
2 | 1964 | 244 | 7707 | 5961 | 1747 | 0.009302 | 3.4905 | 18.3 | 24 | 17.238 | 0.011462 |  |  |  | E310 | 4.1276 | 1900-04-30 | 15 | 2.8726 | 1900-12-01 | 15 | 26.62 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.015432 | 1900-10-02 | 8 | 0.002019 | 1900-01-04 | 7 | 77 | 1900-06-12 | 8 | 16 | 1900-11-06 | 8
3 | 1881 | 236 | 7445 | 5788 | 1657 | 0.009239 | 3.5168 | 17.8 | 23.92 | 17.12 | 0.0111 |  |  |  | E320 | 3.9433 | 1900-09-16 | 15 | 2.8145 | 1900-03-31 | 15 | 32.32 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.017547 | 1900-07-10 | 12 | 0.001968 | 1900-01-10 | 3 | 83 | 1900-09-03 | 17 | 15 | 1900-11-06 | 5
4 | 1878 | 236 | 7432 | 5788 | 1644 | 0.009201 | 3.5156 | 17.8 | 23.92 | 17.102 | 0.0111 |  |  |  | E330 | 4.1219 | 1900-06-17 | 16 | 2.8233 | 1900-03-31 | 15 | 31.9 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.017045 | 1900-07-10 | 13 | 0.001968 | 1900-01-10 | 3 | 76 | 1900-06-10 | 18 | 15 | 1900-11-06 | 5
5 | 1756 | 224 | 7000 | 5580 | 1420 | 0.008969 | 3.5354 | 17.2 | 23.83 | 16.787 | 0.01018 |  |  |  | E340 | 4.0172 | 1900-09-16 | 16 | 2.8233 | 1900-03-31 | 15 | 32.15 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.017272 | 1900-07-10 | 13 | 0.001968 | 1900-01-10 | 3 | 80 | 1900-09-03 | 17 | 15 | 1900-11-06 | 5
6 | 2075 | 253 | 7915 | 6341 | 1574 | 0.009012 | 3.3999 | 19.4 | 24.16 | 17.032 | 0.011001 |  |  |  | E350 | 3.9321 | 1900-10-04 | 24 | 2.7859 | 1900-06-13 | 17 | 35 | 1900-04-21 | 1 | 8 | 1900-01-05 | 5 | 0.016479 | 1900-10-02 | 2 | 0.001968 | 1900-01-10 | 3 | 70 | 1900-10-02 | 8 | 15 | 1900-11-06 | 5
7 | 3035 | 334 | 10450 | 8277 | 2173 | 0.00949 | 3.1018 | 25 | 25 | 17.911 | 0.01314 |  |  |  | E360 | 4.432 | 1900-10-04 | 24 | 2.8233 | 1900-03-31 | 15 | 33 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.013457 | 1900-11-16 | 16 | 0.001968 | 1900-01-10 | 3 | 68 | 1900-11-16 | 16 | 15 | 1900-11-06 | 5
8 | 3303 | 352 | 10813 | 9038 | 1775 | 0.009314 | 2.9584 | 27.2 | 25.33 | 17.646 | 0.011075 |  |  |  | E400
9 | 4483 | 463 | 14631 | 11971 | 2660 | 0.009708 | 2.9581 | 28.9 | 25.59 | 18.118 | 0.011995 |  |  |  | E410
10 | 4594 | 472 | 15099 | 11971 | 3128 | 0.010041 | 2.9805 | 28.9 | 25.59 | 18.442 | 0.01276 |  |  |  | E420
11 | 5238 | 516 | 16722 | 12731 | 3991 | 0.010588 | 2.9062 | 31.1 | 25.91 | 19.142 | 0.014809 |  |  |  | E430
12 | 5066 | 504 | 16258 | 12559 | 3699 | 0.01058 | 2.9189 | 30.6 | 25.84 | 18.935 | 0.013253 |  |  |  | E440
13 | 6442 | 642 | 21090 | 17422 | 3669 | 0.009975 | 2.9771 | 31.1 | 25.91 | 18.326 | 0.011329 |  |  |  | E500 | 4.1846 | 1900-03-16 | 10 | 2.6665 | 1900-07-30 | 12 | 25.02 | 1900-03-30 | 17 | 8.54 | 1900-12-20 | 20 | 0.011713 | 1900-07-20 | 15 | 0.006908 | 1900-12-20 | 20 | 100 | 1900-11-14 | 5 | 54 | 1900-10-04 | 24
14 | 6523 | 645 | 21067 | 17629 | 3438 | 0.009778 | 2.939 | 31.7 | 26 | 18.269 | 0.011729 |  |  |  | E510 | 4.6896 | 1900-10-04 | 24 | 2.8817 | 1900-03-31 | 15 | 25.02 | 1900-03-30 | 17 | 8.54 | 1900-12-20 | 20 | 0.011716 | 1900-07-20 | 15 | 0.006908 | 1900-12-20 | 20 | 100 | 1900-11-14 | 5 | 54 | 1900-10-04 | 23
15 | 8000 | 785 | 26636 | 22491 | 4145 | 0.009579 | 3.032 | 32.2 | 26.08 | 18.239 | 0.012379 |  |  |  | E520 | 3.8017 | 1900-04-30 | 16 | 2.3333 | 1900-01-28 | 10 | 15.98 | 1900-07-20 | 15 | 8.51 | 1900-12-20 | 20 | 0.007566 | 1900-07-20 | 15 | 0.006525 | 1900-11-27 | 23 | 95 | 1900-12-20 | 17 | 61 | 1900-11-27 | 22
16 | 8169 | 799 | 27416 | 22491 | 4925 | 0.009733 | 3.0571 | 32.2 | 26.08 | 18.557 | 0.014232 |  |  |  | E522 | 3.9858 | 1900-04-30 | 16 | 2.4286 | 1900-03-30 | 17 | 20.05 | 1900-03-13 | 22 | 8.54 | 1900-12-20 | 20 | 0.009398 | 1900-07-20 | 15 | 0.006908 | 1900-12-20 | 20 | 100 | 1900-12-15 | 1 | 60 | 1900-10-04 | 23
17 | 5306 | 519 | 16702 | 12939 | 3763 | 0.01044 | 2.8673 | 31.7 | 26 | 19.063 | 0.01473 |  |  |  | E525 | 4.6381 | 1900-03-16 | 10 | 2.8941 | 1900-07-29 | 12 | 35 | 1900-03-11 | 10 | 8.54 | 1900-12-20 | 20 | 0.017626 | 1900-07-20 | 15 | 0.006909 | 1900-12-20 | 20 | 100 | 1900-11-11 | 23 | 44 | 1900-05-04 | 4
18 | 5381 | 528 | 17312 | 12729 | 4582 | 0.010912 | 2.9298 | 31.1 | 25.91 | 19.458 | 0.015684 |  |  |  | E530 | 3.84 | 1900-03-16 | 10 | 2.4733 | 1900-07-29 | 12 | 25.02 | 1900-03-30 | 17 | 8.54 | 1900-12-20 | 20 | 0.005491 | 1900-04-01 | 1 | 0.005454 | 1900-11-01 | 21 | 79 | 1900-12-20 | 8 | 28 | 1900-04-01 | 10
19 | 4791 | 492 | 16232 | 11761 | 4470 | 0.010914 | 3.0725 | 28.3 | 25.5 | 19.199 | 0.014539 |  |  |  | E540 | 3.6667 | 1900-03-11 | 22 | 2.1429 | 1900-04-05 | 20 | 15.05 | 1900-01-27 | 20 | 8.51 | 1900-12-20 | 20 | 0.003256 | 1900-04-01 | 1 | 0.003253 | 1900-04-29 | 23 | 47 | 1900-12-20 | 6 | 31 | 1900-04-01 | 1
20 | 4809 | 498 | 16867 | 11381 | 5486 | 0.011269 | 3.1783 | 27.2 | 25.33 | 19.65 | 0.016878 |  |  |  | E545 | 4.1565 | 1900-03-16 | 10 | 2.692 | 1900-07-29 | 12 | 35 | 1900-03-11 | 10 | 8.54 | 1900-12-20 | 20 | 0.006689 | 1900-04-01 | 1 | 0.006685 | 1900-07-20 | 15 | 97 | 1900-12-20 | 4 | 19 | 1900-04-01 | 10
21 | 3939 | 408 | 13484 | 9036 | 4447 | 0.011348 | 3.1019 | 27.2 | 25.33 | 19.706 | 0.016878 |  |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 3852 | 402 | 13322 | 8864 | 4459 | 0.011383 | 3.1316 | 26.7 | 25.25 | 19.697 | 0.016832
23 | 3752 | 395 | 13139 | 8656 | 4482 | 0.011416 | 3.1683 | 26.1 | 25.16 | 19.694 | 0.016889
24 | 3794 | 399 | 13323 | 8656 | 4666 | 0.011507 | 3.1774 | 26.1 | 25.16 | 19.805 | 0.017329
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3901.0417 | 3020.0417 | 377.25 | 503.75 | 13169.5417 | 9365.4583 | 3804.375 | 0.010938 | 3.8372 | 16.8833 | 25
June 25 | 5066.5 | 4105.9583 | 411.3333 | 549.2083 | 13198.0833 | 9387.625 | 3810.4167 | 0.011479 | 2.9213 | 29.5167 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3091.5417 | 2378.4583 | 305.3333 | 407.75 | 9365.4583 | 9365.4583 | 0 | 0.005485 | 3.4604 | 16.8833 | 25
June 25 | 3934.625 | 3165.5833 | 329.25 | 439.7917 | 9387.625 | 9387.625 | 0 | 0.005478 | 2.69 | 29.5167 | 25

## HOT3000
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
HOT3000 received 07/21/03
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
HOT3000 received 07/21/03
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 35070 | 21876 | 2323 | 10880 | 78257 | 55191 | 23067 | 3.23 | 23.99 | 0.0092 | 47.93 | 19.91 | 0.0116 | E300 | 11548 | 2003-07-20 | 15 | 22908 | 2003-06-04 | 15 | 10392 | 2003-09-03 | 15 | 32072 | 2003-07-20 | 15 | 35 | 2003-07-20 | 15 | 0.0223 | 2003-10-02 | 9
E310 | 39608 | 26053 | 2691 | 10880 | 97261 | 55083 | 42178 | 3.38 | 24.01 | 0.0111 | 57.8 |  |  | E310 | 12162 | 2003-08-16 | 16 | 22649 | 2003-06-13 | 16 | 16077 | 2003-09-03 | 16 | 36991 | 2003-09-03 | 16
E320 | 39457 | 25912 | 2681 | 10880 | 96957 | 62734 | 34224 | 3.39 | 24.53 | 0.0099 | 49.94 |  |  | E320 | 12875 | 2003-07-20 | 14 | 30967 | 2003-04-24 | 15 | 21929 | 2003-10-01 | 20 | 39920 | 2003-09-03 | 16
E330 | 40330 | 26775 | 2693 | 10880 | 102008 | 61822 | 40186 | 3.46 | 24.18 | 0.0099 | 50.7 |  |  | E330 | 13335 | 2003-07-20 | 15 | 33421 | 2003-09-09 | 14 | 27488 | 2003-09-18 | 15 | 42415 | 2003-07-10 | 11
E340 | 39947 | 26400 | 2684 | 10880 | 99753 | 61406 | 38346 | 3.42 | 24.21 | 0.0099 | 50.78 |  |  | E340 | 13101 | 2003-07-20 | 14 | 32180 | 2003-04-24 | 15 | 23794 | 2003-10-01 | 20 | 41132 | 2003-09-03 | 16
E350 | 31742 | 18891 | 1970 | 10880 | 67389 | 48768 | 18621 | 3.23 | 26.15 | 0.00977 | 44.56 |  |  | E350 | 11546 | 2003-07-20 | 15 | 22876 | 2003-07-10 | 15 | 11603 | 2003-08-03 | 7 | 32077 | 2003-07-20 | 15
E360 | 55068 | 39941 | 4272 | 10880 | 162168 | 134697 | 27470 | 3.66 | 25.37 | 0.00858 | 41.21 |  |  | E360 | 12762 | 2003-07-20 | 14 | 32179 | 2003-04-24 | 15 | 8934 | 2003-09-03 | 17 | 38451 | 2003-10-02 | 10
E400 | 31413 | 18629 | 1902 | 10880 | 66898 | 41181 | 25717 | 3.26 | 23.99 | 0.01 | 52.01 |  |  | E400 | 11519 | 2003-07-20 | 15 | 22877 | 2003-07-08 | 16 | 26645 | 2003-09-16 | 14 | 40774 | 2003-09-16 | 14
E410 | 31503 | 18685 | 1936 | 10880 | 66175 | 45585 | 20590 | 3.21 | 23.99 | 0.0095 | 49.75 |  |  | E410 | 11549 | 2003-07-20 | 15 | 22893 | 2003-07-29 | 15 | 10377 | 2003-09-09 | 15 | 32073 | 2003-07-20 | 15
E420 | 33208 | 20214 | 2115 | 10880 | 71803 | 49984 | 21855 | 3.21 | 23.99 | 0.0093 | 48.76 |  |  | E420 | 11548 | 2003-07-20 | 15 | 22893 | 2003-07-29 | 15 | 10394 | 2003-09-03 | 15 | 32072 | 2003-07-20 | 15
E430 | 31818 | 18966 | 1970 | 10880 | 67200 | 46143 | 21057 | 3.21 | 23.99 | 0.0094 | 49.17 |  |  | E430 | 11548 | 2003-07-20 | 15 | 22893 | 2003-07-29 | 15 | 10394 | 2003-09-03 | 15 | 32072 | 2003-07-20 | 15
E440 | 33248 | 20249 | 2120 | 10880 | 72029 | 49785 | 22244 | 3.22 | 23.99 | 0.0092 | 48.23 |  |  | E440 | 11461 | 2003-08-16 | 16 | 22875 | 2003-08-16 | 16 | 10139 | 2003-09-03 | 15 | 31777 | 2003-07-08 | 16
E500 | 23138 | 18522 | 1976 | 2639 | 65614 | 47530 | 18084 | 3.2 | 22.86 | 0.0107 | 63.73 |  |  | E500 | 10274 | 2003-06-04 | 15 | 19818 | 2003-07-29 | 15 | 7762 | 2003-06-29 | 15 | 27555 | 2003-06-29 | 15
E500 May-Sep | 18051 | 14491 | 1524 | 2035 | 50357 | 36480 | 13877 | 3.14 | 25 | 0.0109 | 55.13 |  |  | E510 | 11344 | 2003-07-20 | 14 | 22269 | 2003-07-20 | 14 | 8874 | 2003-06-17 | 13 | 31097 | 2003-06-17 | 13
E510 May-Sep | 35845 | 28721 | 3050 | 4073 | 112781 | 81563 | 31217 | 3.55 | 25 | 0.0109 | 55.24 |  |  | E520 | 10684 | 2003-06-04 | 15 | 20378 | 2003-05-23 | 15 | 7964 | 2003-05-23 | 15 | 28343 | 2003-05-23 | 15
E520 | 25781 | 20185 | 2396 | 3200 | 66146 | 48059 | 18087 | 2.92 | 14.89 | 0.00763 | 72.17 |  |  | E522 | 10747 | 2003-08-16 | 15 | 19920 | 2003-08-16 | 15 | 7745 | 2003-06-29 | 15 | 27636 | 2003-06-29 | 15
E522 | 24360 | 19281 | 2174 | 2904 | 65900 | 47795 | 18104 | 3.07 | 18.7 | 0.00901 | 68.11 |  |  | E525 | 9585 | 2003-08-16 | 15 | 19661 | 2003-06-04 | 15 | 7820 | 2003-06-29 | 15 | 27462 | 2003-06-29 | 15
E525 | 21323 | 17443 | 1663 | 2221 | 65155 | 47110 | 18045 | 3.41 | 30.69 | 0.0151 | 57.37 |  |  | E530 | 8089 | 2003-08-16 | 15 | 19626 | 2003-07-08 | 15 | 35.9 | 2003-11-01 | 20 | 19626 | 2003-07-08 | 15
E530 | 17875 | 14172 | 1585 | 2117 | 47002 | 47002 | 0 | 2.98 | 22.86 | 0.00667 | 39.6 |  |  | E540 | 8985 | 2003-08-16 | 15 | 19799 | 2003-08-16 | 15 | 1181 | 2003-03-11 | 10 | 19799 | 2003-08-16 | 15
E540 | 20164 | 15664 | 1926 | 2573 | 47462 | 47460 | 2 | 2.69 | 14.98 | 0.00463 | 43.82 |  |  | E545 | 7471 | 2003-06-04 | 15 | 19497 | 2003-06-04 | 15 | 0 | 2003-01-01 | 1 | 19497 | 2003-06-04 | 15
E545 | 16339 | 13215 | 1337 | 1786 | 46668 | 46668 | 0 | 3.2 | 30.69 | 0.00722 | 29.2
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [10 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum*
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1942.81 | 240.938 | 7667.56 | 5870.06 | 1797.5 | 0.0092502 | 3.5112 | 17.8 | 23.9367 | 17.3042 | 0.011072 |  |  | E300 | 3.88 | 2003-04-30 | 16 | 2.81 | 2003-06-14 | 12 | 26.19 | 2003-11-03 | 15 | 6.99 | 2003-01-06 | 5 | 0.0134 | 2003-11-16 | 16 | 0.00197 | 2003-01-05 | 6 | 67.44 | 2003-11-16 | 16 | 14.94 | 2003-11-06 | 8
2 | 1950.53 | 241.104 | 7674.46 | 5871.7 | 1802.77 | 0.0092582 | 3.5017 | 18.3 | 23.9367 | 17.31 | 0.011432 |  |  | E310 | 4.12 | 2003-04-30 | 15 | 2.87 | 2003-12-01 | 14 | 27.19 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0157 | 2003-10-02 | 8 | 0.00196 | 2003-01-05 | 7 | 78.19 | 2003-10-02 | 8 | 15.93 | 2003-11-06 | 8
3 | 1902.33 | 236.85 | 7527.94 | 5782.88 | 1745.07 | 0.0092068 | 3.5191 | 17.8 | 23.8958 | 17.2367 | 0.011072 |  |  | E320 | 4.38 | 2003-12-18 | 3 | 2.83 | 2003-03-31 | 14 | 31.65 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0177 | 2003-07-10 | 12 | 0.00197 | 2003-01-05 | 6 | 81.88 | 2003-09-16 | 20 | 12.92 | 2003-12-20 | 5
4 | 1845.43 | 231.118 | 7317.22 | 5683.06 | 1634.17 | 0.0091047 | 3.5238 | 17.8 | 23.8375 | 17.0785 | 0.011072 |  |  | E330 | 4.05 | 2003-06-17 | 16 | 2.84 | 2003-03-31 | 14 | 31.3 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0177 | 2003-07-10 | 12 | 0.00197 | 2003-01-05 | 6 | 78.7 | 2003-09-02 | 12 | 14.94 | 2003-11-06 | 8
5 | 1914.46 | 238.687 | 7514.35 | 5955.01 | 1559.34 | 0.0089519 | 3.4899 | 17.2 | 23.9757 | 17.0075 | 0.010155 |  |  | E340 | 3.95 | 2003-09-16 | 16 | 2.84 | 2003-03-31 | 14 | 31.58 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0177 | 2003-07-10 | 12 | 0.00197 | 2003-01-05 | 6 | 80.25 | 2003-09-16 | 20 | 14.94 | 2003-11-06 | 8
6 | 2506.57 | 292.588 | 9222.93 | 7311.79 | 1911.15 | 0.0091583 | 3.2949 | 19.4 | 24.5756 | 17.5412 | 0.01097 |  |  | E350 | 3.88 | 2003-04-30 | 16 | 2.81 | 2003-06-14 | 12 | 35 | 2003-04-21 | 2 | 6.99 | 2003-01-06 | 5 | 0.0166 | 2003-10-02 | 1 | 0.00197 | 2003-01-05 | 6 | 72.65 | 2003-08-03 | 7 | 14.94 | 2003-11-06 | 8
7 | 3170.95 | 342.969 | 10769.5 | 8646.87 | 2122.59 | 0.0094778 | 3.0648 | 25 | 25.1643 | 17.9926 | 0.013099 |  |  | E360 | 4.44 | 2003-10-04 | 24 | 2.84 | 2003-03-31 | 14 | 33.13 | 2003-07-10 | 12 | 6.99 | 2003-01-06 | 5 | 0.0134 | 2003-11-16 | 16 | 0.00197 | 2003-01-05 | 6 | 67.44 | 2003-11-16 | 16 | 14.94 | 2003-11-06 | 8
8 | 3433.96 | 360.598 | 11186.4 | 9298.63 | 1887.81 | 0.0093737 | 2.948 | 27.2 | 25.4533 | 17.9591 | 0.011039 |  |  | E400 | 4.05 | 2003-06-17 | 16 | 2.81 | 2003-06-14 | 12 | 26.04 | 2003-08-15 | 15 | 6.99 | 2003-01-06 | 5 | 0.0173 | 2003-04-22 | 6 | 0.00197 | 2003-01-05 | 6 | 86.31 | 2003-04-22 | 6 | 14.57 | 2003-11-06 | 5
9 | 4489.15 | 460.788 | 14744.4 | 11923.2 | 2821.19 | 0.0097161 | 2.9787 | 28.9 | 25.5785 | 18.3251 | 0.011957 |  |  | E410 | 3.84 | 2003-05-21 | 15 | 2.81 | 2003-06-14 | 12 | 26.19 | 2003-11-03 | 15 | 6.99 | 2003-01-06 | 5 | 0.0173 | 2003-04-22 | 6 | 0.00197 | 2003-01-05 | 6 | 86.18 | 2003-04-22 | 6 | 14.58 | 2003-11-06 | 5
10 | 4853.28 | 489.455 | 15882.1 | 12287.1 | 3595.03 | 0.010237 | 2.9726 | 28.9 | 25.7393 | 18.8543 | 0.012719 |  |  | E420 | 3.94 | 2003-05-21 | 13 | 2.81 | 2003-06-14 | 12 | 26.23 | 2003-10-20 | 15 | 6.99 | 2003-01-06 | 5 | 0.0147 | 2003-04-02 | 18 | 0.00197 | 2003-01-05 | 6 | 73.85 | 2003-04-02 | 18 | 14.59 | 2003-11-06 | 5
11 | 5164.22 | 508.218 | 16614.5 | 12561.8 | 4052.76 | 0.010622 | 2.929 | 31.1 | 25.8631 | 19.1876 | 0.014761 |  |  | E430 | 3.93 | 2003-04-30 | 13 | 2.81 | 2003-06-14 | 12 | 26.45 | 2003-10-23 | 15 | 6.99 | 2003-01-06 | 5 | 0.0158 | 2003-04-02 | 5 | 0.00197 | 2003-01-05 | 6 | 78.94 | 2003-04-02 | 5 | 14.58 | 2003-11-06 | 5
12 | 5004.96 | 496.504 | 16029.6 | 12561.3 | 3468.23 | 0.010433 | 2.9137 | 30.6 | 25.8628 | 18.8671 | 0.013211 |  |  | E440 | 3.81 | 2003-04-30 | 15 | 2.81 | 2003-04-08 | 13 | 26.26 | 2003-10-23 | 15 | 7 | 2003-01-06 | 5 | 0.0134 | 2003-11-16 | 16 | 0.00197 | 2003-01-05 | 7 | 67.51 | 2003-11-16 | 16 | 14.54 | 2003-11-06 | 5
13 | 6454.59 | 639.274 | 21179.7 | 17430.7 | 3749.01 | 0.0099715 | 2.9856 | 31.1 | 25.9424 | 18.518 | 0.011293 |  |  | E500 | 4.14 | 2003-04-30 | 16 | 2.71 | 2003-07-29 | 12 | 25 | 2003-03-11 | 11 | 24.04 | 2003-04-15 | 5 | 0.0115 | 2003-03-11 | 10 | 0.0103 | 2003-11-02 | 2 | 60.08 | 2003-04-01 | 5 | 52.83 | 2003-10-05 | 1
14 | 6503.4 | 639.953 | 21055.4 | 17608.6 | 3446.79 | 0.0097436 | 2.9476 | 31.7 | 26.022 | 18.4421 | 0.011692 |  |  | E510 | 4.53 | 2003-05-04 | 3 | 2.9 | 2003-03-31 | 14 | 25 | 2003-04-24 | 12 | 24.04 | 2003-04-15 | 5 | 0.0115 | 2003-03-11 | 10 | 0.0105 | 2003-04-02 | 22 | 57.51 | 2003-04-01 | 5 | 53.15 | 2003-05-04 | 4
15 | 8040.55 | 784.905 | 27069.8 | 22350.4 | 4719.45 | 0.0097834 | 3.0672 | 32.2 | 26.1296 | 18.6471 | 0.01234 |  |  | E520 | 3.84 | 2003-04-30 | 16 | 2.47 | 2003-07-30 | 12 | 18.62 | 2003-06-04 | 16 | 13.57 | 2003-11-01 | 7 | 0.0106 | 2003-01-05 | 16 | 0.00657 | 2003-11-01 | 7 | 71.77 | 2003-08-16 | 17 | 61.9 | 2003-07-20 | 15
16 | 8133.59 | 793.61 | 27623.3 | 22292 | 5331.25 | 0.0098255 | 3.0943 | 32.2 | 26.0323 | 18.7965 | 0.014188 |  |  | E522 | 4 | 2003-04-30 | 16 | 2.59 | 2003-07-29 | 12 | 20.93 | 2003-04-21 | 15 | 15.98 | 2003-04-12 | 19 | 0.0107 | 2003-01-01 | 2 | 0.00783 | 2003-04-02 | 21 | 71.32 | 2003-04-05 | 17 | 57.97 | 2003-10-05 | 1
17 | 5211.79 | 509.581 | 16551 | 12739.1 | 3811.95 | 0.010257 | 2.8928 | 31.7 | 25.943 | 19.1104 | 0.014684 |  |  | E525 | 4.4 | 2003-03-16 | 10 | 2.9 | 2003-07-29 | 12 | 35 | 2003-03-11 | 11 | 33.01 | 2003-04-01 | 8 | 0.0173 | 2003-07-20 | 15 | 0.0154 | 2003-11-02 | 2 | 51.12 | 2003-04-01 | 8 | 44.4 | 2003-10-05 | 1
18 | 5122.29 | 506.956 | 16829.6 | 12180.9 | 4648.77 | 0.010859 | 2.9897 | 31.1 | 25.6955 | 19.3936 | 0.015634 |  |  | E530 | 3.88 | 2003-03-16 | 10 | 2.52 | 2003-07-29 | 12 | 25 | 2003-03-11 | 11 | 24.04 | 2003-04-15 | 5 | 0.00677 | 2003-10-26 | 9 | 0.00663 | 2003-04-01 | 5 | 36.01 | 2003-04-20 | 21 | 33.68 | 2003-04-01 | 13
19 | 4831.72 | 492.97 | 16635.3 | 11540.7 | 5094.59 | 0.011024 | 3.1242 | 28.3 | 25.4093 | 19.5323 | 0.014493 |  |  | E540 | 3.69 | 2003-10-17 | 5 | 2.28 | 2003-07-29 | 12 | 15 | 2003-03-11 | 10 | 14.95 | 2003-12-19 | 1 | 0.00634 | 2003-03-11 | 9 | 0.0042 | 2003-10-15 | 5 | 39.96 | 2003-04-18 | 18 | 39.74 | 2003-10-05 | 1
20 | 4874.85 | 501.239 | 17131.1 | 11359.2 | 5771.92 | 0.011357 | 3.1865 | 27.2 | 25.3281 | 19.7431 | 0.016824 |  |  | E545 | 4.17 | 2003-03-16 | 10 | 2.72 | 2003-07-29 | 12 | 35 | 2003-03-11 | 11 | 33.01 | 2003-04-01 | 8 | 0.00763 | 2003-11-05 | 9 | 0.007 | 2003-04-01 | 8 | 24.14 | 2003-12-24 | 1 | 20.14 | 2003-04-01 | 12
21 | 3935.62 | 405.543 | 13524.8 | 8931.39 | 4593.42 | 0.011378 | 3.1155 | 27.2 | 25.291 | 19.7437 | 0.016824 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 3844.33 | 398.939 | 13355.8 | 8747.22 | 4608.6 | 0.011398 | 3.1475 | 26.7 | 25.2092 | 19.7887 | 0.016777
23 | 3807.46 | 397.275 | 13343.3 | 8646.75 | 4696.56 | 0.01145 | 3.1734 | 26.1 | 25.1645 | 19.8355 | 0.016835
24 | 3664.17 | 385.64 | 12972.7 | 8359.6 | 4613.06 | 0.011462 | 3.2033 | 26.1 | 25.0374 | 19.7678 | 0.017273
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 4073 | 3159 | 391 | 522 | 13673 | 9902 | 3770 | 0.016 | 3.85 | 16.96 | 25
June 25 | 5230 | 4239 | 424 | 566 | 13727 | 9946 | 3780 | 0.011 | 2.94 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3144 | 2411 | 314 | 419 | 9798 | 9798 | 0 | 0.00674 | 3.59 | 16.96 | 25
June 25 | 4043 | 3248 | 340 | 454 | 9834 | 9834 | 0 | 0.00674 | 2.74 | 29.5 | 25