## Read Me
ASHRAE Standard 140
Informative Annex B16, Section B16.6 Example Results
for
Section 5.4 - HVAC Equipment Performance Tests HE100 through HE230
This spreadsheet contains the Standard 140, Informative Annex B16, Section B16.6 example results.
Users interested in looking at the example result tables and figures should go to the "Table&Figure List"
sheet for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE: (see RESULTS5-4.DOCX for spreadsheet navigation)
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results. See instructions on page.
"Program List" : Documentation of simulation programs used to produce Informative Annex B16, Section B16.6 example results
"Table&FigureList" : Listing of Informative Annex B16, Section B16.6 Tables and Figures with locations
"Tables" : Formatted Informative Annex B16, Section B16.6 result tables
"Fig B16.6-1 LOAD" through "Fig B16.6-7 MIN T" : Informative Annex B16, Section B16.6 figures
"A" : Unformatted raw data compilation, all programs used by tables.
"Q-Chart Data": Unformatted data compilation, all programs. Used by Charts.
Individual Example Result Worksheets as follows:
ESP-HOT: Example Results for ESP-r/HOT3000 version 1.1, submitted by CANMET Energy Technology Centre, Natural resources Canada, Canada (CETC)
EnergyPlusV10: Example Results for EnergyPlus Version 1.0.2.008 submitted by GARD Analytics
DOE21E: Example Results for DOE 2.1E, version 107, submitted by CANMET Energy Technology Centre, Natural resources Canada, Canada (CETC)

## Adding Results
RESULTS5-4.XLSX
Output spreadsheet for HVAC BESTEST. See RESULTS5-4.DOCX for spreadsheet navigation.
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
New result data can be entered on sheet "YourData". The format for the results data is identical to the Standard Output Report (Sec5-4out.XLS).
Import data so that Cell B20 of Sec5-4out.XLS is in B20 of Sheet "YourData"
Check that the first value (TOTAL FURNACE LOAD GJ for HE100) lands in YourData!B20.
Data should land in "YourData" cells as tabulated below. Your data will then appear in the tables and figures
Complete the program information block on "Yourdata" which is used for legend titles for the tables and graphs.
CELL ADDRESS GUIDE FOR EXAMPLE RESULT WORKSHEETS AND NEW RESULTS
Gives locations in participant spreadsheets (.xls)
Cases | FURNACE LOAD | FURNACE INPUT | FUEL CONSUMPTION | FAN ENERGY | MEAN TEMP. | MAX TEMP. | MIN TEMP.
HE100: 100% eff. | B20 | B36 | B52 | - | - | - | -
HE110: 80% eff. | B21 | B37 | B53 | - | - | - | -
HE120: 80% eff., PLR=0.4 | B22 | B38 | B54 | - | - | - | -
HE130: No Load | B23 | B39 | B55 | - | - | - | -
HE140: Periodic PLR | B24 | B40 | B56 | - | - | - | -
HE150: Continuous Circ. Fan | B25 | B41 | B57 | B68 | - | - | -
HE160: Cycling Circ. Fan | B26 | B42 | B58 | B69 | - | - | -
HE170: Draft Fan | B27 | B43 | B59 | B70 | - | - | -
HE210: Realistic Weather | B28 | B44 | B60 | B71 | B79 | B87 | B95
HE220: Setback Thermostat | B29 | B45 | B61 | B72 | B80 | B88 | B96
HE230: Undersized Furnace | B30 | B46 | B62 | B73 | B81 | B89 | B97

## YourData
Sec5-4out.XLS |  |  | Program Name and Version (with full build detail): |  | Paste new data in row 20 and below.
Output spreadsheet for FURNACE BESTEST |  |  | EnergyPlus 23.2 |  | Cells in blue are used in titles and labels
|  |  | Program Version Release Date: | 09/28/2023 | Editing them here flows thru to other tabs
|  |  | Program Name for Tables and Charts (short): | E+ | To print pdf file, see instructions on "Title Page" tab.
Content Instructions (same as for Sec5-4out.XLS) |  |  | Results Submission Date: | 11/18/2023
Modeler Organization for Titles (long):
1) Please use specified units. |  |  | National Renewable Energy Laboratory
|  |  | Modeler Organization for Tables and Charts (short): | NREL
2) Data entry is restricted to the specified cells.
|  |  | Model / Organization Indentifier for Charts (short): | Tested Prg/Org | defaults to short program name / short organization name
TOTAL FURNACE LOAD
CODENAME: | Tested Prg | These cells are used in table and chart headers, and currently link to the program information block above. Do not overwrite.
COUNTRY: | Org
GJ
HE100: 100% eff. | 77.76
HE110: 80% eff. | 77.76
HE120: 80% eff., PLR=0.4 | 31.189
HE130: No Load | 0
HE140: Periodic PLR | 31.189
HE150: Continuous Circ. Fan | 31.226
HE160: Cycling Circ. Fan | 31.19
HE170: Draft Fan | 31.226
HE210: Realistic Weather | 43.002
HE220: Setback Thermostat | 40.71
HE230: Undersized Furnace | 35.789
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
HE100: 100% eff. | 77.76
HE110: 80% eff. | 97.2
HE120: 80% eff., PLR=0.4 | 38.38
HE130: No Load | 0
HE140: Periodic PLR | 39.03
HE150: Continuous Circ. Fan | 37.31
HE160: Cycling Circ. Fan | 38.32
HE170: Draft Fan | 37.31
HE210: Realistic Weather | 52.73
HE220: Setback Thermostat | 49.86
HE230: Undersized Furnace | 43.38
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
HE100: 100% eff. | 0.00026316
HE110: 80% eff. | 0.00032895
HE120: 80% eff., PLR=0.4 | 0.00012989
HE130: No Load | 0
HE140: Periodic PLR | 0.00013209
HE150: Continuous Circ. Fan | 0.00012627
HE160: Cycling Circ. Fan | 0.00012968
HE170: Draft Fan | 0.00012627
HE210: Realistic Weather | 0.00017845
HE220: Setback Thermostat | 0.00016874
HE230: Undersized Furnace | 0.00014681
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
HE150: Continuous Circ. Fan | 433.333
HE160: Cycling Circ. Fan | 172.222
HE170: Draft Fan | 475
HE210: Realistic Weather | 294.444
HE220: Setback Thermostat | 277.778
HE230: Undersized Furnace | 483.333
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
HE210: Realistic Weather | 20.0003
HE220: Setback Thermostat | 18.5369
HE230: Undersized Furnace | 15.3792
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
HE210: Realistic Weather | 20.0014
HE220: Setback Thermostat | 20.0014
HE230: Undersized Furnace | 20.0014
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
HE210: Realistic Weather | 20
HE220: Setback Thermostat | 15
HE230: Undersized Furnace | 1.8576

## Title Page
ASHRAE Standard 140-2020 | To print example results:
Informative Annex B16, Section B16.6 | 1. Select results type in cell B21:
"Example" for Standard 140 Annex B16.6 Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 5.4 - HVAC Equipment Performance Tests HE100 through HE230 | "Title Page" thru "Table&Figure List"
"Tables"
"Fig B16.6-1 LOAD" thru "Fig B16.6-7 Min T"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.6
Scratch area for Table subtitle 1
Example Results for Section 5.4 - HVAC Equipment Performance Tests HE100 through HE230
Scratch area for Table subtitle 2
Scratch area for chart subtitles
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.6 Example Results for Section 5.4 - HVAC Equipment Performance Tests HE100 through HE230

## Program List
ASHRAE Standard 140-2020
Participating Organizations and Computer Programs for
Quasi-Analytical Solutions and Example Simulation Results
Section 5.4 - HVAC Equipment Performance Tests HE100 through HE230
The quasi-analytical solutions and programs used to generate the example simulation results are described below.
The first column ("Model"), indicates the proper program name and version number, or indicates a quasi-analytical solution.
The second column ("Authoring Organization") indicates the national research facility, university, or industry
organization with expertise in building science that wrote the simulation software or did the quasi-analytical solutions.
The third column ("Implemented By") indicates the national research facility, university, or industry
organization with expertise in building science that performed the simulations or did the quasi-analytical solutions.
The entries in the fourth column are the abbreviations for the simulations and quasi-analytical solutions
generally used in the tables and charts which follow.
See Standard 140, Annex B17 for further details.
Participating Organizations and Computer Programs
Model | Authoring Organization | Implemented By | Abbreviation
ESP-r/HOT3000 Tier 1 tests - version 1.1 Tier 2 tests - version 1.7 | CETC/ESRU,a,b Canada/United Kingdom | CETC,a Canada | ESP-r/HOT3000/CETC
EnergyPlus 1.0.2.008 | LBNL/UIUC/CERL/OSU/GARD Analytics/FSEC/DOE-OBT,c,d,e,f,g,h | GARD Analytics, USA | EnergyPlus/GARD
DOE-2.1E version c133 | LANL/LBNL/JJH,i,c,j USA | CETC,a Canada | DOE-2.1E/CETC
Analytical/Quasi-Analytical | CETCa | CETCa | Analytical/Quasi-Analytical
aCETC CANMET Energy Technology Centre, Natural Resources Canada, Canada
bESRU: Energy Systems Research Unit, University of Strathclyde, Scotland, United Kingdom
cLBNL: Lawrence Berkeley National Laboratory, United States
dUIUC: University of Illinois Urbana/Champaign, United States
eCERL: U.S. Army Corps of Engineers, Construction Engineering Research Laboratories, United States
fOSU: Oklahoma State University, United States
gFSEC: University of Central Florida, Florida Solar Energy Center, United States
hDOE-OBT: U.S. Department of Energy, Office of Building Technology, State and Community Programs,
Energy Efficiency and Renewable Energy, United States
iLANL: Los Alamos National Laboratory, United States
jJJH: James J. Hirsch & Associates, United States

## Table&Figure List
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.6
Example Results for Section 5.4 - HVAC Equipment Performance Tests HE100 through HE230
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B16.6-1 | Total Furnace Load (GJ) | Tables | A7 – L24
| B16.6-2 | Total Furnace Input (GJ) | Tables | A26 – L43
| B16.6-3 | Fuel Consumption (m3/s) | Tables | A45 – L62
| B16.6-4 | Fan Energy, both fans (kWh) | Tables | A64 – K76
| B16.6-5 | Mean Zone Temperature (°C) | Tables | A78 – J85
| B16.6-6 | Maximum Zone Temperature (°C) | Tables | A87 – J94
| B16.6-7 | Minimum Zone Temperature (°C) | Tables | A96 – J103
List of Figures
| Figure | Description | Sheet Tab
| B16.6-1 | Total Furnace Load (GJ) | B16.1-1 LOAD
| B16.6-2 | Total Furnace Input (GJ) | B16.1-2 INPUT
| B16.6-3 | Fuel Consumption (m3/s) | B16.1-3 FUEL
| B16.6-4 | Fan Energy, both fans (kWh) | B16.1-4 FANS
| B16.6-5 | Mean Zone Temperature (°C) | B16.1-5 MEAN T
| B16.6-6 | Maximum Zone Temperature (°C) | B16.1-6 MAX T
| B16.6-7 | Minimum Zone Temperature (°C) | B16.1-7 MIN T

## Tables
ASHRAE Standard 140-2020, Informative Annex B16, Section B16.6
Example Results for Section 5.4 - HVAC Equipment Performance Tests HE100 through HE230
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B16.6-1. Total Furnace Load (GJ)
Statistics, All Results
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max |  | /Analytical* | Quasi-Analytical | Org
HE100: 100% eff. | 77.94 | 77.75 | 77.755 | 77.75 | 77.94 |  | 0.2444% | 77.74
HE110: 80% eff. | 77.94 | 77.75 | 77.755 | 77.75 | 77.94 |  | 0.2444% | 77.74
HE120: 80% eff., PLR=0.4 | 31.25 | 31.1 | 31.129 | 31.1 | 31.25 |  | 0.4823% | 31.1
HE130: No Load | 0 | 0 | 0.155 | 0 | 0.155 |  | ---- | 0
HE140: Periodic PLR | 31.26 | 31.1 | 31.123 | 31.1 | 31.26 |  | 0.5145% | 31.1
HE150: Continuous Circ. Fan | 29.88 | 29.59 | 29.565 | 29.565 | 29.88 |  | 1.062% | 29.65
HE160: Cycling Circ. Fan | 31.26 | 30.46 | 30.49 | 30.46 | 31.26 |  | 2.572% | 31.1
HE170: Draft Fan | 29.88 | 29.59 | 29.565 | 29.565 | 29.88 |  | 1.062% | 29.65
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max | Mean | /Mean** | Quasi-Analytical | Org
HE210: Realistic Weather | 41.36 | 42.04 | 42.057 | 41.36 | 42.057 | 41.819 | 1.667% | -
HE220: Setback Thermostat | 39.41 | 39.87 | 39.757 | 39.41 | 39.87 | 39.679 | 1.159% | -
HE230: Undersized Furnace | 34.32 | 34.59 | 34.372 | 34.32 | 34.59 | 34.4273 | 0.7843% | -
* Abs[ (Max-Min) / (Analytic Solution) ] |  | **Abs[ (Max-Min) / (Mean of Example Results) ]
Table B16.6-2. Total Furnace Input (GJ)
Statistics, All Results
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max |  | /Analytical* | Quasi-Analytical | Org
HE100: 100% eff. | 77.74 | 77.7133 | 78.417 | 77.7133 | 78.417 |  | 0.9055% | 77.7133
HE110: 80% eff. | 96.9201 | 97.2156 | 98.02 | 96.9201 | 98.02 |  | 1.131% | 97.2156
HE120: 80% eff., PLR=0.4 | 38.4134 | 38.2657 | 38.556 | 38.2657 | 38.556 |  | 0.7587% | 38.2657
HE130: No Load | 0 | 0 | 0.142 | 0 | 0.142 |  | ---- | 0
HE140: Periodic PLR | 39.0044 | 39.0044 | 38.764 | 38.764 | 39.0044 |  | 0.6164% | 39.0044
HE150: Continuous Circ. Fan | 37.2315 | 36.936 | 36.82 | 36.82 | 37.2315 |  | 1.111% | 37.0246
HE160: Cycling Circ. Fan | 38.118 | 38.118 | 37.962 | 37.962 | 38.118 |  | 0.4094% | 38.0884
HE170: Draft Fan | 37.2315 | 36.936 | 36.82 | 36.82 | 37.2315 |  | 1.111% | 37.0246
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max | Mean | /Mean** | Quasi-Analytical | Org
HE210: Realistic Weather | 50.5284 | 52.0059 | 52.371 | 50.5284 | 52.371 | 51.6351 | 3.568% | -
HE220: Setback Thermostat | 47.8691 | 49.3465 | 49.466 | 47.8691 | 49.466 | 48.8939 | 3.266% | -
HE230: Undersized Furnace | 41.3683 | 42.5503 | 43.219 | 41.3683 | 43.219 | 42.3792 | 4.367% | -
* Abs[ (Max-Min) / (Analytic Solution) ] |  | **Abs[ (Max-Min) / (Mean of Example Results) ]
Table B16.6-3. Fuel Consumption (m3/s)
Statistics, All Results
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max |  | /Analytical* | Quasi-Analytical | Org
HE100: 100% eff. | 0.000263 | 0.000263 | 0.0002654 | 0.000263 | 0.0002654 |  | 0.9125% | 0.000263
HE110: 80% eff. | 0.000328 | 0.000329 | 0.0003317 | 0.000328 | 0.0003317 |  | 1.125% | 0.000329
HE120: 80% eff., PLR=0.4 | 0.00013 | 0.0001295 | 0.0001305 | 0.0001295 | 0.0001305 |  | 0.7722% | 0.0001295
HE130: No Load | 0 | 0 | 0 | 0 | 0 |  | ---- | 0
HE140: Periodic PLR | 0.000132 | 0.000132 | 0.0001312 | 0.0001312 | 0.000132 |  | 0.6061% | 0.000132
HE150: Continuous Circ. Fan | 0.000126 | 0.000125 | 0.0001246 | 0.0001246 | 0.000126 |  | 1.117% | 0.0001253
HE160: Cycling Circ. Fan | 0.000129 | 0.000129 | 0.0001285 | 0.0001285 | 0.000129 |  | 0.3879% | 0.0001289
HE170: Draft Fan | 0.000126 | 0.000125 | 0.0001246 | 0.0001246 | 0.000126 |  | 1.117% | 0.0001253
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max | Mean | /Mean** | Quasi-Analytical | Org
HE210: Realistic Weather | 0.000171 | 0.000176 | 0.0001772 | 0.000171 | 0.0001772 | 0.00017473 | 3.548% | -
HE220: Setback Thermostat | 0.000162 | 0.000167 | 0.0001674 | 0.000162 | 0.0001674 | 0.00016547 | 3.263% | -
HE230: Undersized Furnace | 0.00014 | 0.000144 | 0.0001462 | 0.00014 | 0.0001462 | 0.0001434 | 4.324% | -
* Abs[ (Max-Min) / (Analytic Solution) ] |  | **Abs[ (Max-Min) / (Mean of Example Results) ]
Table B16.6-4. Fan Energy, both fans (kWh)
Statistics, All Results
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max |  | /Analytical* | Quasi-Analytical | Org
HE150: Continuous Circ. Fan | 432 | 433.3 | 432.08 | 432 | 433.3 |  | 0.3009% | 432
HE160: Cycling Circ. Fan | 170.2 | 172.2 | 172.385 | 170.2 | 172.385 |  | 1.265% | 172.76
HE170: Draft Fan | 473.4 | 473.1 | 473.13 | 473.1 | 473.4 |  | 0.0634% | 473.18
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Analytical/ | Tested Prg
| CETC | GARD | CETC | Min | Max | Mean | /Mean** | Quasi-Analytical | Org
HE210: Realistic Weather | 281.6 | 291.4 | 298.918 | 281.6 | 298.918 | 290.6393 | 5.959% | -
HE220: Setback Thermostat | 268.3 | 276.1 | 281.157 | 268.3 | 281.157 | 275.1857 | 4.672% | -
HE230: Undersized Furnace | 458.3 | 431.4 | 478.408 | 431.4 | 478.408 | 456.036 | 10.31% | -
* Abs[ (Max-Min) / (Analytic Solution) ] |  | **Abs[ (Max-Min) / (Mean of Example Results) ]
Table B16.6-5. Mean Zone Temperature (°C)
Statistics, All Results
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Tested Prg
| CETC | GARD | CETC | Min | Max | Mean | /Mean** | Org
HE210: Realistic Weather | 20.01 | 20 | 19.98 | 19.98 | 20.01 | 19.9967 | 0.15%
HE220: Setback Thermostat | 18.75 | 18.53 | 18.53 | 18.53 | 18.75 | 18.6033 | 1.183%
HE230: Undersized Furnace | 15.48 | 15.17 | 15.64 | 15.17 | 15.64 | 15.43 | 3.046%
**Abs[ (Max-Min) / (Mean of Example Results) ]
Table B16.6-6. Maximum Zone Temperature (°C)
Statistics, All Results
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Tested Prg
| CETC | GARD | CETC | Min | Max | Mean | /Mean* | Org
HE210: Realistic Weather | 21.45 | 20 | 20.06 | 20 | 21.45 | 20.5033 | 7.072%
HE220: Setback Thermostat | 22.7 | 20 | 20.11 | 20 | 22.7 | 20.9367 | 12.9%
HE230: Undersized Furnace | 20.14 | 20 | 20.06 | 20 | 20.14 | 20.0667 | 0.6977%
**Abs[ (Max-Min) / (Mean of Example Results) ]
Table B16.6-7. Minimum Zone Temperature (°C)
Statistics, All Results
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E |  |  |  | (Max-Min) | Tested Prg
| CETC | GARD | CETC | Min | Max | Mean | /Mean* | Org
HE210: Realistic Weather | 20 | 20 | 19.89 | 19.89 | 20 | 19.9633 | 0.551%
HE220: Setback Thermostat | 15 | 15 | 14.94 | 14.94 | 15 | 14.98 | 0.4005%
HE230: Undersized Furnace | 1.45 | 4.48 | 3.22 | 1.45 | 4.48 | 3.05 | 99.34%
**Abs[ (Max-Min) / (Mean of Example Results) ]

## A
RESULTS5-4.XLSX
Output spreadsheet for HVAC BESTEST
Aggregator Sheet
Cases | FURNACE LOAD | FURNACE INPUT | FUEL CONSUMPTION | FAN ENERGY | MEAN TEMP. | MAX TEMP. | MIN TEMP.
HE100: 100% eff. | B20 | B36 | B52 | - | - | - | -
HE110: 80% eff. | B21 | B37 | B53 | - | - | - | -
HE120: 80% eff., PLR=0.4 | B22 | B38 | B54 | - | - | - | -
HE130: No Load | B23 | B39 | B55 | - | - | - | -
HE140: Periodic PLR | B24 | B40 | B56 | - | - | - | -
HE150: Continuous Circ. Fan | B25 | B41 | B57 | B68 | - | - | -
HE160: Cycling Circ. Fan | B26 | B42 | B58 | B69 | - | - | -
HE170: Draft Fan | B27 | B43 | B59 | B70 | - | - | -
HE210: Realistic Weather | B28 | B44 | B60 | B71 | B79 | B87 | B95
HE220: Setback Thermostat | B29 | B45 | B61 | B72 | B80 | B88 | B96
HE230: Undersized Furnace | B30 | B46 | B62 | B73 | B81 | B89 | B97
| TOTAL FURNACE LOAD |  |  |  | TOTAL FURNACE INPUT |  |  |  | FUEL CONSUMPTION
| GJ |  |  |  | GJ |  |  |  | m3/s
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E | Tested Prg | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E | Tested Prg | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E | Tested Prg
| CETC | GARD | CETC | Org | CETC | GARD | CETC | Org | CETC | GARD | CETC | Org
HE100: 100% eff. | 77.94 | 77.75 | 77.755 |  | 77.74 | 77.7133 | 78.417 |  | 0.000263 | 0.000263 | 0.0002654
HE110: 80% eff. | 77.94 | 77.75 | 77.755 |  | 96.9201 | 97.2156 | 98.02 |  | 0.000328 | 0.000329 | 0.0003317
HE120: 80% eff., PLR=0.4 | 31.25 | 31.1 | 31.129 |  | 38.4134 | 38.2657 | 38.556 |  | 0.00013 | 0.0001295 | 0.0001305
HE130: No Load | 0 | 0 | 0.155 |  | 0 | 0 | 0.142 |  | 0 | 0 | 0
HE140: Periodic PLR | 31.26 | 31.1 | 31.123 |  | 39.0044 | 39.0044 | 38.764 |  | 0.000132 | 0.000132 | 0.0001312
HE150: Continuous Circ. Fan | 29.88 | 29.59 | 29.565 |  | 37.2315 | 36.936 | 36.82 |  | 0.000126 | 0.000125 | 0.0001246
HE160: Cycling Circ. Fan | 31.26 | 30.46 | 30.49 |  | 38.118 | 38.118 | 37.962 |  | 0.000129 | 0.000129 | 0.0001285
HE170: Draft Fan | 29.88 | 29.59 | 29.565 |  | 37.2315 | 36.936 | 36.82 |  | 0.000126 | 0.000125 | 0.0001246
HE210: Realistic Weather | 41.36 | 42.04 | 42.057 |  | 50.5284 | 52.0059 | 52.371 |  | 0.000171 | 0.000176 | 0.0001772
HE220: Setback Thermostat | 39.41 | 39.87 | 39.757 |  | 47.8691 | 49.3465 | 49.466 |  | 0.000162 | 0.000167 | 0.0001674
HE230: Undersized Furnace | 34.32 | 34.59 | 34.372 |  | 41.3683 | 42.5503 | 43.219 |  | 0.00014 | 0.000144 | 0.0001462
FAN ENERGY (BOTH FANS)
kWh
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E | Tested Prg
| CETC | GARD | CETC | Org
HE150: Continuous Circ. Fan | 432 | 433.3 | 432.08
HE160: Cycling Circ. Fan | 170.2 | 172.2 | 172.385
HE170: Draft Fan | 473.4 | 473.1 | 473.13
HE210: Realistic Weather | 281.6 | 291.4 | 298.918
HE220: Setback Thermostat | 268.3 | 276.1 | 281.157
HE230: Undersized Furnace | 458.3 | 431.4 | 478.408
| MEAN ZONE TEMPERATURE |  |  |  | MAXIMUM ZONE TEMPERATURE |  |  |  | MINIMUM ZONE TEMPERATURE
| °C |  |  |  | °C |  |  |  | °C
Cases | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E | Tested Prg | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E | Tested Prg | ESP-r/HOT3000 | EnergyPlus | DOE-2.1E | Tested Prg
| CETC | GARD | CETC | Org | CETC | GARD | CETC | Org | CETC | GARD | CETC | Org
HE210: Realistic Weather | 20.01 | 20 | 19.98 |  | 21.45 | 20 | 20.06 |  | 20 | 20 | 19.89
HE220: Setback Thermostat | 18.75 | 18.53 | 18.53 |  | 22.7 | 20 | 20.11 |  | 15 | 15 | 14.94
HE230: Undersized Furnace | 15.48 | 15.17 | 15.64 |  | 20.14 | 20 | 20.06 |  | 1.45 | 4.48 | 3.22

## Q-Chart Data
SEE SHEET 'A' FOR INSTRUCTIONS
NB: (Max-Min)/Analytical is replaced with (Max-Min)/Average for cases 2A,2B and 2C
Total Furnace Load (GJ) |  | GJ
|  |  |  | Statistics, All Results |  |  | Analytical/Quasi-Analytical
Cases | ESP-r/HOT3000/CETC | EnergyPlus/GARD | DOE-2.1E/CETC |  |  |  |  | Tested Prg/Org
|  |  |  | Min | Max | Mean
HE100: 100% eff. | 77.94 | 77.75 | 77.755 | 77.75 | 77.94 | 77.815 | 77.74
HE110: 80% eff. | 77.94 | 77.75 | 77.755 | 77.75 | 77.94 | 77.815 | 77.74
HE120: 80% eff., PLR=0.4 | 31.25 | 31.1 | 31.129 | 31.1 | 31.25 | 31.1597 | 31.1
HE130: No Load | 0 | 0 | 0.155 | 0 | 0.155 | 0.051667 | 0
HE140: Periodic PLR | 31.26 | 31.1 | 31.123 | 31.1 | 31.26 | 31.161 | 31.1
HE150: Continuous Circ. Fan | 29.88 | 29.59 | 29.565 | 29.565 | 29.88 | 29.6783 | 29.65
HE160: Cycling Circ. Fan | 31.26 | 30.46 | 30.49 | 30.46 | 31.26 | 30.7367 | 31.1
HE170: Draft Fan | 29.88 | 29.59 | 29.565 | 29.565 | 29.88 | 29.6783 | 29.65
HE210: Realistic Weather | 41.36 | 42.04 | 42.057 | 41.36 | 42.057 | 41.819 | -
HE220: Setback Thermostat | 39.41 | 39.87 | 39.757 | 39.41 | 39.87 | 39.679 | -
HE230: Undersized Furnace | 34.32 | 34.59 | 34.372 | 34.32 | 34.59 | 34.4273 | -
Total Furnace Input (GJ) |  | GJ
|  |  |  | Statistics, All Results |  |  | Analytical/Quasi-Analytical
Cases | ESP-r/HOT3000/CETC | EnergyPlus/GARD | DOE-2.1E/CETC |  |  |  |  | Tested Prg/Org
|  |  |  | Min | Max | Mean
HE100: 100% eff. | 77.74 | 77.7133 | 78.417 | 77.7133 | 78.417 | 77.9568 | 77.7133
HE110: 80% eff. | 96.9201 | 97.2156 | 98.02 | 96.9201 | 98.02 | 97.3852 | 97.2156
HE120: 80% eff., PLR=0.4 | 38.4134 | 38.2657 | 38.556 | 38.2657 | 38.556 | 38.4117 | 38.2657
HE130: No Load | 0 | 0 | 0.142 | 0 | 0.142 | 0.047333 | 0
HE140: Periodic PLR | 39.0044 | 39.0044 | 38.764 | 38.764 | 39.0044 | 38.9243 | 39.0044
HE150: Continuous Circ. Fan | 37.2315 | 36.936 | 36.82 | 36.82 | 37.2315 | 36.9958 | 37.0246
HE160: Cycling Circ. Fan | 38.118 | 38.118 | 37.962 | 37.962 | 38.118 | 38.066 | 38.0884
HE170: Draft Fan | 37.2315 | 36.936 | 36.82 | 36.82 | 37.2315 | 36.9958 | 37.0246
HE210: Realistic Weather | 50.5284 | 52.0059 | 52.371 | 50.5284 | 52.371 | 51.6351 | -
HE220: Setback Thermostat | 47.8691 | 49.3465 | 49.466 | 47.8691 | 49.466 | 48.8939 | -
HE230: Undersized Furnace | 41.3683 | 42.5503 | 43.219 | 41.3683 | 43.219 | 42.3792 | -
Fuel Consumption (m**3/s) |  | m3/s
|  |  |  | Statistics, All Results |  |  | Analytical/Quasi-Analytical
Cases | ESP-r/HOT3000/CETC | EnergyPlus/GARD | DOE-2.1E/CETC |  |  |  |  | Tested Prg/Org
|  |  |  | Min | Max | Mean
HE100: 100% eff. | 0.000263 | 0.000263 | 0.0002654 | 0.000263 | 0.0002654 | 0.0002638 | 0.000263
HE110: 80% eff. | 0.000328 | 0.000329 | 0.0003317 | 0.000328 | 0.0003317 | 0.00032957 | 0.000329
HE120: 80% eff., PLR=0.4 | 0.00013 | 0.0001295 | 0.0001305 | 0.0001295 | 0.0001305 | 0.00013 | 0.0001295
HE130: No Load | 0 | 0 | 0 | 0 | 0 | 0 | 0
HE140: Periodic PLR | 0.000132 | 0.000132 | 0.0001312 | 0.0001312 | 0.000132 | 0.00013173 | 0.000132
HE150: Continuous Circ. Fan | 0.000126 | 0.000125 | 0.0001246 | 0.0001246 | 0.000126 | 0.0001252 | 0.0001253
HE160: Cycling Circ. Fan | 0.000129 | 0.000129 | 0.0001285 | 0.0001285 | 0.000129 | 0.00012883 | 0.0001289
HE170: Draft Fan | 0.000126 | 0.000125 | 0.0001246 | 0.0001246 | 0.000126 | 0.0001252 | 0.0001253
HE210: Realistic Weather | 0.000171 | 0.000176 | 0.0001772 | 0.000171 | 0.0001772 | 0.00017473 | -
HE220: Setback Thermostat | 0.000162 | 0.000167 | 0.0001674 | 0.000162 | 0.0001674 | 0.00016547 | -
HE230: Undersized Furnace | 0.00014 | 0.000144 | 0.0001462 | 0.00014 | 0.0001462 | 0.0001434 | -
Cumulative Fan Energy (kWh) |  | Kwh
|  |  |  | Statistics, All Results |  |  | Analytical/Quasi-Analytical
Cases | ESP-r/HOT3000/CETC | EnergyPlus/GARD | DOE-2.1E/CETC |  |  |  |  | Tested Prg/Org
|  |  |  | Min | Max | Mean
HE150 Continuous Circ. Fan | 432 | 433.3 | 432.08 | 432 | 433.3 | 432.46 | 432
HE160 Cycling Circ. Fan | 170.2 | 172.2 | 172.385 | 170.2 | 172.385 | 171.595 | 172.76
HE170 Draft Fan | 473.4 | 473.1 | 473.13 | 473.1 | 473.4 | 473.21 | 473.18
HE210 Realistic Weather | 281.6 | 291.4 | 298.918 | 281.6 | 298.918 | 290.6393 | -
HE220 Setback Thermostat | 268.3 | 276.1 | 281.157 | 268.3 | 281.157 | 275.1857 | -
HE230 Undersized Furnace | 458.3 | 431.4 | 478.408 | 431.4 | 478.408 | 456.036 | -
Mean Zone Temperature (deg. C) |  | °C
Statistics, All Results
Cases | ESP-r/HOT3000/CETC | EnergyPlus/GARD | DOE-2.1E/CETC |  |  |  | Tested Prg/Org
|  |  |  | Min | Max | Mean
HE210 Realistic Weather | 20.01 | 20 | 19.98 | 19.98 | 20.01 | 19.9967 | #N/A
HE220 Setback Thermostat | 18.75 | 18.53 | 18.53 | 18.53 | 18.75 | 18.6033 | #N/A
HE230 Undersized Furnace | 15.48 | 15.17 | 15.64 | 15.17 | 15.64 | 15.43 | #N/A
Maximum Zone Temperature (deg. C) |  | °C
Statistics, All Results
Cases | ESP-r/HOT3000/CETC | EnergyPlus/GARD | DOE-2.1E/CETC |  |  |  | Tested Prg/Org
|  |  |  | Min | Max | Mean
HE210 Realistic Weather | 21.45 | 20 | 20.06 | 20 | 21.45 | 20.5033 | #N/A
HE220 Setback Thermostat | 22.7 | 20 | 20.11 | 20 | 22.7 | 20.9367 | #N/A
HE230 Undersized Furnace | 20.14 | 20 | 20.06 | 20 | 20.14 | 20.0667 | #N/A
Minimum Zone Temperature (deg. C) |  | °C
Statistics, All Results
Cases | ESP-r/HOT3000/CETC | EnergyPlus/GARD | DOE-2.1E/CETC |  |  |  | Tested Prg/Org
|  |  |  | Min | Max | Mean
HE210 Realistic Weather | 20 | 20 | 19.89 | 19.89 | 20 | 19.9633 | #N/A
HE220 Setback Thermostat | 15 | 15 | 14.94 | 14.94 | 15 | 14.98 | #N/A
HE230 Undersized Furnace | 1.45 | 4.48 | 3.22 | 1.45 | 4.48 | 3.05 | #N/A

## ESP-HOT
Output spreadsheet for Furnace BESTEST
ESP-r /HOT3000 by CANMET/NRCAN
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME: | ESP-r/HOT3000
COUNTRY: | CETC
GJ
CASE HE100 | 77.94
CASE HE110 | 77.94
CASE HE120 | 31.25
CASE HE130 | 0
CASE HE140 | 31.26
CASE HE150 | 29.88
CASE HE160 | 31.26
CASE HE170 | 29.88
CASE HE210 | 41.36
CASE HE220 | 39.41
CASE HE230 | 34.32
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.74
CASE HE110 | 96.9201
CASE HE120 | 38.4134
CASE HE130 | 0
CASE HE140 | 39.0044
CASE HE150 | 37.2315
CASE HE160 | 38.118
CASE HE170 | 37.2315
CASE HE210 | 50.5284
CASE HE220 | 47.8691
CASE HE230 | 41.3683
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000263
CASE HE110 | 0.000328
CASE HE120 | 0.00013
CASE HE130 | 0
CASE HE140 | 0.000132
CASE HE150 | 0.000126
CASE HE160 | 0.000129
CASE HE170 | 0.000126
CASE HE210 | 0.000171
CASE HE220 | 0.000162
CASE HE230 | 0.00014
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 432
CASE HE160 | 170.2
CASE HE170 | 473.4
CASE HE210 | 281.6
CASE HE220 | 268.3
CASE HE230 | 458.3
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.01
CASE HE220 | 18.75
CASE HE230 | 15.48
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 21.45
CASE HE220 | 22.7
CASE HE230 | 20.14
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 15
CASE HE230 | 1.45

## EnergyPlusV10
Output spreadsheet for Furnace BESTEST
EnergyPlus by GARD
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME: | EnergyPlus
COUNTRY: | GARD
GJ
CASE HE100 | 77.75
CASE HE110 | 77.75
CASE HE120 | 31.1
CASE HE130 | 0
CASE HE140 | 31.1
CASE HE150 | 29.59
CASE HE160 | 30.46
CASE HE170 | 29.59
CASE HE210 | 42.04
CASE HE220 | 39.87
CASE HE230 | 34.59
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.7133
CASE HE110 | 97.2156
CASE HE120 | 38.2657
CASE HE130 | 0
CASE HE140 | 39.0044
CASE HE150 | 36.936
CASE HE160 | 38.118
CASE HE170 | 36.936
CASE HE210 | 52.0059
CASE HE220 | 49.3465
CASE HE230 | 42.5503
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000263
CASE HE110 | 0.000329
CASE HE120 | 0.0001295
CASE HE130 | 0
CASE HE140 | 0.000132
CASE HE150 | 0.000125
CASE HE160 | 0.000129
CASE HE170 | 0.000125
CASE HE210 | 0.000176
CASE HE220 | 0.000167
CASE HE230 | 0.000144
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 433.3
CASE HE160 | 172.2
CASE HE170 | 473.1
CASE HE210 | 291.4
CASE HE220 | 276.1
CASE HE230 | 431.4
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 18.53
CASE HE230 | 15.17
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 20
CASE HE230 | 20
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 15
CASE HE230 | 4.48

## DOE21E
Output spreadsheet for Furnace BESTEST
DOE-2.1E by CANMET
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME: | DOE-2.1E
COUNTRY: | CETC
GJ
CASE HE100 | 77.755
CASE HE110 | 77.755
CASE HE120 | 31.129
CASE HE130 | 0.155
CASE HE140 | 31.123
CASE HE150 | 29.565
CASE HE160 | 30.49
CASE HE170 | 29.565
CASE HE210 | 42.057
CASE HE220 | 39.757
CASE HE230 | 34.372
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 78.417
CASE HE110 | 98.02
CASE HE120 | 38.556
CASE HE130 | 0.142
CASE HE140 | 38.764
CASE HE150 | 36.82
CASE HE160 | 37.962
CASE HE170 | 36.82
CASE HE210 | 52.371
CASE HE220 | 49.466
CASE HE230 | 43.219
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.0002654
CASE HE110 | 0.0003317
CASE HE120 | 0.0001305
CASE HE130 | 0
CASE HE140 | 0.0001312
CASE HE150 | 0.0001246
CASE HE160 | 0.0001285
CASE HE170 | 0.0001246
CASE HE210 | 0.0001772
CASE HE220 | 0.0001674
CASE HE230 | 0.0001462
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 432.08
CASE HE160 | 172.385
CASE HE170 | 473.13
CASE HE210 | 298.918
CASE HE220 | 281.157
CASE HE230 | 478.408
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.98
CASE HE220 | 18.53
CASE HE230 | 15.64
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.06
CASE HE220 | 20.11
CASE HE230 | 20.06
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.89
CASE HE220 | 14.94
CASE HE230 | 3.22