## Read Me
RESULTS5-2A.XLSX
Example results workbook for Section 5.2 - Building Thermal Envelope Tests Cases 195-995, & 600FF-980FF
This spreadsheet contains the Standard 140, Informative Annex B8, Section B8.1 example results.
See the "Table List" and "Figure List" sheets for a listing of tables and figures and their locations.
This workbook can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab) for instructions and to enter identifying information for your program.
Import your results to sheet "Your Data" (3rd tab); your results will then automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE: (see RESULTS5-2A.DOC for spreadsheet navigation)
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results.
"YourData" : For tested program results if doing comparison; see sheet "Adding Results" for instructions.
"Title Page" : Sets headers for tables and charts and provides cover sheet for example results or new comparison results. See instructions there.
"Program List" : Documentation of simulation programs used to produce example results for Standard 140 Informative Annex B8, Section B8.1
"Table List": List of compiled results Tables in workbook with sheet tab locations (for Standard 140, Informative Annex B8, Section B8.1).
"Figure List": List of compiled results Figures in workbook with sheet tab labels (for Standard 140, Informative Annex B8, Section B8.1).
Compiled Example-Results Tables and Figures as follows:
"Tables 1" through "Tables 7" : tables for annual loads, free-float zone temperatures, solar radiation, sky temperatures
"Tables M1" through "Tables M3" : tables for monthly loads
"Fig B8-1" through "Fig B8-59": figures for annual loads, free-float zone temperatures, solar radiation, sky temperatures
"Fig B8-M1" through "Fig B8-M12": figures for monthly loads
"Fig B8-H1" through "Fig B8-H38" : figures for hourly loads, free-float zone temperatures, solar radiation, sky temperatures
"DATA for charts" : Unformatted compiled results for use in charts.
Individual Example Result Worksheets as follows:
"BSIMAC": BSIMAC, Version 9.0.74, submitted by Alec Johannsen Consulting Engineers, South Africa
"CSE": California Simulation Engine, Version 0.861.1, submitted by Big Ladder Software, United States
"DeST": DeST 2.0, Version 20190401, submitted by Southeast University, China and Tsinghua University, China
"EnergyPlus": EnergyPlus, Version 9.0.1, submitted by GARD Analytics, Inc., United States
"ESP-r": ESP-r, Version 13.3, submitted by University of Strathclyde, United Kingdom
"TRNSYS": TRNSYS, Version 18.01.0001, submitted by Transsolar Energietechnik GmbH, Germany
"TestSpecAlt": Tsky alternative values from test spec (Section 5.2.1.1.1.2 and Annex A1, Section A1.1.1.2)
'TestSpecAlt' data applies only for Tsky as shown in Table B8-16 and Figures B8-6, B8-H10, B8-H11.
"K": Spare data entry sheet

## Adding Results
INSTRUCTIONS FOR ADDING NEW RESULTS
New result data can be imported into this workbook (sheet 'YourData', next tab) and will automatically be included in tables and charts.
Import data so that Cell B66 of Sec5-2Aout.XLS is in B66 of Sheet "YourData"
Check that the first value Annual Heating Load for Case 600 lands in YourData!C70.
Your data will then appear in the rightmost column of each table on sheets "Tables 1" to "Tables 7" and "Tables M1" to "Tables M3".
Charts are also updated with "your data" automatically.
Complete the program information block just below in the cyan highlighted cells.
This information is used for legend titles for the tables and graphs. See "Comparison" setting on sheet 'Title Page'
Program Name and Version (with full build detail):
OpenStudio 3.4.0
| Program Version Release Date: | 05/05/2022
| Program Name for Tables and Charts (short): | OS
| Results Submission Date: | 05/05/2022
Modeler Organization for Titles (long):
National Renewable Energy Laboratory
| Modeler Organization for Tables and Charts (short): | NREL
| Model / Organization Indentifier for Charts (short): | Tested Prg/Org

## YourData
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx |  | 2020-01-01
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
[Note to Users: This file is reorganized since 140-2017. Red text indicates content changes to 140-2017.]
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | EnergyPlus 22.1
March |  | Mar |  |  |  | 03/29/22
April |  | Apr |  |  |  | E+
May |  | May |  |  |  | 05/05/2022
June |  | Jun
July |  | National Renewable Energy Laboratory
August |  | Aug |  |  |  | NREL
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
| USER NOTE: Paste new data in row 61 and below. | Program Label in C61 flows to data labels in charts and figures. Avoid overwrite or re-enter "='Adding Results'!G24" there.
Version and Date of Results will also transfer from 'Adding Results' sheet.
To print pdf file, see instructions on "Title Page" tab.
Enter identifying information in C61, C62, C63
| Software: | Tested Prg
| Version: | Tested Program V1.2.3
| Date of Results: | 2020-03-10
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.2306 | 6.0361 | 3.1455 | DEC | 31 | 24 | 6.3595 | JAN | 22 | 14
| 610 | 4.2778 | 4.3389 | 3.1328 | DEC | 31 | 24 | 6.1344 | DEC | 1 | 14
| 620 | 4.3806 | 4.0528 | 3.1712 | DEC | 31 | 24 | 4.76 | JUN | 26 | 17
| 630 | 4.6722 | 2.8222 | 3.1488 | DEC | 31 | 24 | 4.1744 | JUN | 26 | 17
| 640 | 2.7083 | 5.8361 | 5.4843 | NOV | 26 | 8 | 6.3205 | JAN | 22 | 14
| 650 | 0 | 5.1639 | 0 | JAN | 1 | 1 | 6.2776 | JAN | 22 | 14
| 660 | 3.0278 | 4.2056 | 2.4908 | DEC | 31 | 24 | 4.349 | OCT | 18 | 14
| 670 | 2.9444 | 8.6944 | 2.569 | DEC | 31 | 24 | 8.1118 | JAN | 22 | 14
| 680 | 3.9583 | 5.9111 | 3.0085 | DEC | 31 | 24 | 6.3121 | JAN | 22 | 14
| 685 | 4.7806 | 9.1306 | 3.1649 | DEC | 31 | 24 | 7.1138 | JAN | 22 | 14
| 695 | 4.5306 | 9.0306 | 3.0349 | DEC | 31 | 24 | 7.0691 | JAN | 22 | 14
| 900 | 1.5889 | 2.4944 | 2.6322 | FEB | 9 | 6 | 3.0351 | OCT | 1 | 14
| 910 | 1.8722 | 1.3806 | 2.644 | FEB | 9 | 6 | 2.2388 | OCT | 18 | 15
| 920 | 3.2306 | 2.7167 | 2.7165 | FEB | 9 | 6 | 3.2341 | JUN | 26 | 18
| 930 | 3.8806 | 1.9028 | 2.7316 | FEB | 9 | 6 | 2.7556 | JUN | 26 | 18
| 940 | 1.0917 | 2.4361 | 4.2937 | NOV | 26 | 8 | 3.035 | OCT | 1 | 14
| 950 | 0 | 0.67222 | 0 | JAN | 1 | 1 | 2.2778 | SEP | 11 | 15
| 960 | 2.5806 | 0.88056 | 2.2011 | FEB | 9 | 6 | 1.4446 | JUN | 26 | 17
| 980 | 1.3694 | 2.5694 | 2.467 | FEB | 9 | 6 | 3.0315 | OCT | 1 | 14
| 985 | 2.2972 | 6.3917 | 2.6407 | FEB | 9 | 6 | 3.9207 | OCT | 18 | 15
| 995 | 2.0583 | 6.4333 | 2.4781 | FEB | 9 | 6 | 3.8909 | OCT | 18 | 15
| 195 | 3.9389 | 0.58889 | 1.7369 | DEC | 31 | 24 | 1.0057 | JUN | 26 | 17
| 200 | 5.0667 | 0.81111 | 2.3411 | NOV | 26 | 8 | 1.2946 | JUN | 26 | 17
| 210 | 6.0417 | 0.55 | 2.5635 | DEC | 31 | 24 | 1.0717 | JUN | 26 | 17
| 215 | 5.4167 | 0.88056 | 2.5009 | NOV | 26 | 8 | 1.3991 | JUN | 26 | 17
| 220 | 6.5222 | 0.60833 | 2.7132 | DEC | 31 | 24 | 1.1855 | JUN | 26 | 18
| 230 | 9.9972 | 0.99167 | 4.3373 | DEC | 31 | 24 | 1.8437 | JUN | 26 | 17
| 240 | 5.3472 | 0.975 | 2.5288 | DEC | 31 | 24 | 1.3665 | JUN | 26 | 18
| 250 | 4.9333 | 3.3556 | 2.7083 | DEC | 31 | 24 | 2.9958 | SEP | 12 | 13
| 270 | 4.2889 | 7.5306 | 2.5382 | DEC | 31 | 24 | 6.8453 | JAN | 22 | 14
| 280 | 4.4722 | 5.1861 | 2.5436 | DEC | 31 | 24 | 4.7344 | JAN | 22 | 14
| 290 | 4.3278 | 5.75 | 2.525 | DEC | 31 | 24 | 6.601 | DEC | 22 | 13
| 300 | 4.3194 | 5.15 | 2.5452 | DEC | 31 | 24 | 4.437 | JUN | 26 | 17
| 310 | 4.5778 | 3.6583 | 2.5223 | DEC | 31 | 24 | 3.9314 | JUN | 26 | 18
| 320 | 3.675 | 4.9917 | 2.514 | DEC | 31 | 24 | 6.2167 | JAN | 22 | 14
| 395 | 4.5167 | 0.0083333 | 1.8926 | DEC | 31 | 24 | 0.32655 | JUN | 26 | 19
| 400 | 6.4167 | 0.027778 | 2.7132 | DEC | 31 | 24 | 0.59188 | JUN | 26 | 18
| 410 | 8.1472 | 0.055556 | 3.5252 | DEC | 31 | 24 | 0.81277 | JUN | 26 | 18
| 420 | 6.975 | 0.14444 | 3.3408 | DEC | 31 | 24 | 1.0161 | JUN | 26 | 18
| 430 | 5.6417 | 0.87778 | 3.3378 | DEC | 31 | 24 | 1.952 | JUN | 26 | 16
| 440 | 4.4028 | 4.0917 | 3.1594 | DEC | 31 | 24 | 4.6787 | OCT | 18 | 14
| 450 | 4.8278 | 5.5944 | 3.412 | DEC | 31 | 24 | 5.925 | JAN | 22 | 14
| 460 | 4.6611 | 6.1944 | 3.2637 | DEC | 31 | 24 | 6.1112 | JAN | 22 | 14
| 470 | 4.3417 | 5.4444 | 3.2548 | DEC | 31 | 24 | 6.1658 | JAN | 22 | 14
| 800 | 5.1 | 0.375 | 2.9422 | FEB | 9 | 6 | 1.052 | JUN | 26 | 16
| 810 | 2.25 | 1.4972 | 2.6946 | FEB | 9 | 6 | 2.2564 | SEP | 11 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 25.0598 | -11.9274 | FEB | 10 | 6 | 63.8601 | OCT | 19 | 15
| 900FF | 25.2621 | 1.7235 | FEB | 10 | 6 | 44.2069 | SEP | 13 | 14
| 650FF | 19.4301 | -16.875 | DEC | 32 | 23 | 67.6849 | OCT | 19 | 15
| 950FF | 15.1283 | -12.5915 | FEB | 10 | 5 | 37.1604 | SEP | 12 | 15
| 680FF | 25.3863 | -11.2631 | FEB | 10 | 6 | 62.855 | OCT | 19 | 15
| 980FF | 25.8307 | 2.7879 | FEB | 10 | 6 | 44.5443 | SEP | 13 | 14
| 960 | 27.5392 | 5.2272 | FEB | 10 | 6 | 49.1204 | OCT | 13 | 14
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1664.34
| NORTH | 438.241
| EAST | 1062.16
| SOUTH | 1370.48
| WEST | 967.278
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 804.021
| 660/South | 435.995
| 670/South | 1032.72
| 620/West | 612.304
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 646.673
| 630/West | 445.215
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -2.017 | -37.9796 | DEC | 32 | 23 | 24.7306 | AUG | 5 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 899.49 | 527.52 | 3.33 | 1 | 3 | 6.41 | 22 | 14 | 336.14 | 56.49 | 2.28 | 29 | 6 | 2.17 | 22 | 14
| Feb | 843.12 | 392.6 | 3.42 | 9 | 5 | 5.62 | 2 | 14 | 360.3 | 14.23 | 3.04 | 9 | 5 | 1.09 | 15 | 14
| Mar | 628.78 | 488.22 | 2.41 | 17 | 5 | 5.1 | 24 | 12 | 184.32 | 69.19 | 2.03 | 17 | 5 | 1.6 | 11 | 14
| Apr | 622.56 | 242.43 | 2.65 | 11 | 4 | 4 | 12 | 14 | 322.89 | 19.79 | 2.28 | 3 | 2 | 0.99 | 7 | 15
| May | 195.09 | 340.12 | 1.83 | 1 | 5 | 3.13 | 10 | 12 | 64.93 | 115 | 1.46 | 1 | 5 | 1.54 | 11 | 14
| Jun | 55.65 | 539.65 | 0.91 | 9 | 5 | 3.5 | 13 | 12 | 51.63 | 402.44 | 0.29 | 7 | 13 | 1.96 | 14 | 14
| Jul | 35.07 | 534.41 | 0.54 | 26 | 4 | 3.63 | 17 | 14 | 26.94 | 397.61 | 0.24 | 4 | 12 | 2.08 | 17 | 13
| Aug | 36.53 | 648.2 | 0.66 | 24 | 10 | 4.74 | 27 | 13 | 38.93 | 511.61 | 0.3 | 24 | 10 | 2.56 | 29 | 15
| Sep | 140.72 | 731.39 | 1.29 | 28 | 23 | 5.77 | 30 | 13 | 68.67 | 491.4 | 0.52 | 17 | 10 | 3 | 11 | 15
| Oct | 442.73 | 677.18 | 1.93 | 15 | 4 | 6.28 | 18 | 14 | 140.78 | 296.84 | 1.48 | 7 | 7 | 3.05 | 1 | 14
| Nov | 781.31 | 441.83 | 3.47 | 26 | 6 | 6.35 | 28 | 12 | 373.43 | 71.3 | 2.71 | 26 | 8 | 2.1 | 22 | 14
| Dec | 914.74 | 485.95 | 3.61 | 31 | 23 | 6.39 | 1 | 12 | 392.21 | 64.05 | 2.5 | 31 | 23 | 2.02 | 2 | 15
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -22.96 | -1.17 | 4.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -24.14 | -1.19 | 3.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -25.31 | -1.26 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -27.19 | -1.44 | 1.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 5.65 | 2.83 | 2.83 | -26.9 | -1.44 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 10.11 | 5.5 | 12.87
| 6 | 21.25 | 10.98 | 10.98 | 103.19 | 27.06 | 27.06 | -26.67 | -1.44 | 1.79 | 0 | 0 | 0 | 39.3 | 21.38 | 50.03 | 96.82 | 52.68 | 123.25
| 7 | 64.75 | 33.82 | 33.82 | 289.86 | 55.39 | 55.39 | -27.39 | -1.19 | 4.42 | 0 | 0 | 0 | 121.03 | 65.85 | 154.08 | 198.21 | 107.84 | 252.32
| 8 | 114.58 | 59.97 | 59.78 | 493.43 | 82.4 | 81.97 | -26.6 | -0.88 | 6.6 | 657.38 | 352.22 | 877.4 | 214.59 | 116.75 | 273.17 | 293.42 | 159.65 | 373.53
| 9 | 160.25 | 84.39 | 83.07 | 682.34 | 179.12 | 104.12 | -25.36 | -0.53 | 8.39 | 1942.8 | 1051.15 | 2473.88 | 302 | 164.32 | 384.44 | 423.01 | 231.77 | 584.17
| 10 | 203.25 | 108.11 | 104.63 | 837.84 | 305.79 | 119.48 | -24.49 | 0.66 | 10.72 | 2904.49 | 1578.15 | 3605.61 | 386.89 | 210.5 | 492.51 | 699.86 | 378.17 | 1033.77
| 11 | 259.83 | 139.61 | 132.04 | 948 | 396.71 | 128.25 | -23.14 | 1.87 | 12.61 | 3551.61 | 1935.41 | 4359.64 | 499.58 | 271.82 | 635.96 | 1016.67 | 542.85 | 1479.46
| 12 | 276.58 | 149.44 | 140.24 | 1005.24 | 443.51 | 131.55 | -21.79 | 2.1 | 13.27 | 3892.41 | 2127.05 | 4756.16 | 534.75 | 290.96 | 680.74 | 1210.9 | 644.87 | 1732.94
| 13 | 274.08 | 147.92 | 142.63 | 1004.03 | 442.66 | 258.93 | -20.21 | 0.89 | 13.9 | 3929.03 | 2147.86 | 4798.81 | 529.34 | 288.01 | 673.85 | 1207.43 | 643.03 | 1728.47
| 14 | 255.17 | 136.71 | 137.73 | 946.15 | 394.89 | 491.65 | -20.69 | -0.55 | 14.39 | 3655.62 | 1993.59 | 4480.37 | 489.22 | 266.18 | 622.78 | 1009.03 | 538.84 | 1469.44
| 15 | 222 | 117.61 | 123.31 | 835.48 | 303.17 | 683.86 | -21.77 | -2.03 | 14.9 | 3078.26 | 1673.66 | 3807.6 | 420.86 | 228.99 | 535.76 | 691.63 | 373.91 | 1021.55
| 16 | 172 | 90 | 96.87 | 679.26 | 175.53 | 811.98 | -22.21 | -2 | 14.78 | 2199.98 | 1192 | 2779.21 | 322.07 | 175.23 | 409.99 | 417.69 | 228.85 | 574.91
| 17 | 101.92 | 53.26 | 54.93 | 489.97 | 81.51 | 853.44 | -22.93 | -1.83 | 14.47 | 1070.25 | 574.71 | 1413.28 | 190.6 | 103.7 | 242.63 | 291.7 | 158.71 | 371.33
| 18 | 50.25 | 26.16 | 26.16 | 285.84 | 54.81 | 778.08 | -24.62 | -2.11 | 13.6 | 58.73 | 31.18 | 82.08 | 93.63 | 50.94 | 119.19 | 196.13 | 106.71 | 249.68
| 19 | 10.53 | 5.43 | 5.43 | 99.08 | 26.26 | 527.4 | -25.92 | -2.36 | 12.31 | 0 | 0 | 0 | 19.43 | 10.57 | 24.73 | 93.98 | 51.13 | 119.63
| 20 | 0 | 0 | 0 | 4.44 | 2.35 | 70.21 | -26.5 | -2.94 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 8.41 | 4.57 | 10.7
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -27.61 | -3.22 | 9.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -28.94 | -3.74 | 7.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -29.44 | -4.78 | 7.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -29.27 | -5.26 | 5.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.11 | 0.06 | 1.62 | 1.67 | 2.02 | 2.15 | 2.07 | 0.93 | 0 | 0.79 | 1.1 | 1 | 0 | 0 | 0 | 0 | -0.08 | -0.11 | -0.1 | -0.12 | -0.7 | -0.71 | 10 | 15.3
| 2 | 2.18 | 0.52 | 1.67 | 1.74 | 2.1 | 2.2 | 2.13 | 1.04 | 0 | 0.9 | 1.2 | 1.09 | 0 | 0 | 0 | 0 | -0.02 | -0.04 | -0.03 | -0.05 | -0.62 | -0.63 | 10 | 14.8
| 3 | 2.24 | 0.88 | 1.71 | 1.78 | 2.16 | 2.25 | 2.17 | 1.14 | 0 | 1.01 | 1.3 | 1.18 | 0 | 0 | 0 | 0 | 0.06 | 0.03 | 0 | 0 | -0.52 | -0.54 | 10 | 14.2
| 4 | 2.29 | 1.11 | 1.75 | 1.82 | 2.21 | 2.29 | 2.22 | 1.24 | 0 | 1.1 | 1.39 | 1.27 | 0 | 0 | 0 | 0 | 0.18 | 0.12 | 0 | 0 | -0.42 | -0.44 | 10 | 13.7
| 5 | 2.31 | 1.23 | 1.76 | 1.84 | 2.24 | 2.31 | 2.24 | 1.32 | 0 | 1.17 | 1.46 | 1.34 | 0 | 0 | 0 | 0 | 0.27 | 0.22 | 0 | 0 | -0.32 | -0.35 | 10 | 13.2
| 6 | 2.31 | 1.3 | 1.76 | 1.84 | 2.24 | 2.31 | 2.24 | 1.39 | 0 | 1.24 | 1.53 | 1.41 | 0 | 0 | 0 | 0 | 0.16 | 0.15 | 0 | 0 | -0.33 | -0.35 | 10 | 12.8
| 7 | 2.31 | 1.34 | 1.77 | 1.85 | 2.24 | 2.31 | 2.24 | 1.46 | 0 | 1.31 | 1.59 | 1.46 | 0 | 0 | 0 | 0 | -0.14 | -0.11 | 0 | 0 | -0.44 | -0.44 | 20 | 20.1
| 8 | 1.84 | 4.27 | 1.43 | 1.33 | 1.8 | 1.84 | 1.8 | 1.28 | 2.5 | 1.14 | 1.39 | 1.27 | 0 | 0 | 0 | 0 | -0.54 | -0.46 | -0.02 | -0.02 | -0.6 | -0.57 | 20 | 20
| 9 | 0.45 | 1.24 | 0.44 | 0.11 | 0.47 | 0.41 | 0.44 | 0.74 | 1.31 | 0.64 | 0.83 | 0.75 | 0 | 0 | -0.09 | 0 | -1.02 | -0.92 | -0.16 | -0.15 | -0.8 | -0.76 | 21.8 | 20
| 10 | 0 | 0.01 | 0 | -0.59 | 0 | -1.4 | -1.33 | 0.22 | 0.7 | 0.15 | 0.31 | 0.24 | -0.36 | -0.39 | -0.97 | -0.25 | -1.7 | -1.56 | -0.41 | -0.39 | -1.11 | -1.05 | 26.8 | 20.1
| 11 | -1.41 | -0.92 | -0.24 | -3.51 | -1.3 | -3.34 | -3.27 | 0 | 0.17 | 0 | -0.31 | -0.38 | -1.45 | -1.21 | -2.23 | -1.24 | -2.56 | -2.38 | -0.76 | -0.72 | -1.49 | -1.41 | 27 | 21.5
| 12 | -3.53 | -3.24 | -1.74 | -5.65 | -3.42 | -4.79 | -4.74 | 0 | 0 | 0 | -1.01 | -1.08 | -2.41 | -1.93 | -3.28 | -2.19 | -3.3 | -3.11 | -1.09 | -1.03 | -1.86 | -1.74 | 27 | 23.6
| 13 | -4.75 | -4.63 | -2.83 | -6.79 | -4.67 | -5.67 | -5.63 | 0 | 0 | 0 | -1.71 | -1.77 | -2.83 | -2.24 | -3.73 | -2.69 | -3.6 | -3.47 | -1.32 | -1.28 | -2.09 | -2 | 27 | 25.1
| 14 | -4.98 | -4.93 | -3.18 | -6.98 | -4.94 | -5.76 | -5.73 | -0.01 | 0 | -0.05 | -2.1 | -2.16 | -2.89 | -2.29 | -3.74 | -2.78 | -3.6 | -3.49 | -1.46 | -1.41 | -2.23 | -2.14 | 27 | 25.7
| 15 | -4.21 | -4.19 | -2.77 | -6.16 | -4.29 | -4.92 | -5 | -0.12 | 0 | -0.24 | -2.14 | -2.23 | -2.62 | -2.12 | -3.33 | -2.55 | -3.29 | -3.21 | -1.47 | -1.43 | -2.22 | -2.14 | 27 | 25.8
| 16 | -2.96 | -2.96 | -1.96 | -4.71 | -3.09 | -3.63 | -3.74 | -0.08 | 0 | -0.21 | -1.96 | -2.06 | -2.19 | -1.83 | -2.68 | -2.14 | -2.84 | -2.77 | -1.39 | -1.34 | -2.12 | -2.03 | 27 | 25
| 17 | -1.27 | -1.27 | -0.82 | -2.68 | -1.42 | -1.91 | -2.05 | 0 | 0 | -0.01 | -1.45 | -1.56 | -1.74 | -1.48 | -2.04 | -1.74 | -2.38 | -2.36 | -1.28 | -1.25 | -1.99 | -1.93 | 25.5 | 23.3
| 18 | -0.02 | -0.02 | -0.01 | -0.41 | -0.05 | 0.01 | -0.15 | 0 | 0 | 0 | -0.68 | -0.79 | -1.35 | -1.18 | -1.55 | -1.38 | -1.97 | -1.99 | -1.15 | -1.14 | -1.85 | -1.8 | 21.2 | 22
| 19 | 0.06 | 0.06 | 0 | 0 | 0.01 | 1.07 | 0.87 | 0 | 0 | 0 | -0.23 | -0.34 | -0.96 | -0.88 | -1.11 | -1.02 | -1.57 | -1.62 | -1 | -1 | -1.68 | -1.65 | 20 | 21
| 20 | 0.94 | 0.94 | 0.34 | 0.12 | 0.66 | 1.66 | 1.47 | 0 | 0 | 0 | 0.06 | -0.03 | -0.55 | -0.54 | -0.66 | -0.63 | -1.13 | -1.21 | -0.83 | -0.84 | -1.49 | -1.47 | 20 | 20.2
| 21 | 1.6 | 1.6 | 1.04 | 0.84 | 1.37 | 1.99 | 1.84 | 0 | 0.02 | 0 | 0.3 | 0.2 | -0.22 | -0.26 | -0.31 | -0.29 | -0.77 | -0.84 | -0.69 | -0.7 | -1.33 | -1.31 | 20 | 20
| 22 | 2.01 | 2.01 | 1.45 | 1.38 | 1.82 | 2.23 | 2.1 | 0 | 0.24 | 0 | 0.53 | 0.4 | -0.04 | -0.1 | -0.12 | -0.08 | -0.56 | -0.61 | -0.58 | -0.59 | -1.2 | -1.19 | 20 | 20
| 23 | 2.28 | 2.28 | 1.7 | 1.7 | 2.12 | 2.4 | 2.28 | 0.1 | 0.48 | 0 | 0.72 | 0.6 | 0 | -0.01 | -0.02 | 0 | -0.43 | -0.46 | -0.48 | -0.49 | -1.09 | -1.08 | 13 | 18.3
| 24 | 2.39 | 0 | 1.82 | 1.85 | 2.27 | 2.45 | 2.36 | 0.32 | 0 | 0.13 | 0.85 | 0.73 | 0 | 0 | 0 | 0 | -0.3 | -0.33 | -0.36 | -0.39 | -0.96 | -0.96 | 0 | 0
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 4.2 | 12.8 | 19.1 | 20.7 | 5.3 | 13.9
| 2 | 2.8 | 12.4 | 18.1 | 20 | 3.9 | 13.4
| 3 | 1.5 | 11.9 | 17 | 19.2 | 2.6 | 12.9
| 4 | 0.4 | 11.4 | 15.9 | 18.3 | 1.4 | 12.4
| 5 | -0.5 | 11 | 16.4 | 18.6 | 0.5 | 12
| 6 | -1.3 | 10.6 | 18.8 | 20.3 | -0.4 | 11.6
| 7 | -1 | 10.8 | 20.9 | 23 | -0.2 | 11.8
| 8 | 3.2 | 12.2 | 23.3 | 24.5 | 4 | 13.2
| 9 | 10.4 | 14.3 | 26.2 | 25.6 | 11 | 15.2
| 10 | 19.3 | 16.4 | 30.3 | 26.8 | 19.4 | 17.3
| 11 | 28.6 | 18.7 | 35.2 | 28.1 | 28.1 | 19.6
| 12 | 37 | 20.9 | 39.9 | 29 | 36.6 | 21.8
| 13 | 43.7 | 22.5 | 43.2 | 29.7 | 43.1 | 23.3
| 14 | 47.4 | 23.2 | 45.5 | 30.1 | 46.8 | 24.1
| 15 | 48 | 23.3 | 46.6 | 30.3 | 47.6 | 24.2
| 16 | 45.3 | 22.6 | 46.5 | 30.3 | 45.3 | 23.5
| 17 | 39.1 | 20.9 | 45.8 | 30.3 | 39.6 | 21.9
| 18 | 32.6 | 19.7 | 34.9 | 29 | 33.3 | 20.7
| 19 | 26.7 | 18.8 | 31.1 | 27.6 | 28.1 | 19.8
| 20 | 22 | 18 | 28.1 | 26.3 | 23.2 | 19
| 21 | 17.5 | 17.2 | 26.1 | 25.5 | 19 | 18.3
| 22 | 13.7 | 16.5 | 24.6 | 24.8 | 15.4 | 17.5
| 23 | 10.7 | 15.8 | 23 | 23.9 | 12.3 | 16.9
| 24 | 0 | 0 | 0 | 0 | 0 | 0
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
-50
-49
-48
-47
-46
-45
-44
-43
-42
-41
-40
-39
-38
-37
-36
-35
-34
-33
-32
-31
-30
-29
-28
-27
-26
-25
-24
-23
-22
-21
-20
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 2
| 1 | 3
| 2 | 13
| 3 | 25
| 4 | 29
| 5 | 46
| 6 | 56
| 7 | 70
| 8 | 78
| 9 | 114
| 10 | 154
| 11 | 199
| 12 | 203
| 13 | 191
| 14 | 232
| 15 | 279
| 16 | 243
| 17 | 294
| 18 | 330
| 19 | 339
| 20 | 302
| 21 | 332
| 22 | 316
| 23 | 287
| 24 | 307
| 25 | 297
| 26 | 305
| 27 | 309
| 28 | 340
| 29 | 373
| 30 | 382
| 31 | 378
| 32 | 412
| 33 | 374
| 34 | 313
| 35 | 248
| 36 | 207
| 37 | 147
| 38 | 111
| 39 | 64
| 40 | 30
| 41 | 18
| 42 | 6
| 43 | 2
| 44 | 0
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
| 97 |  |  | Sum (check)
| 98 |  |  | 0

## Title Page
ASHRAE Standard 140-2020 | To print example results:
Informative Annex B8, Section B8.1 | 1. Select results type in cell B21:
"Example" for Standard 140 Annex B8 Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF | "Title Page" thru "Figure List"
"Tables 1" thru "Tables M3" (all tables tabs)
"Fig B8-1" thru "Fig B8-H38" (all figures tabs)
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "Adding Results" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Scratch area for Table subtitle 1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Scratch area for Table subtitle 2
Scratch area for chart subtitles
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1 Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF

## Program List
ASHRAE Standard 140-2020
Computer Programs, Program Authors, and Producers of Example Results for
Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
The programs used to generate the example results for Sections 5.2.1, 5.2.2, and 5.2.3 are described in Table B11-1. Under the "Computer Program" column, the first entry in each cell is the proper program name and version number. The entries in parentheses are the abbreviations for the programs used in the tables and charts of this workbook.
The second column ("Authoring Organization") indicates the national research facility, university,
or industry organization with expertise in building science that wrote the simulation software.
The third column ("Example Results Produced By") indicates the national research facility, university, or industry organization with expertise in building science that performed the simulations. Most of the organizations that performed simulations are members of the development team for the simulation model that they ran.
See Standard 140, Annex B11 for further details.
TABLE B11-1
Computer Programs, Program Authors, and Producers of Example Results
Computer Program (Abbrev.) | Authoring Organization | Example Results Produced by
BSIMAC 9, Version 9.0.74 (BSIMAC) | Alec Johannsen Consulting Engineers, South Africa | Alec Johannsen Consulting Engineers, South Africa
California Simulation Engine, Version 0.861.1 (CSE) | J.R. Barnaby/C.S. Barnaby/Big Ladder Software LLC/Wrightsoft Corp., United States | Big Ladder Software LLC, United States
DeST 2.0, Version 20190401 (DeST) | Tsinghua University, China | Southeast University, China Tsinghua University, China
EnergyPlus, Version 9.0.1 (EnergyPlus) | U.S. Department of Energy, Building Technologies Office, United States | GARD Analytics, Inc., United States
ESP-r, Version 13.3 (ESP-r) | University of Strathclyde, United Kingdom | University of Strathclyde, United Kingdom
TRNSYS, Version 18.01.0001 (TRNSYS) | Transsolar Energietechnik GmbH, Germany; Thermal Energy System Specialists, United States | Transsolar Energietechnik GmbH, Germany
TRNSYS, Versions 17.02.0005 and 18.00.0017 (N/A) | Transsolar Energietechnik GmbH, Germany; Thermal Energy System Specialists, United States | Ecole Polytechnique Montréal, Canadaa,b
a Ecole Polytechnique and GARD also worked on simulations for developing alternative constant interior and exterior surface
coefficients, applying TRNSYS and EnergyPlus, respectively.
b Also checking input files versus the Transsolar participant’s files and vice versa.
Note: Results for “TestSpec-Alt” are shown in Table B8-16 and in Figures B8-6, B8-H10, and B8-H11; contents of tables and figures are further described in sheet tabs labeled "Table List" and "Figure List". “TestSpec-Alt” results are alternative values resulting from optional alternative inputs for sky temperature provided in the test specification (see Section 5.2.1.1.1.2 and Annex A1, Section A1.1.1.2).

## Table List
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B8-1 | Annual Heating Loads | Tables 1 | B7 - N57
| B8-2 | Annual Sensible Cooling Loads |  | B59 - N109
| B8-3 | Annual Hourly Integrated Peak Heating Loads | Tables 2 | B7 - AI57
| B8-4 | Annual Hourly Integrated Peak Sensible Cooling Loads |  | B59 - AI109
| B8-5 | Free-Float Temperature Output |  | B111 - AI145
| B8-6 | Low Mass Basic Sensitivity Tests | Tables 3 | B7 - N58
| B8-7 | High Mass Basic Sensitivity Tests |  | B61 - N112
| B8-8 | Low Mass In-Depth (Cases 195 thru 320) Sensitivity Tests | Tables 4 | B7 - N76
| B8-9 | Low Mass In-Depth (Cases 395 thru 470) Sensitivity Tests | Tables 5 | B7 - N64
| B8-10 | High Mass Basic and In-Depth Sensitivity Tests |  | B67 - N122
| B8-11 | Annual Transmissivity Coefficient of Windows | Tables 6 | B7 - N16
| B8-12 | Annual Shading Coefficient of Window Shading Devices: Overhangs & Fins |  | B18 - N25
| B8-13 | Case 600 Annual Incident Solar Radiation (kWh/m2) |  | B27 - N36
| B8-14 | Case 600 Annual Transmitted Solar Radiation – Unshaded (kWh/m2) |  | B38 - N46
| B8-15 | Case 600 Annual Transmitted Solar Radiation –Shaded (kWh/m2) |  | B48 - N54
| B8-16 | Sky Temperature Output, Case 600 | Tables 7 | B7 - AM15
| B8-M1 | Monthly Heating Loads | Tables M1 | B7 - N36
| B8-M2 | Monthly Sensible Cooling Loads |  | B38 - N67
| B8-M3 | Monthly Hourly Integrated Peak Heating Loads | Tables M2 | B7 - AB36
| B8-M4 | Monthly Hourly Integrated Peak Sensible Cooling Loads |  | B38 - AB67
| B8-M5 | Monthly Load 600-900 Sensitivity Tests | Tables M3 | B7 - N68

## Figure List
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
List of Figures
| Figure | Title | Sheet Tab
| B8-1 | Annual Incident Solar Radiation | Fig B8-1 Ann Incident Solar
| B8-2 | Annual Transmitted Solar Radiation Unshaded | Fig B8-2 Ann SolRad Unshaded
| B8-3 | Annual Transmitted Solar Radiation Shaded | Fig B8-3 Ann SolRad Shaded
| B8-4 | Annual Transmissivity Coefficient of Windows | Fig B8-4 Trans Coeff
(Unshaded Transmitted)/(Incident Solar Radiation)
| B8-5 | Annual Overhang and Fin Shading Coefficients | Fig B8-5 OH&Fin Shade Coeff
(1-(Shaded)/(Unshaded)) Transmitted Solar Radiation
| B8-6 | Average, Minimum and Maximum Sky Temperature, Case 600 | Fig B8-6 Sky Temp
| B8-7 | Basic: Low Mass Annual Heating | Fig B8-7 Lomass Ann Heat
| B8-8 | Basic: Low Mass Annual Sensible Cooling | Fig B8-8 Lomass Ann Cool
| B8-9 | Basic: Low Mass Peak Heating | Fig B8-9 Lomass Peak Heat
| B8-10 | Basic: Low Mass Peak Sensible Cooling | Fig B8-10 Lomass Peak Cool
| B8-11 | Basic: High Mass Annual Heating | Fig B8-11 Himass Ann Heat
| B8-12 | Basic: High Mass Annual Sensible Cooling | Fig B8-12 Himass Ann Cool
| B8-13 | Basic: High Mass Peak Heating | Fig B8-13 Himass Peak Heat
| B8-14 | Basic: High Mass Peak Sensible Cooling | Fig B8-14 Himass Peak Cool
| B8-15 | Basic and In-Depth: South Window (Delta), | Fig B8-15 Delta-S Win-Ann
Annual Heating and Sensible Cooling
| B8-16 | Basic and In-Depth: South Window (Delta), | Fig B8-16 Delta-S Win-Peak
Peak Heating and Sensible Cooling
| B8-17 | Basic: Window Shading and Orientation (Delta), | Fig B8-17 Delta-ShadeOrient-Load
Annual Heating and Sensible Cooling
| B8-18 | Basic: Window Shading and Orientation (Delta), | Fig B8-18 Delta-ShadeOrient-Peak
Peak Heating and Sensible Cooling
| B8-19 | Basic: Thermostat Setback, Vent Cooling, and Sunspace (Delta), | Fig B8-19 Delta-640650960-Load
Annual Heating and Sensible Cooling
| B8-20 | Basic: Thermostat Setback, Vent Cooling, and Sunspace (Delta), | Fig B8-20 Delta-640650960-Peak
Peak Heating and Sensible Cooling
| B8-21 | Basic and In-Depth: Mass Effect (Delta), | Fig B8-21 Delta-Mass Effect-Ann
Annual Heating and Sensible Cooling
| B8-22 | Basic and In-Depth: Mass Effect (Delta), | Fig B8-22 Delta-Mass Effect-Pk
Peak Heating and Sensible Cooling
| B8-23 | Basic: Cases 660 to 695 and 980 to 995 Annual Heating | Fig B8-23 660+ Ann Heat
| B8-24 | Basic: Cases 660 to 695 and 980 to 995 Annual Cooling | Fig B8-24 660+ Ann Cool
| B8-25 | Basic: Cases 660 to 695 and 980 to 995 Peak Heating | Fig B8-25 660+ Peak Heat
| B8-26 | Basic: Cases 660 to 695 and 980 to 995 Peak Cooling | Fig B8-26 660+ Peak Cool
| B8-27 | Basic: Window Types (Delta), Annual Heating and Sensible Cooling | Fig B8-27 Delta-Windows-Load
| B8-28 | Basic: Window Types (Delta), Peak Heating and Sensible Cooling | Fig B8-28 Delta-Windows-Peak
| B8-29 | Basic: Insulation (Delta), Annual Heating and Sensible Cooling | Fig B8-29 Delta-Insul-Load
| B8-30 | Basic: Insulation (Delta), Peak Heating and Sensible Cooling | Fig B8-30 Delta-Insul-Peak
| B8-31 | Basic: Insulation, Mass Effect (Delta), | Fig B8-31 Del-Mass-Ins-Load
Annual Heating and Sensible Cooling
| B8-32 | Basic: Insulation, Mass Effect (Delta), | Fig B8-32 Del-Mass-Ins-Peak
Peak Heating and Sensible Cooling
| B8-33 | Basic: Average Hourly Annual Temperature Free-Float Cases | Fig B8-33 FF Average Temp
| B8-34 | Basic: Maximum Hourly Annual Temperature Free-Float Cases | Fig B8-34 FF Maximum Temp
| B8-35 | Basic: Minimum Hourly Annual Temperature Free-Float Cases | Fig B8-35 FF Minimum Temp
| B8-36 | In-Depth: Low Mass Cases 195 to 250 Annual Heating | Fig B8-36 195to250 Ann Heat
| B8-37 | In-Depth: Low Mass Cases 195 to 250 Annual Sensible Cooling | Fig B8-37 195to250 Ann Cool
| B8-38 | In-Depth: Low Mass Cases 195 to 250 Peak Heating | Fig B8-38 195to250 Peak Heat
| B8-39 | In-Depth: Low Mass Cases 195 to 250 Peak Sensible Cooling | Fig B8-39 195to250 Peak Cool
| B8-40 | In-Depth: Low Mass Cases 270 to 320 Annual Heating | Fig B8-40 270to320 Ann Heat
| B8-41 | In-Depth: Low Mass Cases 270 to 320 Annual Sensible Cooling | Fig B8-41 270to320 Ann Cool
| B8-42 | In-Depth: Low Mass Cases 270 to 320 Peak Heating | Fig B8-42 270to320 Peak Heat
| B8-43 | In-Depth: Low Mass Cases 270 to 320 Peak Sensible Cooling | Fig B8-43 270to320 Peak Cool
| B8-44 | In-Depth: Cases 195 to 220 (Delta) | Fig B8-44 Delta 195to220 Load
Annual Heating and Sensible Cooling
| B8-45 | In-Depth: Cases 195 to 220 (Delta) | Fig B8-45 Delta 195to220 Peak
Peak Heating and Sensible Cooling
| B8-46 | In-Depth: Cases 220 to 270 (Delta) | Fig B8-46 Delta 220to270 Load
Annual Heating and Sensible Cooling
| B8-47 | In-Depth: Cases 220 to 270 (Delta) | Fig B8-47 Delta 220to270 Peak
Peak Heating and Sensible Cooling
| B8-48 | In-Depth: Cases 270 to 320 (Delta) | Fig B8-48 Delta 270to320 Load
Annual Heating and Sensible Cooling
| B8-49 | In-Depth: Cases 270 to 320 (Delta) | Fig B8-49 Delta 270to320 Peak
Peak Sensible Cooling
| B8-50 | In-Depth: Cases 395 to 440, 800, 810 Annual Heating | Fig B8-50 395to440,8n0 Ann Heat
| B8-51 | In-Depth: Cases 395 to 440, 800, 810 Annual Sensible Cooling | Fig B8-51 395to440,8n0 Ann Cool
| B8-52 | In-Depth: Cases 395 to 440, 800, 810 Peak Heating | Fig B8-52 395to440,8n0 Pk Heat
| B8-53 | In-Depth: Cases 395 to 440, 800, 810 Peak Sensible Cooling | Fig B8-53 395to440,8n0 Pk Cool
| B8-54 | In-Depth: Cases 395 to 600, 810 to 900 (Delta) | Fig B8-54 Del 395-600,810,900 Ld
Annual Heating and Sensible Cooling
| B8-55 | In-Depth: Cases 395 to 600, 810 to 900 (Delta) | Fig B8-55 Del 395-600,810,900 Pk
Peak Heating and Sensible Cooling
| B8-56 | In-Depth: Surface Heat Transfer Cases 600, 450, 460, 470 | Fig B8-56 SurfCoefs-Load
Annual Heating and Sensible Cooling
| B8-57 | In-Depth: Surface Heat Transfer Cases 600, 450, 460, 470 | Fig B8-57 SurfCoefs-Peak
Peak Heating and Sensible Cooling
| B8-58 | In-Depth: Surface Heat Transfer Cases 450 to 600 (Delta) | Fig B8-58 SurfHT Delta-Load
Annual Heating and Sensible Cooling
| B8-59 | In-Depth: Surface Heat Transfer Cases 450 to 600 (Delta) | Fig B8-59 SurfHT Delta-Peak
Peak Heating and Sensible Cooling
| B8-M1 | Monthly Heating, Case 600 | Fig B8-M1 MthlyHtg-600
| B8-M2 | Monthly Sensible Cooling, Case 600 | Fig B8-M2 MthlyCtg-600
| B8-M3 | Monthly Peak Heating, Case 600 | Fig B8-M3 MthlyPkHtg-600
| B8-M4 | Monthly Peak Sensible Cooling, Case 600 | Fig B8-M4 MthlyPkClg-600
| B8-M5 | Monthly Heating, Case 900 | Fig B8-M5 MthlyHtg-900
| B8-M6 | Monthly Sensible Cooling, Case 900 | Fig B8-M6 MthlyCtg-900
| B8-M7 | Monthly Peak Heating, Case 900 | Fig B8-M7 MthlyPkHtg-900
| B8-M8 | Monthly Peak Sensible Cooling, Case 900 | Fig B8-M8 MthlyPkClg-900
| B8-M9 | Monthly Heating Sensitivity (Delta), Case 600-900 | Fig B8-M9 Del-MthlyHtg 600-900
| B8-M10 | Monthly Cooling Sensitivity (Delta), Case 600-900 | Fig B8-M10 Del-MthlyCtg 600-900
| B8-M11 | Monthly Peak Heating Sensitivity (Delta), Case 600-900 | Fig B8-M11 Del-MthlyPkH 600-900
| B8-M12 | Monthly Peak Cooling Sensitivity (Delta), Case 600-900 | Fig B8-M12 Del-MthlyPkC 600-900
| B8-H1 | Case 900FF Annual Hourly Temperature Frequency | Fig B8-H1 Hrly-Temp Freq
| B8-H2 | Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-H2 Hrly-IncSol-Horz
Horizontal (Upward) Facing Surface
| B8-H3 | Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-H3 Hrly-IncidentSol-S
South Facing Surface
| B8-H4 | Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-H4 Hrly-IncidentSol-W
West Facing Surface
| B8-H5 | Cases 600, 660, 670 Hourly Transmitted Solar, Clear/Cold Day (Feb 1) | Fig B8-H5 Hrly-TransSol-Feb1
Double-Pane, Low-E, Single-Pane Windows
| B8-H6 | Case 600 Hourly Transmitted Solar, Cloudy Day (May 4) | Fig B8-H6 Hrly-Trans-May4-600
Double-Pane Windows
| B8-H7 | Cases 660,670 Hourly Transmitted Solar, Cloudy Day (May 4) | Fig B8-H7 Hrly-Trans-May4-6670
Low-E and Single-Pane Windows
| B8-H8 | Case 600 Hourly Transmitted Solar, Clear/Hot Day (Jul 14) | Fig B8-H8 Hrly-Trans-Jul14-600
Double-Pane Windows
| B8-H9 | Cases 660, 670 Hourly Transmitted Solar, Clear/Hot Day (Jul 14) | Fig B8-H9 Hrl-Trans-Jul14-6670
Low-E and Single-Pane Windows
| B8-H10 | Hourly Sky Temperatures, Case 600: | Fig B8-H10 Hrly-Tsky-ClearCloud
Clear/Cold, Cloudy Days
| B8-H11 | Hourly Sky Temperatures, Case 600: | Fig B8-H11 Hrly-Tsky-ColdHot
Clear/Cold, Clear/Hot Days
| B8-H12 | Hourly Free-Float Temperatures, | Fig B8-H12 Hrly-FF Temp-ColdDay
Clear Cold Day (Feb 1), Cases 600FF and 900FF
| B8-H13 | Hourly Free-Float Temperatures, | Fig B8-H13 Hrly-FF Temp-HotDay
Clear Hot Day (Jul 14), Cases 650FF and 950FF
| B8-H14 | Hourly Free-Float Temperatures, | Fig B8-H14 Hr-6980FF T-ColdDay
Clear Cold Day (Feb 1), Cases 680FF and 980FF
| B8-H15 | Hourly Loads: Clear Cold Day, Case 600 (Low Mass, Double-Clear Window) | Fig B8-H15 Hrly-600Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H16 | Hourly Loads: Clear Hot Day, Case 600 (Low Mass, Double-Clear Window) | Fig B8-H16 Hrly-600Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H17 | Hourly Loads: Clear Cold Day, Case 640 (Low Mass, Night Setback) | Fig B8-H17 Hrly-640Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H18 | Hourly Conditioned Zone Temperatures, Clear Cold Day, Case 640 | Fig B8-H18 Hrly-640Tzone-Cold
Heating (+), Sensible Cooling (-)
| B8-H19 | Hourly Loads: Clear Cold Day, Case 940 (High Mass, Night Setback) | Fig B8-H19 Hrly-940Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H20 | Hourly Conditioned Zone Temperatures, Clear Cold Day, Case 940 | Fig B8-H20 Hrly-940Tzone-Cold
Heating (+), Sensible Cooling (-)
| B8-H21 | Hourly Loads: Clear Cold Day, Case 660 (Low-E Window) | Fig B8-H21 Hrly-660Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H22 | Hourly Loads: Clear Hot Day, Case 660 (Low-E Window) | Fig B8-H22 Hrly-660Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H23 | Hourly Loads: Clear Cold Day, Case 670 (Single-Pane Window) | Fig B8-H23 Hrly-670Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H24 | Hourly Loads: Clear Hot Day, Case 670 (Single-Pane Window) | Fig B8-H24 Hrly-670Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H25 | Hourly Loads: Clear Cold Day, Case 680 (Insulation) | Fig B8-H25 Hrly-680Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H26 | Hourly Loads: Clear Hot Day, Case 680 (Insulation) | Fig B8-H26 Hrly-680Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H27 | Hourly Loads: Clear Cold Day, Case 685 (20/20 Tstat) | Fig B8-H27 Hrly-685Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H28 | Hourly Loads: Clear Hot Day, Case 685 (20/20 Tstat) | Fig B8-H28 Hrly-685Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H29 | Hourly Loads: Clear Cold Day, Case 695 (20/20, Insulation) | Fig B8-H29 Hrly-695Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H30 | Hourly Loads: Clear Hot Day, Case 695 (20/20, Insulation) | Fig B8-H30 Hrly-695Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H31 | Hourly Loads: Clear Cold Day, Case 900 (High Mass) | Fig B8-H31 Hrly-900Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H32 | Hourly Loads: Clear Hot Day, Case 900 (High Mass) | Fig B8-H32 Hrly-900Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H33 | Hourly Loads: Clear Cold Day, Case 980 (High Mass, Insulation) | Fig B8-H33 Hrly-980Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H34 | Hourly Loads: Clear Hot Day, Case 900 (High Mass, Insulation) | Fig B8-H34 Hrly-980Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H35 | Hourly Loads: Clear Cold Day, Case 985 (High Mass, 20/20 Tstat) | Fig B8-H35 Hrly-985Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H36 | Hourly Loads: Clear Hot Day, Case 985 (High Mass, 20/20 Tstat) | Fig B8-H36 Hrly-985Loads-Hot
Heating (+), Sensible Cooling (-)
| B8-H37 | Hourly Loads: Clear Cold Day, Case 995 (High Mass, 20/20, Insulation) | Fig B8-H37 Hrly-995Loads-Cold
Heating (+), Sensible Cooling (-)
| B8-H38 | Hourly Loads: Clear Hot Day, Case 995 (High Mass, 20/20, Insulation) | Fig B8-H38 Hrly-995Loads-Hot
Heating (+), Sensible Cooling (-)

## Tables 1
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-1. Annual Heating Loads (MWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
[7 empty] | Min | Max | Mean | (Max-Min)/
Case | [9 empty] | Mean** (%)
600 Base Case, South Windows | 4.05 | 3.9928 | 4.047 | 4.3244 | 4.362 | 4.5036 | 3.9928 | 4.5036 | 4.2133 | 12.12% |  | 0 | 0
610 S. Windows + Overhang | 4.163 | 4.0664 | 4.144 | 4.3748 | 4.527 | 4.5921 | 4.0664 | 4.5921 | 4.3112 | 12.19% |  | 1 | 1
620 East & West Windows | 4.37 | 4.0936 | 4.297 | 4.4851 | 4.5143 | 4.719 | 4.0936 | 4.719 | 4.4132 | 14.17% |  | 2 | 2
630 E&W Windows + Overhang & Fins | 4.923 | 4.3559 | 4.677 | 4.7835 | 5.0506 | 5.1386 | 4.3559 | 5.1386 | 4.8214 | 16.23% |  | 3 | 3
640 Case 600 with Htg Temp. Setback | 2.682 | 2.4032 | 2.619 | 2.6618 | 2.6544 | 2.6528 | 2.4032 | 2.682 | 2.6122 | 10.67% |  | 4 | 4
650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- |  | 5 | 5
660 Low-E Windows | 3.574 | 3.602 | 3.821 | 3.7067 | 3.787 | 3.7897 | 3.574 | 3.821 | 3.7134 | 6.652% |  |  | 6
670 Single-Pane Windows | 5.484 | 5.3002 | 5.573 | 5.6161 | 5.975 | 6.1399 | 5.3002 | 6.1399 | 5.6814 | 14.78% |  |  | 7
680 Case 600 with Increased Insulation | 2.219 | 1.7861 | 1.732 | 2.1797 | 2.1321 | 2.2863 | 1.732 | 2.2863 | 2.0559 | 26.96% |  |  | 8
685 Case 600 with "20/20" Thermostat | 4.532 | 4.5744 | 4.646 | 4.8771 | 4.9035 | 5.0422 | 4.532 | 5.0422 | 4.7625 | 10.71% |  |  | 9
695 Case 685 with Increased Insulation | 2.709 | 2.4153 | 2.385 | 2.8019 | 2.7321 | 2.8917 | 2.385 | 2.8917 | 2.6558 | 19.08% |  |  | 10
900 South Windows | 1.726 | 1.3789 | 1.591 | 1.6637 | 1.5847 | 1.814 | 1.3789 | 1.814 | 1.6264 | 26.75% |  | 6 | 11
910 S. Windows + Overhang | 2.163 | 1.6477 | 1.86 | 1.9557 | 2.0672 | 2.1318 | 1.6477 | 2.163 | 1.9709 | 26.15% |  | 7 | 12
920 East & West Windows | 3.5 | 2.9561 | 3.259 | 3.3365 | 3.2997 | 3.6067 | 2.9561 | 3.6067 | 3.3263 | 19.56% |  | 8 | 13
930 E&W Windows + Overhang & Fins | 4.27 | 3.5236 | 3.933 | 3.9938 | 4.2776 | 4.3841 | 3.5236 | 4.3841 | 4.0637 | 21.17% |  | 9 | 14
940 Case 900 with Htg Temp. Setback | 1.389 | 0.86324 | 1.149 | 1.0674 | 1.0147 | 1.1691 | 0.86324 | 1.389 | 1.1087 | 47.42% |  | 10 | 15
950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ---- |  | 11 | 16
960 Sunspace |  | 2.5221 | 2.771 | 2.689 | 2.6239 | 2.8595 | 2.5221 | 2.8595 | 2.6931 | 12.53% |  | 12 | 17
980 Case 900 with Increased Insulation | 0.72 | 0.24577 | 0.266 | 0.41094 | 0.3511 | 0.45047 | 0.24577 | 0.72 | 0.40738 | 116.4% |  |  | 18
985 Case 900 with "20/20" Thermostat | 2.801 | 2.1202 | 2.279 | 2.3693 | 2.2833 | 2.5364 | 2.1202 | 2.801 | 2.3982 | 28.39% |  |  | 19
995 Case 985 with Increased Insulation | 1.33 | 0.75518 | 0.77 | 1.0065 | 0.9048 | 1.077 | 0.75518 | 1.33 | 0.97392 | 59.02% |  |  | 20
195 Solid Conduction | 4.217 | 3.9901 | 4.157 | 4.0696 | 3.9509 | 4.0939 | 3.9509 | 4.217 | 4.0798 | 6.522% |  | 13 | 21
200 Surface Convection (Int & Ext IR="off") | 5.041 | 4.8135 | 5.226 | 5.1054 | 4.9204 | 5.1429 | 4.8135 | 5.226 | 5.0415 | 8.183% |  | 14 | 22
210 Infrared Radiation (Int IR="off", Ext IR="on") | 5.627 | 5.9663 | 6.531 | 6.0466 | 6.3171 | 6.4295 | 5.627 | 6.531 | 6.1529 | 14.69% |  | 15 | 23
215 Infrared Radiation (Int IR="on", Ext IR="off") | 5.652 | 5.3066 | 5.697 | 5.4054 | 5.1811 | 5.4434 | 5.1811 | 5.697 | 5.4476 | 9.47% |  | 16 | 24
220 In-Depth Base Case | 6.377 | 6.6663 | 7.178 | 6.4551 | 6.7257 | 6.8678 | 6.377 | 7.178 | 6.7117 | 11.93% |  | 17 | 25
230 Infiltration | 9.851 | 9.8124 | 10.417 | 9.9299 | 9.9385 | 10.2343 | 9.8124 | 10.417 | 10.0305 | 6.028% |  | 18 | 26
240 Internal Gains | 5.116 | 5.4426 | 5.944 | 5.2794 | 5.5393 | 5.6572 | 5.116 | 5.944 | 5.4964 | 15.06% |  | 19 | 27
250 Exterior Shortwave Absorptance | 4.733 | 5.0438 | 5.373 | 4.8991 | 4.935 | 5.1047 | 4.733 | 5.373 | 5.0148 | 12.76% |  | 20 | 28
270 South Solar Windows |  | 4.3465 | 4.273 | 4.3854 | 4.5764 | 4.6312 | 4.273 | 4.6312 | 4.4425 | 8.062% |  | 21 | 29
280 Cavity Albedo |  | 4.5249 | 4.619 | 4.5701 | 4.7381 | 4.8699 | 4.5249 | 4.8699 | 4.6644 | 7.396% |  | 22 | 30
290 South Shading |  | 4.4242 | 4.381 | 4.4244 | 4.7447 | 4.7248 | 4.381 | 4.7447 | 4.5398 | 8.011% |  | 23 | 31
300 East/West Window |  | 4.3184 | 4.46 | 4.4245 | 4.6679 | 4.7256 | 4.3184 | 4.7256 | 4.5193 | 9.012% |  | 24 | 32
310 East/West Shading |  | 4.5803 | 4.846 | 4.6912 | 5.2396 | 5.1626 | 4.5803 | 5.2396 | 4.9039 | 13.44% |  | 25 | 33
320 Thermostat |  | 3.6775 | 3.599 | 3.7712 | 3.9699 | 4.0311 | 3.599 | 4.0311 | 3.8097 | 11.34% |  | 26 | 34
395 Low Mass Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | 4.565 | 5.145 | 4.83 | 12.01% |  | 27 | 35
400 Low Mass High Cond. Wall Elements | 5.906 | 6.5358 | 7.047 | 6.3478 | 6.61 | 6.7692 | 5.906 | 7.047 | 6.536 | 17.46% |  | 28 | 36
410 Low Mass Infiltration | 7.63 | 8.0451 | 8.661 | 8.0803 | 8.2122 | 8.4449 | 7.63 | 8.661 | 8.1789 | 12.61% |  | 29 | 37
420 Low Mass Internal Gains | 6.399 | 6.8345 | 7.433 | 6.9058 | 7.027 | 7.2364 | 6.399 | 7.433 | 6.9726 | 14.83% |  | 30 | 38
430 Low Mass Ext. Shortwave Absorptance | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | 5.171 | 5.954 | 5.5991 | 13.98% |  | 31 | 39
440 Low Mass Cavity Albedo |  | 4.1559 | 4.33 | 4.5001 | 4.5039 | 4.7207 | 4.1559 | 4.7207 | 4.4421 | 12.71% |  | 32 | 40
450 Constant Interior and Exterior Surf Coeffs | 3.743 | 3.9904 | 3.375 | 3.9625 | 3.8503 | 3.8709 | 3.375 | 3.9904 | 3.7987 | 16.2% |  |  | 41
460 Constant Interior Surface Coefficients | 3.828 | 4.0555 | 3.873 | 4.1938 | 4.2625 | 4.2898 | 3.828 | 4.2898 | 4.0838 | 11.31% |  |  | 42
470 Constant Exterior Surface Coefficients | 4.042 | 3.8995 | 3.54 | 4.0939 | 3.9597 | 4.0746 | 3.54 | 4.0939 | 3.9349 | 14.08% |  |  | 43
800 High Mass High Cond. Wall Elements | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | 4.9057 | 5.403 | 5.1524 | 9.652% |  | 33 | 44
810 High Mass Cavity Albedo |  | 2.0375 | 2.454 | 2.3418 | 2.185 | 2.6098 | 2.0375 | 2.6098 | 2.3256 | 24.61% |  | 34 | 45
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-2. Annual Sensible Cooling Loads (MWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
[7 empty] | Min | Max | Mean | (Max-Min)/
Case | [9 empty] | Mean** (%)
600 Base Case, South Windows | 5.822 | 5.9131 | 5.432 | 6.027 | 6.1618 | 5.7795 | 5.432 | 6.1618 | 5.8559 | 12.46%
610 S. Windows + Overhang | 4.299 | 4.3818 | 4.173 | 4.3328 | 4.2325 | 4.1168 | 4.1168 | 4.3818 | 4.256 | 6.226%
620 East & West Windows | 4.404 | 4.0793 | 3.909 | 4.0595 | 4.2457 | 3.8407 | 3.8407 | 4.404 | 4.0897 | 13.77%
630 E&W Windows + Overhang & Fins | 3.074 | 3.0204 | 2.787 | 2.836 | 2.5953 | 2.5729 | 2.5729 | 3.074 | 2.8143 | 17.81%
640 Case 600 with Htg Temp. Setback | 5.804 | 5.6439 | 5.237 | 5.7631 | 5.8926 | 5.4772 | 5.237 | 5.8926 | 5.6363 | 11.63%
650 Case 600 with Night Ventilation | 4.629 | 4.6539 | 4.186 | 4.8168 | 4.9451 | 4.6323 | 4.186 | 4.9451 | 4.6438 | 16.35%
660 Low-E Windows | 3.014 | 3.3397 | 3.26 | 3.2315 | 3.2186 | 2.9663 | 2.9663 | 3.3397 | 3.1717 | 11.77%
670 Single-Pane Windows | 6.539 | 6.5777 | 5.954 | 6.6227 | 6.5203 | 6.1978 | 5.954 | 6.6227 | 6.4019 | 10.45%
680 Case 600 with Increased Insulation | 5.938 | 6.4298 | 5.932 | 6.4439 | 6.5294 | 6.3098 | 5.932 | 6.5294 | 6.2638 | 9.537%
685 Case 600 with "20/20" Thermostat | 9.13 | 8.8592 | 8.238 | 9.1188 | 9.1214 | 8.8513 | 8.238 | 9.13 | 8.8864 | 10.04%
695 Case 685 with Increased Insulation | 8.755 | 8.9741 | 8.386 | 9.1716 | 9.149 | 9.0391 | 8.386 | 9.1716 | 8.9125 | 8.814%
900 South Windows | 2.714 | 2.4638 | 2.383 | 2.4887 | 2.4877 | 2.2671 | 2.2671 | 2.714 | 2.4674 | 18.11%
910 S. Windows + Overhang | 1.484 | 1.4149 | 1.49 | 1.3835 | 1.2829 | 1.1909 | 1.1909 | 1.49 | 1.3744 | 21.77%
920 East & West Windows | 3.128 | 2.7892 | 2.706 | 2.7308 | 2.8144 | 2.5489 | 2.5489 | 3.128 | 2.7862 | 20.79%
930 E&W Windows + Overhang & Fins | 2.161 | 2.075 | 1.908 | 1.9191 | 1.6538 | 1.6718 | 1.6538 | 2.161 | 1.8981 | 26.72%
940 Case 900 with Htg. Temp. Setback | 2.613 | 2.3966 | 2.343 | 2.4244 | 2.4276 | 2.2035 | 2.2035 | 2.613 | 2.4013 | 17.05%
950 Case 900 with Night Ventilation | 0.586 | 0.59803 | 0.618 | 0.70692 | 0.656 | 0.64162 | 0.586 | 0.70692 | 0.63443 | 19.06%
960 Sunspace |  | 0.92578 | 0.909 | 0.90712 | 0.9496 | 0.78896 | 0.78896 | 0.9496 | 0.89609 | 17.93%
980 Case 900 with Increased Insulation | 3.501 | 3.9953 | 3.758 | 3.7118 | 3.7745 | 3.5185 | 3.501 | 3.9953 | 3.7099 | 13.32%
985 Case 900 with "20/20" Thermostat | 7.273 | 6.2336 | 5.88 | 6.3592 | 6.2493 | 6.1135 | 5.88 | 7.273 | 6.3514 | 21.93%
995 Case 985 with Increased Insulation | 7.482 | 7.2022 | 6.771 | 7.2029 | 7.1488 | 7.0638 | 6.771 | 7.482 | 7.1451 | 9.951%
195 Solid Conduction | 0.712 | 0.60552 | 0.628 | 0.61152 | 0.611 | 0.59153 | 0.59153 | 0.712 | 0.6266 | 19.23%
200 Surface Convection (Int & Ext IR="off") | 0.839 | 0.80024 | 0.835 | 0.81408 | 0.8004 | 0.78844 | 0.78844 | 0.839 | 0.81286 | 6.22%
210 Infrared Radiation (Int IR="off", Ext IR="on") | 0.688 | 0.50307 | 0.496 | 0.5599 | 0.5185 | 0.45918 | 0.45918 | 0.688 | 0.53744 | 42.58%
215 Infrared Radiation (Int IR="on", Ext IR="off") | 0.952 | 0.94579 | 0.922 | 0.87747 | 0.8948 | 0.85047 | 0.85047 | 0.952 | 0.90709 | 11.19%
220 In-Depth Base Case | 0.803 | 0.6106 | 0.55 | 0.6099 | 0.5762 | 0.49766 | 0.49766 | 0.803 | 0.60789 | 50.23%
230 Infiltration | 1.184 | 0.99134 | 0.929 | 0.99121 | 0.955 | 0.89664 | 0.89664 | 1.184 | 0.9912 | 28.99%
240 Internal Gains | 1.287 | 0.98237 | 0.876 | 0.97875 | 0.9218 | 0.83378 | 0.83378 | 1.287 | 0.97995 | 46.25%
250 Exterior Shortwave Absorptance | 3.612 | 3.429 | 3.471 | 3.1816 | 3.4668 | 2.9038 | 2.9038 | 3.612 | 3.344 | 21.18%
270 South Solar Windows |  | 7.2708 | 6.698 | 7.5215 | 7.3086 | 7.2885 | 6.698 | 7.5215 | 7.2175 | 11.41%
280 Cavity Albedo |  | 4.9963 | 4.215 | 5.1829 | 5.2058 | 4.8081 | 4.215 | 5.2058 | 4.8816 | 20.3%
290 South Shading |  | 5.6097 | 5.31 | 5.7425 | 5.3206 | 5.4612 | 5.31 | 5.7425 | 5.4888 | 7.88%
300 East/West Window |  | 5.0551 | 4.805 | 5.152 | 5.0381 | 4.913 | 4.805 | 5.152 | 4.9926 | 6.951%
310 East/West Shading |  | 3.7519 | 3.402 | 3.6695 | 3.1279 | 3.3242 | 3.1279 | 3.7519 | 3.4551 | 18.06%
320 Thermostat |  | 4.8585 | 4.42 | 4.986 | 4.9131 | 4.7877 | 4.42 | 4.986 | 4.7931 | 11.81%
395 Low Mass Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | 0.0035162 | 0.021 | 0.0090264 | 193.7%
400 Low Mass High Cond. Wall Elements | 0.063 | 0.023304 | 0.017 | 0.030566 | 0.0244 | 0.012683 | 0.012683 | 0.063 | 0.028492 | 176.6%
410 Low Mass Infiltration | 0.096 | 0.048491 | 0.041 | 0.057269 | 0.0523 | 0.03512 | 0.03512 | 0.096 | 0.05503 | 110.6%
420 Low Mass Internal Gains | 0.228 | 0.14062 | 0.119 | 0.15257 | 0.1419 | 0.10944 | 0.10944 | 0.228 | 0.14859 | 79.79%
430 Low Mass Ext. Shortwave Absorptance | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | 0.73902 | 1.084 | 0.91358 | 37.76%
440 Low Mass Cavity Albedo |  | 3.9853 | 3.458 | 4.085 | 4.4141 | 3.7412 | 3.458 | 4.4141 | 3.9367 | 24.29%
450 Constant Interior and Exterior Surf Coeffs | 6.172 | 5.689 | 6.161 | 6.5073 | 6.6132 | 6.5307 | 5.689 | 6.6132 | 6.2789 | 14.72%
460 Constant Interior Surface Coefficients | 6.26 | 5.9398 | 5.929 | 6.4746 | 6.7291 | 6.2434 | 5.929 | 6.7291 | 6.2626 | 12.78%
470 Constant Exterior Surface Coefficients | 5.987 | 5.6439 | 5.649 | 6.0294 | 6.0054 | 6.0559 | 5.6439 | 6.0559 | 5.8951 | 6.989%
800 High Mass High Cond. Wall Elements | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | 0.28208 | 0.473 | 0.37697 | 50.65%
810 High Mass Cavity Albedo |  | 1.4807 | 1.357 | 1.5078 | 1.6056 | 1.2945 | 1.2945 | 1.6056 | 1.4491 | 21.47%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 2
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-3. Annual Hourly Integrated Peak Heating Loads
Simulation Model: | BSIMAC |  |  |  | CSE |  |  |  | DeST |  |  |  | EnergyPlus |  |  |  | ESP-r |  |  |  | TRNSYS |  |  |  | Example Result Statistics |  |  |  |  | Tested Prg
[25 empty] | Min | Max | Mean | (Max-Min)/
Case | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | kW | kW | Mean** (%) | kW | Mo. | Day | Hr
600 Base Case, South Windows | 3.255 | Nov | 26 | 8 | 3.0202 | Jan | 1 | 1 | 3.035 | Jan | 1 | 0 | 3.2044 | Dec | 31 | 24 | 3.228 | Jan | 1 | 1 | 3.3589 | Jan | 1 | 1 | 3.0202 | 3.3589 | 3.1836 | 10.64% |  |  |  |  | 0 | 0
610 S. Windows + Overhang | 3.166 | Nov | 26 | 8 | 3.0208 | Jan | 1 | 1 | 3.039 | Jan | 1 | 0 | 3.1918 | Dec | 31 | 24 | 3.233 | Jan | 1 | 1 | 3.3595 | Jan | 1 | 1 | 3.0208 | 3.3595 | 3.1684 | 10.69% |  |  |  |  | 1 | 1
620 East & West Windows | 3.145 | Dec | 31 | 24 | 3.0379 | Jan | 1 | 1 | 3.068 | Jan | 1 | 0 | 3.2291 | Dec | 31 | 24 | 3.253 | Jan | 1 | 1 | 3.3846 | Jan | 1 | 1 | 3.0379 | 3.3846 | 3.1863 | 10.88% |  |  |  |  | 2 | 2
630 E&W Windows + Overhang & Fins | 3.252 | Dec | 31 | 24 | 3.0394 | Jan | 1 | 1 | 3.072 | Jan | 1 | 0 | 3.2066 | Dec | 31 | 24 | 3.259 | Jan | 1 | 1 | 3.3876 | Jan | 1 | 1 | 3.0394 | 3.3876 | 3.2027 | 10.87% |  |  |  |  | 3 | 3
640 Case 600 with Htg. Temp. Setback | 4.633 | Feb | 8 | 9 | 4.2225 | Nov | 26 | 8 | 4.658 | Nov | 26 | 7 | 4.5585 | Nov | 26 | 8 | 4.101 | Nov | 26 | 8 | 4.0385 | Nov | 26 | 8 | 4.0385 | 4.658 | 4.3686 | 14.18% |  |  |  |  | 4 | 4
650 Case 600 with Night Ventilation | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 | Jan | 1 | 1 | 0 | Dec | 31 | 0 | 0 | 0 | 0 | ---- |  |  |  |  | 5 | 5
660 Low-E Windows | 2.62 | Nov | 26 | 8 | 2.7583 | Jan | 1 | 1 | 2.798 | Jan | 1 | 0 | 2.8311 | Dec | 31 | 24 | 2.846 | Jan | 1 | 1 | 2.9552 | Jan | 1 | 1 | 2.62 | 2.9552 | 2.8014 | 11.96% | [5 empty] | 6
670 Single-Pane Windows | 4.122 | Nov | 26 | 8 | 3.6554 | Jan | 1 | 1 | 3.812 | Jan | 1 | 0 | 3.8535 | Nov | 26 | 7 | 3.992 | Nov | 26 | 7 | 4.221 | Nov | 26 | 8 | 3.6554 | 4.221 | 3.9427 | 14.34% | [5 empty] | 7
680 Case 600 with Increased Insulation | 2.126 | Nov | 26 | 8 | 1.7776 | Feb | 9 | 6 | 1.811 | Jan | 1 | 1 | 2.0524 | Nov | 26 | 7 | 2.022 | Feb | 9 | 7 | 2.1147 | Nov | 26 | 8 | 1.7776 | 2.126 | 1.984 | 17.56% | [5 empty] | 8
685 Case 600 with "20/20" Thermostat | 3.169 | Nov | 26 | 8 | 3.0319 | Jan | 1 | 1 | 3.054 | Jan | 1 | 0 | 3.2232 | Dec | 31 | 24 | 3.247 | Jan | 1 | 1 | 3.3744 | Jan | 1 | 1 | 3.0319 | 3.3744 | 3.1832 | 10.76% | [5 empty] | 9
695 Case 685 with Increased Insulation | 2.138 | Nov | 26 | 8 | 1.7953 | Jan | 1 | 1 | 1.855 | Jan | 1 | 1 | 2.0718 | Dec | 31 | 24 | 2.025 | Nov | 26 | 7 | 2.1177 | Nov | 26 | 8 | 1.7953 | 2.138 | 2.0005 | 17.13% | [5 empty] | 10
900 South Windows | 2.551 | Feb | 8 | 24 | 2.4434 | Feb | 9 | 6 | 2.453 | Feb | 9 | 5 | 2.6875 | Feb | 9 | 6 | 2.633 | Feb | 9 | 7 | 2.7785 | Feb | 9 | 7 | 2.4434 | 2.7785 | 2.5911 | 12.93% |  |  |  |  | 6 | 11
910 S. Windows + Overhang | 2.761 | Feb | 8 | 24 | 2.469 | Feb | 9 | 6 | 2.474 | Feb | 9 | 5 | 2.6989 | Feb | 9 | 6 | 2.684 | Feb | 9 | 7 | 2.7992 | Feb | 9 | 6 | 2.469 | 2.7992 | 2.6477 | 12.47% |  |  |  |  | 7 | 12
920 East & West Windows | 2.895 | Nov | 26 | 8 | 2.5124 | Feb | 9 | 6 | 2.513 | Feb | 9 | 5 | 2.7702 | Feb | 9 | 6 | 2.706 | Feb | 9 | 7 | 2.8643 | Feb | 9 | 6 | 2.5124 | 2.895 | 2.7101 | 14.12% |  |  |  |  | 8 | 13
930 E&W Windows + Overhang & Fins | 2.968 | Dec | 31 | 24 | 2.537 | Feb | 9 | 6 | 2.549 | Feb | 9 | 5 | 2.7849 | Feb | 9 | 6 | 2.765 | Feb | 9 | 6 | 2.9004 | Feb | 9 | 6 | 2.537 | 2.968 | 2.7507 | 15.67% |  |  |  |  | 9 | 14
940 Case 900 with Htg. Temp. Setback | 3.882 | Feb | 8 | 9 | 3.0519 | Jan | 1 | 9 | 3.659 | Feb | 9 | 7 | 3.1428 | Dec | 31 | 9 | 3.122 | Feb | 9 | 9 | 3.4048 | Jan | 1 | 9 | 3.0519 | 3.882 | 3.3771 | 24.58% |  |  |  |  | 10 | 15
950 Case 900 with Night Ventilation | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 |  |  |  | 0 | Jan | 1 | 1 | 0 | Jan | 1 | 1 | 0 | Dec | 31 | 0 | 0 | 0 | 0 | ---- |  |  |  |  | 11 | 16
960 Sunspace |  |  |  |  | 2.132 | Feb | 9 | 6 | 2.085 | Jan | 1 | 0 | 2.2594 | Feb | 9 | 6 | 2.201 | Feb | 9 | 6 | 2.3004 | Feb | 9 | 6 | 2.085 | 2.3004 | 2.1956 | 9.811% |  |  |  |  | 12 | 17
980 Case 900 with Increased Insulation | 1.693 | Feb | 8 | 24 | 1.2538 | Feb | 9 | 6 | 1.382 | Feb | 9 | 5 | 1.5378 | Feb | 9 | 6 | 1.473 | Feb | 9 | 7 | 1.5921 | Feb | 9 | 7 | 1.2538 | 1.693 | 1.4886 | 29.5% | [5 empty] | 18
985 Case 900 with "20/20" Thermostat | 2.754 | Feb | 8 | 24 | 2.4522 | Feb | 9 | 6 | 2.458 | Feb | 9 | 5 | 2.6954 | Feb | 9 | 6 | 2.642 | Feb | 9 | 7 | 2.7854 | Feb | 9 | 6 | 2.4522 | 2.7854 | 2.6312 | 12.67% | [5 empty] | 19
995 Case 985 with Increased Insulation | 1.711 | Nov | 26 | 8 | 1.3696 | Feb | 9 | 6 | 1.462 | Feb | 9 | 5 | 1.6221 | Feb | 9 | 6 | 1.56 | Feb | 9 | 7 | 1.662 | Feb | 9 | 6 | 1.3696 | 1.711 | 1.5644 | 21.83% | [5 empty] | 20
195 Solid Conduction | 1.802 | Dec | 31 | 24 | 1.7907 | Jan | 1 | 1 | 1.799 | Jan | 1 | 0 | 1.7944 | Dec | 31 | 24 | 1.802 | Jan | 1 | 1 | 1.7959 | Jan | 1 | 1 | 1.7907 | 1.802 | 1.7973 | 0.6288% |  |  |  |  | 13 | 21
200 Surface Convection (Int & Ext IR="off") | 2.272 | Nov | 26 | 8 | 2.226 | Nov | 26 | 8 | 2.308 | Jan | 1 | 0 | 2.3413 | Nov | 26 | 8 | 2.275 | Dec | 31 | 24 | 2.3527 | Nov | 26 | 8 | 2.226 | 2.3527 | 2.2958 | 5.518% |  |  |  |  | 14 | 22
210 Infrared Radiation (Int IR="off", Ext IR="on") | 2.374 | Dec | 31 | 24 | 2.629 | Jan | 1 | 2 | 2.605 | Jan | 1 | 0 | 2.5646 | Dec | 31 | 24 | 2.671 | Jan | 1 | 1 | 2.7498 | Jan | 1 | 1 | 2.374 | 2.7498 | 2.5989 | 14.46% |  |  |  |  | 15 | 23
215 Infrared Radiation (Int IR="on", Ext IR="off") | 2.521 | Nov | 26 | 8 | 2.42 | Nov | 26 | 8 | 2.52 | Jan | 1 | 0 | 2.4778 | Nov | 26 | 8 | 2.39 | Nov | 26 | 8 | 2.4894 | Nov | 26 | 8 | 2.39 | 2.521 | 2.4697 | 5.304% |  |  |  |  | 16 | 24
220 In-Depth Base Case | 2.631 | Nov | 26 | 8 | 2.8394 | Jan | 1 | 1 | 2.863 | Jan | 1 | 0 | 2.692 | Dec | 31 | 24 | 2.788 | Jan | 1 | 1 | 2.8786 | Jan | 1 | 1 | 2.631 | 2.8786 | 2.782 | 8.899% |  |  |  |  | 17 | 25
230 Infiltration | 4.219 | Dec | 31 | 24 | 4.1329 | Jan | 1 | 1 | 4.223 | Jan | 1 | 0 | 4.3161 | Dec | 31 | 24 | 4.16 | Jan | 1 | 1 | 4.3153 | Jan | 1 | 1 | 4.1329 | 4.3161 | 4.2277 | 4.333% |  |  |  |  | 18 | 26
240 Internal Gains | 2.431 | Nov | 26 | 8 | 2.6514 | Jan | 1 | 1 | 2.685 | Jan | 1 | 0 | 2.5071 | Dec | 31 | 24 | 2.605 | Jan | 1 | 1 | 2.6931 | Jan | 1 | 1 | 2.431 | 2.6931 | 2.5954 | 10.1% |  |  |  |  | 19 | 27
250 Exterior Shortwave Absorptance | 2.631 | Nov | 26 | 8 | 2.8371 | Jan | 1 | 1 | 2.855 | Jan | 1 | 0 | 2.6874 | Dec | 31 | 24 | 2.78 | Jan | 1 | 1 | 2.8744 | Jan | 1 | 1 | 2.631 | 2.8744 | 2.7775 | 8.762% |  |  |  |  | 20 | 28
270 South Solar Windows |  |  |  |  | 2.6114 | Jan | 1 | 2 | 2.56 | Jan | 1 | 1 | 2.5966 | Dec | 31 | 24 | 2.748 | Jan | 1 | 1 | 2.8432 | Jan | 1 | 2 | 2.56 | 2.8432 | 2.6718 | 10.6% |  |  |  |  | 21 | 29
280 Cavity Albedo |  |  |  |  | 2.6122 | Jan | 1 | 2 | 2.568 | Jan | 1 | 1 | 2.602 | Dec | 31 | 24 | 2.752 | Jan | 1 | 1 | 2.8487 | Jan | 1 | 1 | 2.568 | 2.8487 | 2.6766 | 10.49% |  |  |  |  | 22 | 30
290 South Shading |  |  |  |  | 2.6115 | Jan | 1 | 2 | 2.561 | Jan | 1 | 1 | 2.5834 | Dec | 31 | 24 | 2.75 | Jan | 1 | 1 | 2.8434 | Jan | 1 | 2 | 2.561 | 2.8434 | 2.6699 | 10.58% |  |  |  |  | 23 | 31
300 East/West Window |  |  |  |  | 2.6141 | Jan | 1 | 1 | 2.589 | Jan | 1 | 0 | 2.6031 | Dec | 31 | 24 | 2.766 | Jan | 1 | 1 | 2.8536 | Jan | 1 | 1 | 2.589 | 2.8536 | 2.6852 | 9.856% |  |  |  |  | 24 | 32
310 East/West Shading |  |  |  |  | 2.6149 | Jan | 1 | 1 | 2.592 | Jan | 1 | 0 | 2.5801 | Dec | 31 | 24 | 2.771 | Jan | 1 | 1 | 2.8563 | Jan | 1 | 1 | 2.5801 | 2.8563 | 2.6829 | 10.3% |  |  |  |  | 25 | 33
320 Thermostat |  |  |  |  | 2.609 | Jan | 1 | 1 | 2.546 | Jan | 1 | 1 | 2.5735 | Dec | 31 | 24 | 2.733 | Jan | 1 | 2 | 2.8335 | Jan | 1 | 2 | 2.546 | 2.8335 | 2.659 | 10.81% |  |  |  |  | 26 | 34
395 Low Mass Solid Conduction | 1.948 | Dec | 31 | 24 | 2.1574 | Jan | 1 | 2 | 2.085 | Jan | 1 | 1 | 1.9517 | Dec | 31 | 24 | 2.09 | Jan | 1 | 2 | 2.1613 | Jan | 1 | 2 | 1.948 | 2.1613 | 2.0656 | 10.33% |  |  |  |  | 27 | 35
400 Low Mass High Cond. Wall Elements | 2.559 | Nov | 26 | 8 | 2.8394 | Jan | 1 | 1 | 2.863 | Jan | 1 | 0 | 2.692 | Dec | 31 | 24 | 2.788 | Jan | 1 | 1 | 2.8786 | Jan | 1 | 1 | 2.559 | 2.8786 | 2.77 | 11.54% |  |  |  |  | 28 | 36
410 Low Mass Infiltration | 3.338 | Dec | 31 | 24 | 3.4407 | Jan | 1 | 1 | 3.543 | Jan | 1 | 0 | 3.504 | Dec | 31 | 24 | 3.473 | Jan | 1 | 1 | 3.5969 | Jan | 1 | 1 | 3.338 | 3.5969 | 3.4826 | 7.435% |  |  |  |  | 29 | 37
420 Low Mass Internal Gains | 3.138 | Dec | 31 | 24 | 3.2562 | Jan | 1 | 1 | 3.365 | Jan | 1 | 0 | 3.3191 | Dec | 31 | 24 | 3.29 | Jan | 1 | 1 | 3.4115 | Jan | 1 | 1 | 3.138 | 3.4115 | 3.2966 | 8.295% |  |  |  |  | 30 | 38
430 Low Mass Ext. Shortwave Absorptance | 3.3 | Dec | 31 | 24 | 3.2539 | Jan | 1 | 1 | 3.36 | Jan | 1 | 0 | 3.3163 | Dec | 31 | 24 | 3.285 | Jan | 1 | 1 | 3.4088 | Jan | 1 | 1 | 3.2539 | 3.4088 | 3.3207 | 4.666% |  |  |  |  | 31 | 39
440 Low Mass Cavity Albedo |  |  |  |  | 3.0272 | Jan | 1 | 1 | 3.06 | Jan | 1 | 0 | 3.2187 | Dec | 31 | 24 | 3.237 | Jan | 1 | 1 | 3.3743 | Jan | 1 | 1 | 3.0272 | 3.3743 | 3.1834 | 10.9% |  |  |  |  | 32 | 40
450 Constant Interior and Exterior Surf Coeffs | 2.989 | Nov | 26 | 8 | 2.9783 | Jan | 1 | 1 | 2.753 | Jan | 1 | 0 | 3.0998 | Dec | 31 | 24 | 3.042 | Jan | 1 | 1 | 3.0373 | Jan | 1 | 1 | 2.753 | 3.0998 | 2.9832 | 11.63% | [5 empty] | 41
460 Constant Interior Surface Coefficients | 3.055 | Nov | 26 | 8 | 2.9714 | Jan | 1 | 1 | 2.98 | Jan | 1 | 0 | 3.0911 | Dec | 31 | 24 | 3.101 | Jan | 1 | 1 | 3.1597 | Jan | 1 | 1 | 2.9714 | 3.1597 | 3.0597 | 6.155% | [5 empty] | 42
470 Constant Exterior Surface Coefficients | 3.118 | Nov | 26 | 8 | 3.0007 | Jan | 1 | 1 | 2.807 | Jan | 1 | 0 | 3.2067 | Dec | 31 | 24 | 3.169 | Jan | 1 | 1 | 3.2315 | Jan | 1 | 1 | 2.807 | 3.2315 | 3.0888 | 13.74% | [5 empty] | 43
800 High Mass High Cond. Wall Elements | 2.957 | Dec | 31 | 24 | 2.7776 | Feb | 9 | 6 | 2.864 | Feb | 9 | 5 | 2.9237 | Feb | 9 | 6 | 2.84 | Feb | 9 | 7 | 2.9669 | Feb | 9 | 6 | 2.7776 | 2.9669 | 2.8882 | 6.555% |  |  |  |  | 33 | 44
810 High Mass Cavity Albedo |  |  |  |  | 2.5001 | Feb | 9 | 6 | 2.512 | Feb | 9 | 5 | 2.749 | Feb | 9 | 6 | 2.695 | Feb | 9 | 7 | 2.8447 | Feb | 9 | 6 | 2.5001 | 2.8447 | 2.6602 | 12.95% |  |  |  |  | 34 | 45
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-4. Annual Hourly Integrated Peak Sensible Cooling Loads
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | Mo. | Day | Hr | kW | kW | kW | Mean** (%) | kW | Mo. | Day | Hr
600 Base Case, South Windows | 5.65 | Jan | 22 | 15 | 6.481 | Jan | 22 | 14 | 5.422 | Jan | 22 | 14 | 6.3516 | Jan | 22 | 14 | 6.193 | Jan | 22 | 14 | 6.0457 | Jan | 22 | 14 | 5.422 | 6.481 | 6.0239 | 17.58%
610 S. Windows + Overhang | 5.466 | Jan | 22 | 15 | 6.4322 | Dec | 1 | 14 | 5.331 | Jan | 22 | 14 | 6.1345 | Dec | 1 | 14 | 5.934 | Jan | 22 | 14 | 5.8678 | Dec | 1 | 14 | 5.331 | 6.4322 | 5.8609 | 18.79%
620 East & West Windows | 4.704 | Jun | 26 | 18 | 4.4928 | Jun | 26 | 17 | 3.955 | Jun | 26 | 17 | 4.7974 | Jun | 26 | 17 | 4.622 | Jun | 26 | 17 | 4.5883 | Jun | 26 | 17 | 3.955 | 4.7974 | 4.5266 | 18.61%
630 E&W Windows + Overhang & Fins | 4.121 | Jun | 26 | 18 | 3.9983 | Jun | 26 | 18 | 3.526 | Jun | 26 | 17 | 4.2122 | Jun | 26 | 17 | 3.971 | Jun | 26 | 17 | 3.9494 | Jun | 26 | 17 | 3.526 | 4.2122 | 3.963 | 17.31%
640 Case 600 with Htg. Temp. Setback | 5.65 | Jan | 22 | 15 | 6.429 | Jan | 22 | 14 | 5.365 | Jan | 22 | 14 | 6.2974 | Jan | 22 | 14 | 6.127 | Jan | 22 | 14 | 5.9671 | Jan | 22 | 14 | 5.365 | 6.429 | 5.9726 | 17.81%
650 Case 600 with Night Ventilation | 5.648 | Jan | 22 | 15 | 6.2897 | Dec | 1 | 14 | 5.045 | Oct | 18 | 14 | 6.1381 | Oct | 18 | 14 | 5.961 | Oct | 18 | 14 | 5.7975 | Oct | 18 | 14 | 5.045 | 6.2897 | 5.8132 | 21.41%
660 Low-E Windows | 3.343 | Oct | 18 | 15 | 3.933 | Oct | 1 | 13 | 3.355 | Oct | 11 | 14 | 3.7703 | Oct | 18 | 14 | 3.53 | Oct | 1 | 14 | 3.4574 | Oct | 18 | 14 | 3.343 | 3.933 | 3.5648 | 16.55%
670 Single-Pane Windows | 6.217 | Oct | 18 | 14 | 6.9253 | Oct | 1 | 13 | 5.839 | Oct | 10 | 13 | 6.8062 | Jan | 22 | 14 | 6.482 | Oct | 18 | 14 | 6.4013 | Oct | 18 | 14 | 5.839 | 6.9253 | 6.4451 | 16.85%
680 Case 600 with Increased Insulation | 5.761 | Jan | 22 | 15 | 7.0513 | Jan | 22 | 14 | 5.861 | Jan | 22 | 14 | 6.7702 | Jan | 22 | 14 | 6.676 | Jan | 22 | 14 | 6.5566 | Jan | 22 | 14 | 5.761 | 7.0513 | 6.446 | 20.02%
685 Case 600 with "20/20" Thermostat | 6.318 | Jan | 22 | 15 | 7.1594 | Jan | 22 | 14 | 6.071 | Jan | 22 | 14 | 7.1068 | Jan | 22 | 14 | 6.934 | Jan | 22 | 14 | 6.8674 | Jan | 22 | 14 | 6.071 | 7.1594 | 6.7428 | 16.14%
695 Case 685 with Increased Insulation | 6.232 | Jan | 22 | 15 | 7.5407 | Jan | 22 | 14 | 6.355 | Jan | 22 | 14 | 7.3343 | Jan | 22 | 14 | 7.239 | Jan | 22 | 14 | 7.1752 | Jan | 22 | 14 | 6.232 | 7.5407 | 6.9794 | 18.75%
900 South Windows | 3.039 | Oct | 1 | 15 | 3.3764 | Oct | 1 | 14 | 2.556 | Sep | 11 | 14 | 3.0404 | Oct | 1 | 14 | 2.896 | Oct | 12 | 15 | 2.9401 | Oct | 1 | 14 | 2.556 | 3.3764 | 2.9747 | 27.58%
910 S. Windows + Overhang | 2.493 | Oct | 18 | 14 | 2.7221 | Oct | 2 | 15 | 2.103 | Oct | 12 | 14 | 2.2221 | Oct | 18 | 15 | 2.212 | Oct | 2 | 15 | 2.081 | Oct | 12 | 15 | 2.081 | 2.7221 | 2.3055 | 27.8%
920 East & West Windows | 3.481 | Jun | 26 | 18 | 3.0567 | Jun | 26 | 18 | 2.71 | Jun | 26 | 17 | 3.2603 | Jun | 26 | 18 | 3.099 | Jun | 26 | 18 | 3.1541 | Jun | 26 | 18 | 2.71 | 3.481 | 3.1269 | 24.66%
930 E&W Windows + Overhang & Fins | 3.052 | Jun | 26 | 18 | 2.6618 | Jun | 26 | 18 | 2.335 | Jun | 26 | 17 | 2.7815 | Jun | 26 | 18 | 2.494 | Jun | 26 | 18 | 2.6131 | Jun | 26 | 18 | 2.335 | 3.052 | 2.6562 | 26.99%
940 Case 900 with Htg. Temp. Setback | 3.158 | Oct | 1 | 15 | 3.3764 | Oct | 1 | 14 | 2.556 | Sep | 11 | 14 | 3.04 | Oct | 1 | 14 | 2.891 | Oct | 12 | 15 | 2.9376 | Oct | 1 | 14 | 2.556 | 3.3764 | 2.9932 | 27.41%
950 Case 900 with Night Ventilation | 2.366 | Sep | 10 | 15 | 2.3635 | Sep | 4 | 15 | 2.054 | Sep | 11 | 14 | 2.3875 | Sep | 11 | 15 | 2.202 | Sep | 10 | 15 | 2.2364 | Sep | 11 | 15 | 2.054 | 2.3875 | 2.2682 | 14.7%
960 Sunspace |  |  |  |  | 1.3771 | Jun | 26 | 17 | 1.367 | Jun | 26 | 16 | 1.4799 | Jun | 26 | 17 | 1.403 | Jun | 26 | 17 | 1.3385 | Jun | 26 | 17 | 1.3385 | 1.4799 | 1.3931 | 10.15%
980 Case 900 with Increased Insulation | 3.384 | Oct | 18 | 14 | 3.668 | Oct | 2 | 14 | 2.93 | Oct | 18 | 14 | 3.4501 | Oct | 18 | 15 | 3.341 | Oct | 12 | 15 | 3.3126 | Oct | 12 | 14 | 2.93 | 3.668 | 3.3476 | 22.05%
985 Case 900 with "20/20" Thermostat | 3.977 | Oct | 18 | 14 | 4.2253 | Oct | 1 | 14 | 3.208 | Oct | 11 | 14 | 3.9148 | Oct | 18 | 15 | 3.736 | Oct | 12 | 15 | 3.8847 | Oct | 1 | 14 | 3.208 | 4.2253 | 3.8243 | 26.6%
995 Case 985 with Increased Insulation | 4.129 | Jan | 22 | 14 | 4.2238 | Jan | 22 | 15 | 3.315 | Jan | 22 | 14 | 4.1774 | Jan | 22 | 15 | 3.954 | Jan | 22 | 15 | 4.1149 | Jan | 22 | 15 | 3.315 | 4.2238 | 3.9857 | 22.8%
195 Solid Conduction | 1.118 | Jun | 26 | 17 | 0.99425 | Jun | 26 | 17 | 0.973 | Jun | 26 | 16 | 1.041 | Jun | 26 | 17 | 0.944 | Jun | 26 | 17 | 0.99351 | Jun | 26 | 17 | 0.944 | 1.118 | 1.0106 | 17.22%
200 Surface Convection (Int & Ext IR="off") | 1.271 | Jun | 26 | 17 | 1.2152 | Jun | 26 | 17 | 1.239 | Jun | 26 | 16 | 1.3075 | Jun | 26 | 17 | 1.198 | Jun | 26 | 17 | 1.2589 | Jun | 26 | 17 | 1.198 | 1.3075 | 1.2483 | 8.77%
210 Infrared Radiation (Int IR="off", Ext IR="on") | 1.193 | Jun | 26 | 17 | 0.94562 | Jun | 13 | 15 | 0.937 | Jun | 26 | 16 | 1.0844 | Jun | 26 | 17 | 0.877 | Jun | 14 | 14 | 0.88416 | Jun | 26 | 18 | 0.877 | 1.193 | 0.98686 | 32.02%
215 Infrared Radiation (Int IR="on", Ext IR="off") | 1.393 | Jun | 26 | 17 | 1.3692 | Jun | 26 | 17 | 1.386 | Jun | 26 | 16 | 1.4004 | Jun | 26 | 17 | 1.366 | Jun | 26 | 17 | 1.3521 | Jun | 26 | 17 | 1.3521 | 1.4004 | 1.3778 | 3.505%
220 In-Depth Base Case | 1.336 | Jun | 26 | 18 | 1.1085 | Jun | 13 | 15 | 1.04 | Jun | 26 | 16 | 1.1845 | Jun | 26 | 18 | 1.012 | Jun | 14 | 15 | 0.96801 | Jun | 26 | 18 | 0.96801 | 1.336 | 1.1082 | 33.21%
230 Infiltration | 1.994 | Jun | 26 | 17 | 1.7281 | Jun | 26 | 17 | 1.734 | Jun | 26 | 16 | 1.8409 | Jun | 26 | 17 | 1.701 | Jun | 26 | 17 | 1.6936 | Jun | 26 | 17 | 1.6936 | 1.994 | 1.7819 | 16.86%
240 Internal Gains | 1.534 | Jun | 26 | 18 | 1.2947 | Jun | 13 | 15 | 1.218 | Jun | 26 | 16 | 1.3659 | Jun | 26 | 18 | 1.192 | Jun | 14 | 15 | 1.1496 | Jun | 26 | 18 | 1.1496 | 1.534 | 1.2924 | 29.75%
250 Exterior Shortwave Absorptance | 2.913 | Sep | 12 | 14 | 2.79 | Sep | 12 | 14 | 2.751 | Sep | 3 | 14 | 2.8666 | Sep | 12 | 14 | 3.034 | Sept | 12 | 14 | 2.688 | Sep | 12 | 14 | 2.688 | 3.034 | 2.8404 | 12.18%
270 South Solar Windows |  |  |  |  | 7.011 | Jan | 22 | 14 | 5.832 | Jan | 22 | 14 | 6.8388 | Jan | 22 | 14 | 6.613 | Jan | 22 | 14 | 6.6375 | Jan | 22 | 14 | 5.832 | 7.011 | 6.5865 | 17.9%
280 Cavity Albedo |  |  |  |  | 4.7651 | Jan | 22 | 14 | 3.768 | Dec | 1 | 13 | 4.7272 | Jan | 22 | 14 | 4.676 | Jan | 22 | 14 | 4.3999 | Jan | 22 | 14 | 3.768 | 4.7651 | 4.4672 | 22.32%
290 South Shading |  |  |  |  | 6.8722 | Jan | 22 | 14 | 5.739 | Jan | 22 | 14 | 6.5946 | Jan | 22 | 14 | 6.411 | Jan | 22 | 14 | 6.4019 | Jan | 22 | 14 | 5.739 | 6.8722 | 6.4037 | 17.7%
300 East/West Window |  |  |  |  | 4.1631 | Jun | 26 | 17 | 3.695 | Jun | 26 | 17 | 4.4755 | Jun | 26 | 17 | 4.221 | Jun | 26 | 17 | 4.2782 | Jun | 26 | 17 | 3.695 | 4.4755 | 4.1666 | 18.73%
310 East/West Shading |  |  |  |  | 3.7959 | Jun | 26 | 18 | 3.252 | Jun | 26 | 17 | 3.9695 | Jun | 26 | 18 | 3.618 | Jun | 26 | 18 | 3.7015 | Jun | 26 | 18 | 3.252 | 3.9695 | 3.6674 | 19.57%
320 Thermostat |  |  |  |  | 6.4733 | Jan | 22 | 14 | 5.304 | Jan | 22 | 14 | 6.2091 | Jan | 22 | 14 | 5.993 | Jan | 22 | 14 | 5.9494 | Jan | 22 | 14 | 5.304 | 6.4733 | 5.9858 | 19.53%
395 Low Mass Solid Conduction | 0.547 | Jun | 26 | 18 | 0.3575 | Jun | 14 | 18 | 0.308 | Jun | 14 | 16 | 0.37747 | Jun | 26 | 19 | 0.294 | Aug | 5 | 18 | 0.2652 | Jun | 14 | 18 | 0.2652 | 0.547 | 0.3582 | 78.67%
400 Low Mass High Cond. Wall Elements | 0.798 | Jun | 26 | 18 | 0.49365 | Jun | 14 | 15 | 0.457 | Jun | 26 | 17 | 0.60691 | Jun | 26 | 18 | 0.456 | Aug | 5 | 17 | 0.37199 | Jun | 14 | 17 | 0.37199 | 0.798 | 0.53059 | 80.29%
410 Low Mass Infiltration | 1.011 | Jun | 26 | 17 | 0.69988 | Jun | 26 | 18 | 0.709 | Jun | 26 | 16 | 0.82785 | Jun | 26 | 18 | 0.624 | Jun | 26 | 18 | 0.60368 | Jun | 26 | 18 | 0.60368 | 1.011 | 0.7459 | 54.61%
420 Low Mass Internal Gains | 1.208 | Jun | 26 | 17 | 0.90853 | Jun | 26 | 18 | 0.917 | Jun | 26 | 16 | 1.0325 | Jun | 26 | 18 | 0.836 | Jun | 26 | 17 | 0.81407 | Jun | 26 | 18 | 0.81407 | 1.208 | 0.95269 | 41.35%
430 Low Mass Ext. Shortwave Absorptance | 2.167 | Jun | 26 | 16 | 1.8398 | Jun | 26 | 15 | 1.84 | Jun | 26 | 15 | 1.9294 | Jun | 26 | 16 | 1.874 | Jul | 17 | 14 | 1.7041 | Jun | 26 | 15 | 1.7041 | 2.167 | 1.8924 | 24.46%
440 Low Mass Cavity Albedo |  |  |  |  | 4.6655 | Oct | 1 | 13 | 3.766 | Oct | 11 | 13 | 4.686 | Oct | 18 | 14 | 4.679 | Oct | 18 | 14 | 4.3076 | Oct | 18 | 14 | 3.766 | 4.686 | 4.4208 | 20.81%
450 Constant Interior and Exterior Surf Coeffs | 5.812 | Jan | 22 | 15 | 6.1798 | Jan | 22 | 14 | 6.063 | Jan | 22 | 13 | 6.4663 | Jan | 22 | 14 | 6.501 | Jan | 22 | 14 | 6.3134 | Jan | 22 | 14 | 5.812 | 6.501 | 6.2226 | 11.07%
460 Constant Interior Surface Coefficients | 5.804 | Jan | 22 | 15 | 6.2429 | Jan | 22 | 14 | 5.902 | Jan | 22 | 13 | 6.3742 | Jan | 22 | 14 | 6.304 | Jan | 22 | 14 | 6.0689 | Jan | 22 | 14 | 5.804 | 6.3742 | 6.116 | 9.323%
470 Constant Exterior Surface Coefficients | 5.695 | Jan | 22 | 15 | 6.3877 | Jan | 22 | 14 | 5.57 | Jan | 22 | 14 | 6.4436 | Jan | 22 | 14 | 6.407 | Jan | 22 | 14 | 6.32 | Jan | 22 | 14 | 5.57 | 6.4436 | 6.1372 | 14.24%
800 High Mass High Cond. Wall Elements | 1.286 | Jun | 26 | 16 | 1.1019 | Aug | 5 | 15 | 1.157 | Aug | 5 | 14 | 1.0458 | Jun | 26 | 16 | 1.052 | Aug | 5 | 15 | 0.93559 | Aug | 5 | 15 | 0.93559 | 1.286 | 1.0964 | 31.96%
810 High Mass Cavity Albedo |  |  |  |  | 2.4105 | Sep | 4 | 15 | 1.94 | Sep | 11 | 14 | 2.2702 | Sep | 11 | 15 | 2.179 | Sep | 4 | 15 | 2.1129 | Sep | 11 | 15 | 1.94 | 2.4105 | 2.1825 | 21.56%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-5. Free-Float Temperature Output
MAXIMUM ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Mo. | Day | Hr
600FF - Low Mass with S. Windows | 63.4 | Oct | 18 | 17 | 68.3608 | Oct | 1 | 16 | 65 | Oct | 11 | 15 | 63.8408 | Oct | 18 | 16 | 64.6 | Oct | 1 | 16 | 62.3692 | Oct | 1 | 15 | 62.3692 | 68.3608 | 64.5951 | 9.276%
900FF - High Mass with S. Windows | 46 | Oct | 1 | 17 | 45.1138 | Sep | 4 | 15 | 44.46 | Sep | 11 | 15 | 44.2922 | Sep | 12 | 15 | 44.3 | Sep | 12 | 16 | 43.2522 | Sep | 12 | 15 | 43.2522 | 46 | 44.5697 | 6.165%
650FF Case 600FF with Night Ventilation | 62.1 | Oct | 18 | 17 | 66.8465 | Oct | 1 | 16 | 62.59 | Oct | 11 | 15 | 62.469 | Oct | 18 | 16 | 63.3 | Oct | 1 | 16 | 61.1332 | Oct | 1 | 15 | 61.1332 | 66.8465 | 63.0731 | 9.058%
950FF Case 900FF with Night Ventilation | 37.1 | Oct | 1 | 17 | 36.7765 | Sep | 11 | 15 | 36.37 | Sep | 11 | 15 | 36.6805 | Sep | 11 | 16 | 36.4 | Aug | 5 | 16 | 36.1267 | Sep | 11 | 16 | 36.1267 | 37.1 | 36.5756 | 2.661%
680FF Case 600FF with Increased Insulation | 72.5 | Jan | 22 | 17 | 78.5143 | Jan | 22 | 16 | 74.97 | Oct | 12 | 15 | 70.1447 | Jan | 22 | 16 | 72.2 | Oct | 12 | 16 | 69.7742 | Jan | 22 | 16 | 69.7742 | 78.5143 | 73.0172 | 11.97%
980FF Case 900FF with Increased Insulation | 49.7 | Oct | 1 | 17 | 52.2464 | Sep | 12 | 15 | 52.81 | Oct | 21 | 14 | 49.6221 | Sep | 12 | 16 | 50.2 | Sep | 12 | 15 | 48.5406 | Sep | 12 | 15 | 48.5406 | 52.81 | 50.5198 | 8.451%
960 Sunspace |  |  |  |  | 48.9033 | Oct | 2 | 16 | 53.18 | Oct | 20 | 14 | 49.8773 | Oct | 12 | 15 | 49.5 | Oct | 12 | 15 | 48.0966 | Oct | 12 | 15 | 48.0966 | 53.18 | 49.9114 | 10.18%
MINIMUM ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Mo. | Day | Hr
600FF - Low Mass with S. Windows | -9.9 | Nov | 26 | 8 | -12.8904 | Feb | 9 | 7 | -13.52 | Feb | 9 | 6 | -12.5613 | Feb | 9 | 7 | -13.5 | Feb | 9 | 7 | -13.8442 | Feb | 9 | 7 | -13.8442 | -9.9 | -12.7026 | 31.05%
900FF - High Mass with S. Windows | 0.6 | Feb | 8 | 11 | 2.1647 | Feb | 9 | 7 | 1.31 | Feb | 9 | 7 | 1.2424 | Feb | 9 | 7 | 1.6 | Feb | 9 | 7 | 0.63931 | Feb | 9 | 7 | 0.6 | 2.1647 | 1.2594 | 124.2%
650FF Case 600FF with Night Ventilation | -16.7 | Dec | 31 | 24 | -17.7616 | Jan | 1 | 1 | -17.37 | Dec | 30 | 23 | -17.0758 | Dec | 31 | 24 | -17.5 | Jan | 1 | 1 | -17.5067 | Dec | 31 | 24 | -17.7616 | -16.7 | -17.319 | 6.129%
950FF Case 900FF with Night Ventilation | -13.2 | Dec | 31 | 24 | -13.2443 | Jan | 1 | 1 | -13.36 | Dec | 30 | 23 | -12.8122 | Feb | 9 | 7 | -12.5 | Feb | 9 | 6 | -12.7995 | Feb | 9 | 6 | -13.36 | -12.5 | -12.986 | 6.623%
680FF Case 600FF with Increased Insulation | -5.7 | Feb | 8 | 11 | -6.1966 | Feb | 9 | 7 | -6.89 | Feb | 9 | 7 | -7.0523 | Feb | 9 | 7 | -7.2 | Feb | 9 | 7 | -8.0736 | Feb | 9 | 7 | -8.0736 | -5.7 | -6.8521 | 34.64%
980FF Case 900FF with Increased Insulation | 7.3 | Feb | 8 | 11 | 12.5361 | Nov | 4 | 7 | 12.4 | Nov | 5 | 6 | 9.917 | Nov | 4 | 7 | 10.5 | Nov | 4 | 8 | 9.4717 | Nov | 4 | 7 | 7.3 | 12.5361 | 10.3541 | 50.57%
960 Sunspace |  |  |  |  | 8.0165 | Feb | 9 | 8 | 6.74 | Feb | 9 | 6 | 5.0931 | Feb | 9 | 7 | 5 | Feb | 9 | 7 | 4.2376 | Feb | 9 | 7 | 4.2376 | 8.0165 | 5.8174 | 64.96%
AVERAGE ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Case: Simulation Model:; kW: BSIMAC; kW: CSE; kW: DeST; kW: EnergyPlus; kW: ESP-r; kW: TRNSYS; Min kW: Example Result Statistics |  |  | Tested Prg
Min kW: Min; Max kW: Max; Mean kW: Mean | (Max-Min)/
Case: Case; kW: T (°C); kW: T (°C); kW: T (°C); kW: T (°C); kW: T (°C); kW: T (°C); Min kW: T (°C); Max kW: T (°C); Mean kW: T (°C) | Mean** (%) | T (°C)
Case: 600FF - Low Mass with S. Windows; kW: 26.1; kW: 25.5736; kW: 25.26; kW: 24.9173; kW: 25.26; kW: 24.2578; Min kW: 24.2578; Max kW: 26.1; Mean kW: 25.2281 | 7.302%
Case: 900FF - High Mass with S. Windows; kW: 25.5; kW: 25.6921; kW: 25.25; kW: 25.1213; kW: 25.34; kW: 24.4623; Min kW: 24.4623; Max kW: 25.6921; Mean kW: 25.2276 | 4.875%
Case: 650FF Case 600FF with Night Ventilation; kW: 17.6; kW: 18.4599; kW: 18.04; kW: 18.4195; kW: 18.93; kW: 18.402; Min kW: 17.6; Max kW: 18.93; Mean kW: 18.3086 | 7.264%
Case: 950FF Case 900FF with Night Ventilation; kW: 15; kW: 14.7096; kW: 14.35; kW: 14.789; kW: 14.78; kW: 14.6786; Min kW: 14.35; Max kW: 15; Mean kW: 14.7179 | 4.416%
Case: 680FF Case 600FF with Increased Insulation; kW: 31.8; kW: 33.1103; kW: 33.3; kW: 30.9584; kW: 31.71; kW: 30.1869; Min kW: 30.1869; Max kW: 33.3; Mean kW: 31.8443 | 9.776%
Case: 980FF Case 900FF with Increased Insulation; kW: 30.7; kW: 33.2952; kW: 33.3; kW: 31.1618; kW: 31.84; kW: 30.492; Min kW: 30.492; Max kW: 33.3; Mean kW: 31.7982 | 8.831%
Case: 960 Sunspace; kW: 28.5573; kW: 29.45; kW: 27.7427; kW: 27.74; kW: 26.7976; Min kW: 26.7976; Max kW: 29.45; Mean kW: 28.0575 | 9.453%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 3
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-6. Low Mass Basic Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Heat, S. Shade | 0.113 | 0.073669 | 0.097 | 0.050431 | 0.165 | 0.08851 | 0.050431 | 0.165 | 0.097935 | 117%
620-600 Heat, E&W Orient. | 0.32 | 0.10084 | 0.25 | 0.1607 | 0.1523 | 0.21543 | 0.10084 | 0.32 | 0.19988 | 109.6%
630-620 Heat, E&W Shade | 0.553 | 0.26235 | 0.38 | 0.29847 | 0.5363 | 0.4196 | 0.26235 | 0.553 | 0.40829 | 71.19%
640-600 Heat, Htg. Setback | -1.368 | -1.5895 | -1.428 | -1.6625 | -1.7076 | -1.8508 | -1.8508 | -1.368 | -1.6011 | 30.15%
660-600 Heat, Low-E Win. | -0.476 | -0.3908 | -0.226 | -0.61764 | -0.575 | -0.71389 | -0.71389 | -0.226 | -0.49989 | 97.6%
670-600 Heat, 1-Pane Win. | 1.434 | 1.3074 | 1.526 | 1.2918 | 1.613 | 1.6363 | 1.2918 | 1.6363 | 1.4681 | 23.47%
680-600 Heat, > Ins. 20/27 | -1.831 | -2.2067 | -2.315 | -2.1447 | -2.2299 | -2.2173 | -2.315 | -1.831 | -2.1574 | 22.43%
685-600 Heat, 20/20 tstat | 0.482 | 0.58167 | 0.599 | 0.55275 | 0.5415 | 0.53862 | 0.482 | 0.599 | 0.54926 | 21.3%
695-685 Heat, > Ins. 20/20 | -1.823 | -2.1592 | -2.261 | -2.0752 | -2.1714 | -2.1504 | -2.261 | -1.823 | -2.1067 | 20.79%
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Cool, S. Shade | -1.523 | -1.5313 | -1.259 | -1.6943 | -1.9293 | -1.6627 | -1.9293 | -1.259 | -1.5999 | 41.9%
620-600 Cool, E&W Orient. | -1.418 | -1.8338 | -1.523 | -1.9675 | -1.9161 | -1.9389 | -1.9675 | -1.418 | -1.7662 | 31.11%
630-620 Cool, E&W Shade | -1.33 | -1.0589 | -1.122 | -1.2235 | -1.6504 | -1.2678 | -1.6504 | -1.0589 | -1.2754 | 46.38%
640-600 Cool, Htg. Setback | -0.018 | -0.26921 | -0.195 | -0.26394 | -0.2692 | -0.3023 | -0.3023 | -0.018 | -0.21961 | 129.5%
650-600 Cool, Night Vent | -1.193 | -1.2592 | -1.246 | -1.2103 | -1.2167 | -1.1472 | -1.2592 | -1.1472 | -1.2121 | 9.246%
660-600 Heat, Low-E Win. | -2.808 | -2.5734 | -2.172 | -2.7955 | -2.9432 | -2.8133 | -2.9432 | -2.172 | -2.6842 | 28.73%
670-600 Heat, 1-Pane Win. | 0.717 | 0.66462 | 0.522 | 0.59566 | 0.3585 | 0.41828 | 0.3585 | 0.717 | 0.54601 | 65.66%
680-600 Heat, > Ins. 20/27 | 0.116 | 0.51669 | 0.5 | 0.41686 | 0.3676 | 0.53023 | 0.116 | 0.53023 | 0.4079 | 101.6%
685-600 Heat, 20/20 tstat | 3.308 | 2.9461 | 2.806 | 3.0918 | 2.9596 | 3.0718 | 2.806 | 3.308 | 3.0305 | 16.56%
695-685 Heat, > Ins. 20/20 | -0.375 | 0.1149 | 0.148 | 0.052759 | 0.0276 | 0.18778 | -0.375 | 0.18778 | 0.026007 | 2164%
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Heat, S. Shade | -0.089 | 0.000526 | 0.004 | -0.012584 | 0.005 | 0.00060921 | -0.089 | 0.005 | -0.015241 | 616.7%
620-600 Heat, E&W Orient. | -0.11 | 0.017627 | 0.033 | 0.024696 | 0.025 | 0.025699 | -0.11 | 0.033 | 0.0026702 | 5355%
630-620 Heat, E&W Shade | 0.107 | 0.001512 | 0.004 | -0.022564 | 0.006 | 0.0029619 | -0.022564 | 0.107 | 0.016485 | 786%
640-600 Heat, Htg. Setback | 1.378 | 1.2022 | 1.623 | 1.3541 | 0.873 | 0.67965 | 0.67965 | 1.623 | 1.185 | 79.61%
660-600 Heat, Low-E Win. | -0.635 | -0.26192 | -0.237 | -0.3733 | -0.382 | -0.40371 | -0.635 | -0.237 | -0.38216 | 104.1% |  | 0 | -0.40023 | -0.40371 | -0.38216 | 0.01327 | 6
670-600 Heat, 1-Pane Win. | 0.867 | 0.63519 | 0.777 | 0.6491 | 0.764 | 0.86207 | 0.63519 | 0.867 | 0.75906 | 30.54% |  | 7 | 0.63519 | 0.86207 | 0.75906 | 0.037066 | 7
680-600 Heat, > Ins. 20/27 | -1.129 | -1.2426 | -1.224 | -1.152 | -1.206 | -1.2442 | -1.2442 | -1.129 | -1.1996 | 9.601% |  | 7 | -1.2426 | -1.2329 | -1.1996 | 0.069211 | 8
685-600 Heat, 20/20 tstat | -0.086 | 0.011624 | 0.019 | 0.018741 | 0.019 | 0.015534 | -0.086 | 0.019 | -0.0003502 | 29983% |  | 0 | 0.011624 | 0.015534 | -0.0003502 | 0.00124 | 9
695-685 Heat, > Ins. 20/20 | -1.031 | -1.2365 | -1.199 | -1.1514 | -1.222 | -1.2567 | -1.2567 | -1.031 | -1.1828 | 19.08% |  | 7 | -1.2365 | -1.2364 | -1.1828 | 0.06368 | 1
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Case | [6 empty] | Min | Max | Mean | Mean** (%)
610-600 Cool, S. Shade | -0.184 | -0.048825 | -0.091 | -0.21703 | -0.259 | -0.17795 | -0.259 | -0.048825 | -0.16297 | 129%
620-600 Cool, E&W Orient. | -0.946 | -1.9882 | -1.467 | -1.5541 | -1.571 | -1.4575 | -1.9882 | -0.946 | -1.4973 | 69.6%
630-620 Cool, E&W Shade | -0.583 | -0.49451 | -0.429 | -0.58526 | -0.651 | -0.63889 | -0.651 | -0.429 | -0.56361 | 39.39%
640-600 Cool, Htg. Setback | 0 | -0.052004 | -0.057 | -0.05417 | -0.066 | -0.078665 | -0.078665 | 0 | -0.051306 | 153.3%
650-600 Cool, Night Vent | -0.002 | -0.19129 | -0.377 | -0.21342 | -0.232 | -0.24825 | -0.377 | -0.002 | -0.21066 | 178%
660-600 Heat, Low-E Win. | -2.307 | -2.548 | -2.067 | -2.5812 | -2.663 | -2.5883 | -2.663 | -2.067 | -2.4591 | 24.24% |  | 0 | -2.079 | -2.548 | -2.4591 | -0.010291
670-600 Heat, 1-Pane Win. | 0.567 | 0.44432 | 0.417 | 0.45463 | 0.289 | 0.35556 | 0.289 | 0.567 | 0.42125 | 65.99% |  | 0 | 0.417 | 0.44432 | 0.42125 | -0.0072513
680-600 Heat, > Ins. 20/27 | 0.111 | 0.57027 | 0.439 | 0.41866 | 0.483 | 0.51086 | 0.111 | 0.57027 | 0.42213 | 108.8% |  | 0 | 0.339 | 0.57027 | 0.42213 | 0.024365
685-600 Heat, 20/20 tstat | 0.668 | 0.67846 | 0.649 | 0.7552 | 0.741 | 0.82169 | 0.649 | 0.82169 | 0.71889 | 24.02% |  | 0 | 0.649 | 0.67846 | 0.71889 | -0.014375
695-685 Heat, > Ins. 20/20 | -0.086 | 0.38129 | 0.284 | 0.22753 | 0.305 | 0.30772 | -0.086 | 0.38129 | 0.23659 | 197.5% |  | 0 | 0.161 | 0.38129 | 0.23659 | 0.026091
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-7. High Mass Basic Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Heat | -2.324 | -2.6139 | -2.456 | -2.6607 | -2.7773 | -2.6895 | -2.7773 | -2.324 | -2.5869 | 17.52%
910-900 Heat, S. Shade | 0.437 | 0.26879 | 0.269 | 0.29205 | 0.4825 | 0.31776 | 0.26879 | 0.4825 | 0.34452 | 62.03%
920-900 Heat, E&W Orient. | 1.774 | 1.5772 | 1.668 | 1.6728 | 1.715 | 1.7927 | 1.5772 | 1.7927 | 1.6999 | 12.68%
930-920 Heat, E&W Shade | 0.77 | 0.56758 | 0.674 | 0.6573 | 0.9779 | 0.7774 | 0.56758 | 0.9779 | 0.73736 | 55.65%
940-900 Heat, Htg. Setback | -0.337 | -0.51566 | -0.442 | -0.5963 | -0.57 | -0.6449 | -0.6449 | -0.337 | -0.51764 | 59.48%
960-900 Heat, Sunspace |  | 1.1432 | 1.18 | 1.0254 | 1.0392 | 1.0455 | 1.0254 | 1.18 | 1.0866 | 14.23%
980-900 Heat, > Ins. 20/27 | -1.006 | -1.1331 | -1.325 | -1.2527 | -1.2336 | -1.3636 | -1.3636 | -1.006 | -1.219 | 29.33%
985-900 Heat, 20/20 tstat | 1.075 | 0.74132 | 0.688 | 0.70563 | 0.6986 | 0.72238 | 0.688 | 1.075 | 0.77182 | 50.14%
995-985 Heat, > Ins. 20/20 | -1.471 | -1.365 | -1.509 | -1.3628 | -1.3785 | -1.4594 | -1.509 | -1.3628 | -1.4243 | 10.26%
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Cool | -3.108 | -3.4493 | -3.049 | -3.5383 | -3.6741 | -3.5124 | -3.6741 | -3.049 | -3.3885 | 18.45%
910-900 Cool, S. Shade | -1.23 | -1.049 | -0.893 | -1.1053 | -1.2048 | -1.0763 | -1.23 | -0.893 | -1.093 | 30.83%
920-900 Cool, E&W Orient. | 0.414 | 0.32538 | 0.323 | 0.2421 | 0.3267 | 0.28174 | 0.2421 | 0.414 | 0.31882 | 53.92%
930-920 Cool, E&W Shade | -0.967 | -0.71422 | -0.798 | -0.81173 | -1.1606 | -0.87711 | -1.1606 | -0.71422 | -0.88811 | 50.26%
940-900 Cool, Htg. Setback | -0.101 | -0.06725 | -0.04 | -0.06439 | -0.0601 | -0.06367 | -0.101 | -0.04 | -0.066068 | 92.33%
950-900 Cool, Night Vent | -2.128 | -1.8658 | -1.765 | -1.7818 | -1.8317 | -1.6255 | -2.128 | -1.6255 | -1.833 | 27.41%
960-900 Cool, Sunspace |  | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | -1.5816 | -1.474 | -1.522 | 7.071%
980-900 Heat, > Ins. 20/27 | 0.787 | 1.5314 | 1.375 | 1.2231 | 1.2868 | 1.2514 | 0.787 | 1.5314 | 1.2425 | 59.92%
985-900 Heat, 20/20 tstat | 4.559 | 3.7698 | 3.497 | 3.8704 | 3.7616 | 3.8463 | 3.497 | 4.559 | 3.884 | 27.34%
995-985 Heat, > Ins. 20/20 | 0.209 | 0.9685 | 0.891 | 0.84367 | 0.8995 | 0.95032 | 0.209 | 0.9685 | 0.79367 | 95.7%
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Heat | -0.704 | -0.57684 | -0.582 | -0.51694 | -0.595 | -0.58042 | -0.704 | -0.51694 | -0.59253 | 31.57%
910-900 Heat, S. Shade | 0.21 | 0.025635 | 0.021 | 0.011437 | 0.051 | 0.020717 | 0.011437 | 0.21 | 0.056631 | 350.6%
920-900 Heat, E&W Orient. | 0.344 | 0.069036 | 0.06 | 0.08269 | 0.073 | 0.085796 | 0.06 | 0.344 | 0.11909 | 238.5%
930-920 Heat, E&W Shade | 0.073 | 0.024542 | 0.036 | 0.014719 | 0.059 | 0.03614 | 0.014719 | 0.073 | 0.040567 | 143.7%
940-900 Heat, Htg. Setback | 1.331 | 0.60852 | 1.206 | 0.45528 | 0.489 | 0.62635 | 0.45528 | 1.331 | 0.78602 | 111.4%
960-900 Heat, Sunspace |  | -0.31135 | -0.368 | -0.42812 | -0.432 | -0.47808 | -0.47808 | -0.31135 | -0.40351 | 41.32%
980-900 Heat, > Ins. 20/27 | -0.858 | -1.1896 | -1.071 | -1.1497 | -1.16 | -1.1863 | -1.1896 | -0.858 | -1.1024 | 30.08% |  | 0 | -1.1896 | -1.0855 | -1.1024 | 0.16572 | 7
985-900 Heat, 20/20 tstat | 0.203 | 0.008773 | 0.005 | 0.0079536 | 0.009 | 0.0069624 | 0.005 | 0.203 | 0.040115 | 493.6% |  | -1 | 0.008773 | 0.0069624 | 0.040115 | -0.0026598 | 8
995-985 Heat, > Ins. 20/20 | -1.043 | -1.0826 | -0.996 | -1.0733 | -1.082 | -1.1235 | -1.1235 | -0.996 | -1.0667 | 11.95% |  | 0 | -1.0826 | -1.0744 | -1.0667 | 0.091588 | 1
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
900-600 Mass, Cool | -2.611 | -3.1046 | -2.866 | -3.3111 | -3.297 | -3.1057 | -3.3111 | -2.611 | -3.0492 | 22.96%
910-900 Cool, S. Shade | -0.546 | -0.65436 | -0.453 | -0.81835 | -0.684 | -0.85903 | -0.85903 | -0.453 | -0.66912 | 60.68%
920-900 Cool, E&W Orient. | 0.442 | -0.31975 | 0.154 | 0.21988 | 0.203 | 0.21408 | -0.31975 | 0.442 | 0.1522 | 500.5%
930-920 Cool, E&W Shade | -0.429 | -0.39486 | -0.375 | -0.47881 | -0.605 | -0.54103 | -0.605 | -0.375 | -0.47062 | 48.87%
940-900 Cool, Htg. Setback | 0.119 | 0 | 0 | -0.00048524 | -0.005 | -0.0024478 | -0.005 | 0.119 | 0.018511 | 669.9%
950-900 Cool, Night Vent | -0.673 | -1.0129 | -0.502 | -0.65292 | -0.694 | -0.70368 | -1.0129 | -0.502 | -0.70642 | 72.33%
960-900 Cool, Sunspace |  | -1.9993 | -1.189 | -1.5605 | -1.493 | -1.6016 | -1.9993 | -1.189 | -1.5687 | 51.66%
980-900 Heat, > Ins. 20/27 | 0.345 | 0.29156 | 0.374 | 0.40968 | 0.445 | 0.37249 | 0.29156 | 0.445 | 0.37295 | 41.14% |  | 0 | 0.374 | 0.29156 | 0.37295 | -0.055353
985-900 Heat, 20/20 tstat | 0.938 | 0.84883 | 0.652 | 0.87434 | 0.84 | 0.94464 | 0.652 | 0.94464 | 0.84963 | 34.44% |  | 0 | 0.652 | 0.84883 | 0.84963 | -0.0098063
995-985 Heat, > Ins. 20/20 | 0.152 | -0.001482 | 0.107 | 0.26266 | 0.218 | 0.2302 | -0.001482 | 0.26266 | 0.1614 | 163.7% |  | 1 | 0.107 | -0.001482 | 0.1614 | -0.037989
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 4
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-8. Low Mass In-Depth (Cases 195 thru 320) Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.824 | 0.82337 | 1.069 | 1.0358 | 0.9695 | 1.0489 | 0.82337 | 1.069 | 0.96176 | 25.54%
210-200 Ext IR (Int IR "off") | 0.586 | 1.1529 | 1.305 | 0.94118 | 1.3967 | 1.2866 | 0.586 | 1.3967 | 1.1114 | 72.94%
220-215 Ext IR (Int IR "on") | 0.725 | 1.3597 | 1.481 | 1.0497 | 1.5446 | 1.4244 | 0.725 | 1.5446 | 1.2641 | 64.84%
215-200 Int IR (Ext IR "off") | 0.611 | 0.49316 | 0.471 | 0.30004 | 0.2607 | 0.30051 | 0.2607 | 0.611 | 0.40607 | 86.27%
220-210 Int IR (Ext IR "on") | 0.75 | 0.70003 | 0.647 | 0.40857 | 0.4086 | 0.43834 | 0.40857 | 0.75 | 0.55876 | 61.1%
230-220 Infiltration | 3.474 | 3.146 | 3.239 | 3.4747 | 3.2128 | 3.3665 | 3.146 | 3.4747 | 3.3188 | 9.904%
240-220 Internal Gains | -1.261 | -1.2237 | -1.234 | -1.1758 | -1.1864 | -1.2106 | -1.261 | -1.1758 | -1.2153 | 7.014%
250-220 Ext Solar Abs. | -1.644 | -1.6225 | -1.805 | -1.556 | -1.7907 | -1.7631 | -1.805 | -1.556 | -1.6969 | 14.67%
270-220 South Windows |  | -2.3199 | -2.905 | -2.0698 | -2.1493 | -2.2367 | -2.905 | -2.0698 | -2.3361 | 35.75%
280-270 Cavity Albedo |  | 0.17846 | 0.346 | 0.18472 | 0.1617 | 0.23873 | 0.1617 | 0.346 | 0.22192 | 83.05%
320-270 Thermostat |  | -0.66901 | -0.674 | -0.61416 | -0.6065 | -0.60003 | -0.674 | -0.60003 | -0.63274 | 11.69%
290-270 South Shading |  | 0.077715 | 0.108 | 0.039046 | 0.1683 | 0.09362 | 0.039046 | 0.1683 | 0.097336 | 132.8%
300-270 E&W Windows |  | -0.028118 | 0.187 | 0.039197 | 0.0915 | 0.09447 | -0.028118 | 0.187 | 0.07681 | 280.1%
310-300 E&W Shading |  | 0.26199 | 0.386 | 0.26662 | 0.5717 | 0.43695 | 0.26199 | 0.5717 | 0.38465 | 80.52%
ANNUAL SENSIBLE COOLING [MWh]
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.127 | 0.19471 | 0.207 | 0.20256 | 0.1894 | 0.19691 | 0.127 | 0.207 | 0.18626 | 42.95%
210-200 Ext IR (Int IR "off") | -0.151 | -0.29717 | -0.339 | -0.25418 | -0.2819 | -0.32926 | -0.339 | -0.151 | -0.27542 | 68.26%
220-215 Ext IR (Int IR "on") | -0.149 | -0.33519 | -0.372 | -0.26756 | -0.3186 | -0.35281 | -0.372 | -0.149 | -0.29919 | 74.53%
215-200 Int IR (Ext IR "off") | 0.113 | 0.14556 | 0.087 | 0.063388 | 0.0944 | 0.062024 | 0.062024 | 0.14556 | 0.094228 | 88.65%
220-210 Int IR (Ext IR "on") | 0.115 | 0.10753 | 0.054 | 0.050007 | 0.0577 | 0.038475 | 0.038475 | 0.115 | 0.070452 | 108.6%
230-220 Infiltration | 0.381 | 0.38074 | 0.379 | 0.38131 | 0.3788 | 0.39898 | 0.3788 | 0.39898 | 0.3833 | 5.265%
240-220 Internal Gains | 0.484 | 0.37177 | 0.326 | 0.36884 | 0.3456 | 0.33612 | 0.326 | 0.484 | 0.37206 | 42.47%
250-220 Ext Solar Abs. | 2.809 | 2.8184 | 2.921 | 2.5717 | 2.8906 | 2.4062 | 2.4062 | 2.921 | 2.7361 | 18.82%
270-220 South Windows |  | 6.6602 | 6.148 | 6.9116 | 6.7324 | 6.7908 | 6.148 | 6.9116 | 6.6486 | 11.49%
280-270 Cavity Albedo |  | -2.2745 | -2.483 | -2.3386 | -2.1028 | -2.4804 | -2.483 | -2.1028 | -2.3359 | 16.28%
320-270 Thermostat |  | -2.4123 | -2.278 | -2.5356 | -2.3955 | -2.5008 | -2.5356 | -2.278 | -2.4244 | 10.62%
290-270 South Shading |  | -1.6611 | -1.388 | -1.779 | -1.988 | -1.8273 | -1.988 | -1.388 | -1.7287 | 34.71%
300-270 E&W Windows |  | -2.2158 | -1.893 | -2.3695 | -2.2705 | -2.3755 | -2.3755 | -1.893 | -2.2249 | 21.69%
310-300 E&W Shading |  | -1.3032 | -1.403 | -1.4825 | -1.9102 | -1.5887 | -1.9102 | -1.3032 | -1.5375 | 39.48%
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.47 | 0.43534 | 0.509 | 0.54692 | 0.473 | 0.5568 | 0.43534 | 0.5568 | 0.49851 | 24.37%
210-200 Ext IR (Int IR "off") | 0.102 | 0.40294 | 0.297 | 0.22323 | 0.396 | 0.39706 | 0.102 | 0.40294 | 0.30304 | 99.31%
220-215 Ext IR (Int IR "on") | 0.11 | 0.41938 | 0.343 | 0.21421 | 0.398 | 0.3892 | 0.11 | 0.41938 | 0.3123 | 99.07%
215-200 Int IR (Ext IR "off") | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | 0.115 | 0.249 | 0.17385 | 77.08%
220-210 Int IR (Ext IR "on") | 0.257 | 0.2104 | 0.258 | 0.12747 | 0.117 | 0.12878 | 0.117 | 0.258 | 0.18311 | 77%
230-220 Infiltration | 1.588 | 1.2935 | 1.36 | 1.6241 | 1.372 | 1.4367 | 1.2935 | 1.6241 | 1.4457 | 22.86%
240-220 Internal Gains | -0.2 | -0.18795 | -0.178 | -0.18492 | -0.183 | -0.18548 | -0.2 | -0.178 | -0.18656 | 11.79%
250-220 Ext Solar Abs. | 0 | -0.002311 | -0.008 | -0.0046183 | -0.008 | -0.0042134 | -0.008 | 0 | -0.0045238 | 176.8%
270-220 South Windows |  | -0.228 | -0.303 | -0.09541 | -0.04 | -0.035333 | -0.303 | -0.035333 | -0.14035 | 190.7%
280-270 Cavity Albedo |  | 0.000866 | 0.008 | 0.005384 | 0.004 | 0.005441 | 0.000866 | 0.008 | 0.0047382 | 150.6%
320-270 Thermostat |  | -0.002429 | -0.014 | -0.023142 | -0.015 | -0.0097238 | -0.023142 | -0.002429 | -0.012859 | 161.1%
290-270 South Shading |  | 7.1e-05 | 0.001 | -0.013189 | 0.002 | 0.00016606 | -0.013189 | 0.002 | -0.0019905 | 763.1%
300-270 E&W Windows |  | 0.002675 | 0.029 | 0.0065091 | 0.018 | 0.010408 | 0.002675 | 0.029 | 0.013318 | 197.7%
310-300 E&W Shading |  | 0.00082 | 0.003 | -0.023064 | 0.005 | 0.0026624 | -0.023064 | 0.005 | -0.0023163 | 1212%
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
200-195 Surface Convection | 0.153 | 0.22092 | 0.266 | 0.26648 | 0.254 | 0.26541 | 0.153 | 0.26648 | 0.23764 | 47.75%
210-200 Ext IR (Int IR "off") | -0.078 | -0.26955 | -0.302 | -0.22309 | -0.321 | -0.37477 | -0.37477 | -0.078 | -0.2614 | 113.5%
220-215 Ext IR (Int IR "on") | -0.057 | -0.26079 | -0.346 | -0.2159 | -0.354 | -0.38409 | -0.38409 | -0.057 | -0.26963 | 121.3%
215-200 Int IR (Ext IR "off") | 0.122 | 0.15407 | 0.147 | 0.092921 | 0.168 | 0.093176 | 0.092921 | 0.168 | 0.12953 | 57.96%
220-210 Int IR (Ext IR "on") | 0.143 | 0.16283 | 0.103 | 0.1001 | 0.135 | 0.083849 | 0.083849 | 0.16283 | 0.1213 | 65.12%
230-220 Infiltration | 0.658 | 0.61968 | 0.694 | 0.6564 | 0.689 | 0.72555 | 0.61968 | 0.72555 | 0.67377 | 15.71%
240-220 Internal Gains | 0.198 | 0.18623 | 0.178 | 0.18145 | 0.18 | 0.18157 | 0.178 | 0.198 | 0.18421 | 10.86%
250-220 Ext Solar Abs. | 1.577 | 1.6815 | 1.711 | 1.6821 | 2.022 | 1.72 | 1.577 | 2.022 | 1.7323 | 25.69%
270-220 South Windows |  | 5.9025 | 4.792 | 5.6543 | 5.601 | 5.6695 | 4.792 | 5.9025 | 5.5239 | 20.1%
280-270 Cavity Albedo |  | -2.2459 | -2.064 | -2.1116 | -1.937 | -2.2376 | -2.2459 | -1.937 | -2.1192 | 14.58%
320-270 Thermostat |  | -0.53772 | -0.528 | -0.62971 | -0.62 | -0.68806 | -0.68806 | -0.528 | -0.6007 | 26.65%
290-270 South Shading |  | -0.13883 | -0.093 | -0.24426 | -0.202 | -0.23557 | -0.24426 | -0.093 | -0.18273 | 82.78%
300-270 E&W Windows |  | -2.8478 | -2.137 | -2.3633 | -2.392 | -2.3592 | -2.8478 | -2.137 | -2.4199 | 29.38%
310-300 E&W Shading |  | -0.36725 | -0.443 | -0.50594 | -0.603 | -0.57679 | -0.603 | -0.36725 | -0.4992 | 47.23%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 5
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-9. Low Mass In-Depth (Cases 395 thru 440) Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 1.341 | 1.6808 | 1.902 | 1.7066 | 1.7443 | 1.8611 | 1.341 | 1.902 | 1.706 | 32.88%
410-400 Infiltration | 1.724 | 1.5093 | 1.614 | 1.7325 | 1.6022 | 1.6757 | 1.5093 | 1.7325 | 1.643 | 13.59%
420-410 Internal Gains | -1.231 | -1.2106 | -1.228 | -1.1745 | -1.1852 | -1.2086 | -1.231 | -1.1745 | -1.2063 | 4.681%
430-420 Ext Solar Abs. | -1.228 | -1.3804 | -1.479 | -1.2857 | -1.4821 | -1.3858 | -1.4821 | -1.228 | -1.3735 | 18.5%
600-430 South Windows | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | -1.907 | -1.121 | -1.3858 | 56.72%
440-600 Cavity Albedo |  | 0.16318 | 0.283 | 0.17569 | 0.1419 | 0.21713 | 0.1419 | 0.283 | 0.19618 | 71.92%
450-600 Const Int&Ext Surf Coefs | -0.307 | -0.0023157 | -0.672 | -0.3619 | -0.5117 | -0.63264 | -0.672 | -0.0023157 | -0.41459 | 161.5%
460-600 Const Int Surf Coefs | -0.222 | 0.062755 | -0.174 | -0.13062 | -0.0995 | -0.21378 | -0.222 | 0.062755 | -0.12952 | 219.8%
460-450 Auto Ext Surf Heat Transf | 0.085 | 0.065071 | 0.498 | 0.23127 | 0.4122 | 0.41886 | 0.065071 | 0.498 | 0.28507 | 151.9%
470-600 Const Ext Surf Coefs | -0.008 | -0.093264 | -0.507 | -0.23051 | -0.4023 | -0.42893 | -0.507 | -0.008 | -0.27833 | 179.3%
470-450 Auto Int Surf Heat Transf | 0.299 | -0.090948 | 0.165 | 0.13138 | 0.1094 | 0.20371 | -0.090948 | 0.299 | 0.13626 | 286.2%
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 0.042 | 0.015542 | 0.011 | 0.020185 | 0.0189 | 0.0091667 | 0.0091667 | 0.042 | 0.019466 | 168.7%
410-400 Infiltration | 0.033 | 0.025188 | 0.024 | 0.026703 | 0.0279 | 0.022437 | 0.022437 | 0.033 | 0.026538 | 39.8%
420-410 Internal Gains | 0.132 | 0.092126 | 0.078 | 0.095302 | 0.0896 | 0.074316 | 0.074316 | 0.132 | 0.093557 | 61.66%
430-420 Ext Solar Abs. | 0.856 | 0.76554 | 0.825 | 0.70305 | 0.8108 | 0.62959 | 0.62959 | 0.856 | 0.765 | 29.6%
600-430 South Windows | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | 4.488 | 5.2091 | 4.9423 | 14.59%
440-600 Cavity Albedo |  | -1.9278 | -1.974 | -1.942 | -1.7477 | -2.0384 | -2.0384 | -1.7477 | -1.926 | 15.09%
450-600 Const Int&Ext Surf Coefs | 0.35 | -0.22415 | 0.729 | 0.48022 | 0.4514 | 0.75118 | -0.22415 | 0.75118 | 0.42294 | 230.6%
460-600 Const Int Surf Coefs | 0.438 | 0.026684 | 0.497 | 0.44757 | 0.5673 | 0.46383 | 0.026684 | 0.5673 | 0.40673 | 132.9%
460-450 Auto Ext Surf Heat Transf | 0.088 | 0.25083 | -0.232 | -0.03265 | 0.1159 | -0.28735 | -0.28735 | 0.25083 | -0.016211 | 3320%
470-600 Const Ext Surf Coefs | 0.165 | -0.26923 | 0.217 | 0.0023448 | -0.1564 | 0.27637 | -0.26923 | 0.27637 | 0.039181 | 1393%
470-450 Auto Int Surf Heat Transf | -0.185 | -0.045084 | -0.512 | -0.47787 | -0.6078 | -0.47481 | -0.6078 | -0.045084 | -0.38376 | 146.6%
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 0.611 | 0.68193 | 0.778 | 0.74028 | 0.698 | 0.71723 | 0.611 | 0.778 | 0.70441 | 23.71%
410-400 Infiltration | 0.779 | 0.60131 | 0.68 | 0.81203 | 0.685 | 0.71836 | 0.60131 | 0.81203 | 0.71262 | 29.57%
420-410 Internal Gains | -0.2 | -0.18445 | -0.178 | -0.18492 | -0.183 | -0.18548 | -0.2 | -0.178 | -0.18597 | 11.83%
430-420 Ext Solar Abs. | 0.162 | -0.002354 | -0.005 | -0.002869 | -0.005 | -0.0026383 | -0.005 | 0.162 | 0.024023 | 695.2%
600-430 South Windows | -0.045 | -0.23365 | -0.325 | -0.11183 | -0.057 | -0.049923 | -0.325 | -0.045 | -0.13707 | 204.3%
440-600 Cavity Albedo |  | 0.006973 | 0.025 | 0.014228 | 0.009 | 0.015399 | 0.006973 | 0.025 | 0.01412 | 127.7%
450-600 Const Int&Ext Surf Coefs | -0.266 | -0.041917 | -0.282 | -0.10461 | -0.186 | -0.32158 | -0.32158 | -0.041917 | -0.20035 | 139.6% |  | 0 | -0.26723 | -0.25907 | -0.20035 | 0.009879 | 41
460-600 Const Int Surf Coefs | -0.2 | -0.04888 | -0.055 | -0.11337 | -0.127 | -0.19922 | -0.2 | -0.04888 | -0.12391 | 122% |  | 0 | -0.04888 | -0.19922 | -0.12391 | -0.044829 | 42
460-450 Auto Ext Surf Heat Transf | 0.066 | -0.006963 | 0.227 | -0.0087666 | 0.059 | 0.12236 | -0.0087666 | 0.227 | 0.076438 | 308.4% |  | 0 | 0.21835 | 0.059851 | 0.076438 | -0.054708 | 1
470-600 Const Ext Surf Coefs | -0.137 | -0.019557 | -0.228 | 0.0023118 | -0.059 | -0.1274 | -0.228 | 0.0023118 | -0.094774 | 243% |  | 0 | -0.21323 | -0.1274 | -0.094774 | 0.031052 | 43
470-450 Auto Int Surf Heat Transf | 0.129 | 0.02236 | 0.054 | 0.10692 | 0.127 | 0.19418 | 0.02236 | 0.19418 | 0.10558 | 162.7% |  | 0 | 0.054 | 0.13167 | 0.10558 | 0.021173 | 2
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
400-395 Surf. Conv. & IR | 0.251 | 0.13615 | 0.149 | 0.22943 | 0.162 | 0.10678 | 0.10678 | 0.251 | 0.17239 | 83.66%
410-400 Infiltration | 0.213 | 0.20623 | 0.252 | 0.22094 | 0.168 | 0.2317 | 0.168 | 0.252 | 0.21531 | 39.01%
420-410 Internal Gains | 0.197 | 0.20865 | 0.208 | 0.20469 | 0.212 | 0.21039 | 0.197 | 0.212 | 0.20679 | 7.254%
430-420 Ext Solar Abs. | 0.959 | 0.93129 | 0.923 | 0.89683 | 1.038 | 0.89001 | 0.89001 | 1.038 | 0.93969 | 15.75%
600-430 South Windows | 3.483 | 4.6412 | 3.582 | 4.4222 | 4.319 | 4.3417 | 3.483 | 4.6412 | 4.1315 | 28.03%
440-600 Cavity Albedo |  | -1.8155 | -1.656 | -1.6656 | -1.514 | -1.7382 | -1.8155 | -1.514 | -1.6778 | 17.97%
450-600 Const Int&Ext Surf Coefs | 0.162 | -0.30121 | 0.641 | 0.11476 | 0.308 | 0.26769 | -0.30121 | 0.641 | 0.19871 | 474.2% |  | 0 | 0.39 | 0.020008 | 0.19871 | -0.065073
460-600 Const Int Surf Coefs | 0.154 | -0.23813 | 0.48 | 0.0226 | 0.111 | 0.023202 | -0.23813 | 0.48 | 0.092113 | 779.6% |  | 0 | 0.382 | -0.10682 | 0.092113 | -0.082573
460-450 Auto Ext Surf Heat Transf | -0.008 | 0.063083 | -0.161 | -0.09216 | -0.197 | -0.24449 | -0.24449 | 0.063083 | -0.10659 | 288.5% |  | 0 | -0.008 | -0.12683 | -0.10659 | -0.0175
470-600 Const Ext Surf Coefs | 0.045 | -0.093327 | 0.148 | 0.092071 | 0.214 | 0.27425 | -0.093327 | 0.27425 | 0.11333 | 324.3% |  | 0 | 0.148 | -0.037353 | 0.11333 | -0.033448
470-450 Auto Int Surf Heat Transf | -0.117 | 0.20788 | -0.493 | -0.022689 | -0.094 | 0.0065584 | -0.493 | 0.20788 | -0.085375 | 821% |  | 0 | -0.242 | -0.057361 | -0.085375 | 0.031625
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-10. High Mass Basic and In-Depth Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.03 | -0.54834 | -0.551 | -0.50457 | -0.5651 | -0.48107 | -0.5651 | -0.03 | -0.44668 | 119.8%
900-800 Himass, S. Win. | -3.415 | -3.5268 | -3.812 | -3.4519 | -3.3951 | -3.5554 | -3.812 | -3.3951 | -3.526 | 11.82%
900-810 Himass, Int. Sol. Abs. |  | -0.65862 | -0.863 | -0.67814 | -0.6003 | -0.79572 | -0.863 | -0.6003 | -0.71916 | 36.53%
910-610 Mass, w/ S. Shade | -2 | -2.4187 | -2.284 | -2.4191 | -2.4598 | -2.4603 | -2.4603 | -2 | -2.3403 | 19.67%
920-620 Mass, w/ E&W Win. | -0.87 | -1.1375 | -1.038 | -1.1486 | -1.2146 | -1.1123 | -1.2146 | -0.87 | -1.0868 | 31.71%
930-630 Mass w/ E&W Shade | -0.653 | -0.8323 | -0.744 | -0.78974 | -0.773 | -0.75448 | -0.8323 | -0.653 | -0.75775 | 23.66%
940-640 Mass, w/ Htg. Setback | -1.293 | -1.54 | -1.47 | -1.5945 | -1.6397 | -1.4836 | -1.6397 | -1.293 | -1.5035 | 23.06%
980-680 Mass, w/ Insulation 20/27 | -1.499 | -1.5403 | -1.466 | -1.7687 | -1.781 | -1.8358 | -1.8358 | -1.466 | -1.6485 | 22.43%
985-685 Mass, w/ 20/20 Tstat | -1.731 | -2.4542 | -2.367 | -2.5078 | -2.6202 | -2.5058 | -2.6202 | -1.731 | -2.3643 | 37.61%
995-695 Mass, w/ Insulation 20/20 | -1.379 | -1.6601 | -1.615 | -1.7954 | -1.8273 | -1.8147 | -1.8273 | -1.379 | -1.6819 | 26.65%
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.611 | -0.52633 | -0.582 | -0.48209 | -0.5613 | -0.45694 | -0.611 | -0.45694 | -0.53661 | 28.71%
900-800 Himass, S. Win. | 2.241 | 2.084 | 2.021 | 2.1152 | 2.0963 | 1.985 | 1.985 | 2.241 | 2.0904 | 12.24%
900-810 Himass, Int. Sol. Abs. |  | 0.98312 | 1.026 | 0.98095 | 0.8821 | 0.97261 | 0.8821 | 1.026 | 0.96896 | 14.85%
910-610 Mass, w/ S. Shade | -2.815 | -2.9669 | -2.683 | -2.9493 | -2.9496 | -2.9259 | -2.9669 | -2.683 | -2.8816 | 9.853%
920-620 Mass, w/ E&W Win. | -1.276 | -1.2901 | -1.203 | -1.3287 | -1.4313 | -1.2918 | -1.4313 | -1.203 | -1.3035 | 17.51%
930-630 Mass w/ E&W Shade | -0.913 | -0.94541 | -0.879 | -0.91693 | -0.9415 | -0.90111 | -0.94541 | -0.879 | -0.91616 | 7.249%
940-640 Mass, w/ Htg. Setback | -3.191 | -3.2473 | -2.894 | -3.3387 | -3.465 | -3.2738 | -3.465 | -2.894 | -3.235 | 17.65%
950-650 Mass, w/ Night Vent | -4.043 | -4.0559 | -3.568 | -4.1099 | -4.2891 | -3.9907 | -4.2891 | -3.568 | -4.0094 | 17.99%
980-680 Mass, w/ Insulation 20/27 | -2.437 | -2.4346 | -2.174 | -2.7321 | -2.7549 | -2.7912 | -2.7912 | -2.174 | -2.554 | 24.17%
985-685 Mass, w/ 20/20 Tstat | -1.857 | -2.6256 | -2.358 | -2.7596 | -2.8721 | -2.7378 | -2.8721 | -1.857 | -2.535 | 40.04%
995-695 Mass, w/ Insulation 20/20 | -1.273 | -1.772 | -1.615 | -1.9687 | -2.0002 | -1.9753 | -2.0002 | -1.273 | -1.7674 | 41.15%
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.343 | -0.47625 | -0.496 | -0.3926 | -0.445 | -0.44187 | -0.496 | -0.343 | -0.43245 | 35.38%
900-800 Himass, S. Win. | -0.406 | -0.33425 | -0.411 | -0.23616 | -0.207 | -0.18847 | -0.411 | -0.18847 | -0.29715 | 74.89%
900-810 Himass, Int. Sol. Abs. |  | -0.056746 | -0.059 | -0.061545 | -0.062 | -0.066177 | -0.066177 | -0.056746 | -0.061094 | 15.44%
910-610 Mass, w/ S. Shade | -0.405 | -0.55173 | -0.565 | -0.49292 | -0.549 | -0.56031 | -0.565 | -0.405 | -0.52066 | 30.73%
920-620 Mass, w/ E&W Win. | -0.25 | -0.52543 | -0.555 | -0.45894 | -0.547 | -0.52032 | -0.555 | -0.25 | -0.47612 | 64.06%
930-630 Mass w/ E&W Shade | -0.284 | -0.5024 | -0.523 | -0.42166 | -0.494 | -0.48714 | -0.523 | -0.284 | -0.45203 | 52.87%
940-640 Mass, w/ Htg. Setback | -0.751 | -1.1705 | -0.999 | -1.4158 | -0.979 | -0.63372 | -1.4158 | -0.63372 | -0.9915 | 78.87%
980-680 Mass, w/ Insulation 20/27 | -0.433 | -0.52385 | -0.429 | -0.51458 | -0.549 | -0.52258 | -0.549 | -0.429 | -0.49534 | 24.23% |  | -1 | -0.52385 | -0.433 | -0.49534 | 0.11946
985-685 Mass, w/ 20/20 Tstat | -0.415 | -0.57969 | -0.596 | -0.52772 | -0.605 | -0.58899 | -0.605 | -0.415 | -0.55207 | 34.42% |  | 5 | -0.57969 | -0.58899 | -0.55207 | 0.019048
995-695 Mass, w/ Insulation 20/20 | -0.427 | -0.42577 | -0.393 | -0.44966 | -0.465 | -0.45573 | -0.465 | -0.393 | -0.43603 | 16.51% |  | -2 | -0.42577 | -0.427 | -0.43603 | 0.046956
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
CASES | [6 empty] | Min | Max | Mean | Mean** (%)
800-430 Mass, w/ High Cond. Wall | -0.881 | -0.73794 | -0.683 | -0.88353 | -0.822 | -0.76849 | -0.88353 | -0.683 | -0.79599 | 25.19%
900-800 Himass, S. Win. | 1.753 | 2.2746 | 1.399 | 1.9946 | 1.844 | 2.0045 | 1.399 | 2.2746 | 1.8783 | 46.62%
900-810 Himass, Int. Sol. Abs. |  | 0.96595 | 0.616 | 0.77023 | 0.717 | 0.8272 | 0.616 | 0.96595 | 0.77927 | 44.91%
910-610 Mass, w/ S. Shade | -2.973 | -3.7101 | -3.228 | -3.9124 | -3.722 | -3.7868 | -3.9124 | -2.973 | -3.5554 | 26.42%
920-620 Mass, w/ E&W Win. | -1.223 | -1.4361 | -1.245 | -1.5371 | -1.523 | -1.4341 | -1.5371 | -1.223 | -1.3997 | 22.44%
930-630 Mass w/ E&W Shade | -1.069 | -1.3365 | -1.191 | -1.4307 | -1.477 | -1.3363 | -1.477 | -1.069 | -1.3067 | 31.22%
940-640 Mass, w/ Htg. Setback | -2.492 | -3.0526 | -2.809 | -3.2574 | -3.236 | -3.0295 | -3.2574 | -2.492 | -2.9794 | 25.69%
950-650 Mass, w/ Night Vent | -3.282 | -3.9262 | -2.991 | -3.7506 | -3.759 | -3.5611 | -3.9262 | -2.991 | -3.545 | 26.38%
980-680 Mass, w/ Insulation 20/27 | -2.377 | -3.3833 | -2.931 | -3.3201 | -3.335 | -3.244 | -3.3833 | -2.377 | -3.0984 | 32.48% |  | 0 | -2.831 | -3.3833 | -3.0984 | 0.020291
985-685 Mass, w/ 20/20 Tstat | -2.341 | -2.9342 | -2.863 | -3.192 | -3.198 | -2.9827 | -3.198 | -2.341 | -2.9185 | 29.36% |  | 0 | -2.863 | -2.9342 | -2.9185 | 0.10458
995-695 Mass, w/ Insulation 20/20 | -2.103 | -3.3169 | -3.04 | -3.1569 | -3.285 | -3.0602 | -3.3169 | -2.103 | -2.9937 | 40.55% |  | 1 | -2.917 | -3.3169 | -2.9937 | 0.040497
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 6
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-11. Annual Transmissivity Coefficient of Windows
(ANNUAL UNSHADED TRANSMITTED SOLAR RADIATION)/(ANNUAL UNSHADED INCIDENT SOLAR RADIATION)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
600 South | 0.5912 | 0.62686 | 0.62378 | 0.58667 | 0.59708 | 0.59426 | 0.58667 | 0.62686 | 0.60331 | 6.661%
620 West | 0.5998 |  | 0.62866 | 0.6007 | 0.61578 | 0.64014 | 0.5998 | 0.64014 | 0.61702 | 6.538%
660 South, Low-E | 0.32228 | 0.38067 | 0.39243 | 0.31813 | 0.32477 | 0.324 | 0.31813 | 0.39243 | 0.34371 | 21.61%
670 South, Single-Pane | 0.74766 | 0.7501 | 0.77043 | 0.74733 | 0.75442 | 0.75076 | 0.74733 | 0.77043 | 0.75345 | 3.067%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-12. Annual Shading Coefficient of Window Shading Devices: Overhangs & Fins
(1-(ANNUAL SHADED TRANSMITTED SOLAR RADIATION)/(ANNUAL UNSHADED TRANSMITTED SOLAR RADIATION))
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
610/600 South | 0.21829 | 0.19413 | 0.17602 | 0.19637 | 0.2243 | 0.19545 | 0.17602 | 0.2243 | 0.20076 | 24.05%
630/620 West | 0.26756 |  | 0.29895 | 0.27827 | 0.34164 | 0.28575 | 0.26756 | 0.34164 | 0.29443 | 25.16%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-13. Case 600 Annual Incident Solar Radiation (kWh/m2)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
Horizontal | 1670 | 1662.5278 | 1667.158 | 1664.3425 | 1665.18 | 1668.98 | 1662.5278 | 1670 | 1666.3647 | 0.4484% |  | 0
North | 453 | 399.0475 | 477.31 | 438.241 | 432.12 | 440.165 | 399.0475 | 477.31 | 439.9806 | 17.79% |  | 1
East | 1061 | 1026.9874 | 1016.676 | 1062.1572 | 1054.24 | 1067.94 | 1016.676 | 1067.94 | 1048.1668 | 4.891% |  | 2
South | 1387 | 1316.9162 | 1290.593 | 1370.4819 | 1363.1 | 1384.23 | 1290.593 | 1387 | 1352.0535 | 7.13% |  | 3
West | 997 | 903.0665 | 905.722 | 967.278 | 961.18 | 974.473 | 903.0665 | 997 | 951.4533 | 9.873% |  | 4
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-14. Annual Transmitted Solar Radiation - Unshaded (kWh/m2)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
600 South | 820 | 825.5194 | 805.046 | 804.0205 | 813.88 | 822.589 | 804.0205 | 825.5194 | 815.1758 | 2.637%
620 West | 598 |  | 569.394 | 581.0395 | 591.88 | 623.797 | 569.394 | 623.797 | 592.8221 | 9.177%
660 South | 447 | 501.3136 | 506.461 | 435.995 | 442.7 | 448.493 | 435.995 | 506.461 | 463.6604 | 15.2%
670 South | 1037 | 987.8182 | 994.318 | 1024.2026 | 1028.35 | 1039.23 | 987.8182 | 1039.23 | 1018.4865 | 5.048%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-15. Annual Transmitted Solar Radiation - Shaded (kWh/m2)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
(Max-Min)/
Case | [6 empty] | Min | Max | Mean | Mean* (%)
610 South | 641 | 665.2609 | 663.345 | 646.1319 | 631.33 | 661.81 | 631.33 | 665.2609 | 651.4796 | 5.208%
630 West | 438 |  | 399.173 | 419.3545 | 389.67 | 445.549 | 389.67 | 445.549 | 418.3493 | 13.36%
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 7
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-16. Sky Temperature Output, Case 600
MAXIMUM ANNUAL HOURLY INTEGRATED SKY TEMPERATURE
Simulation Model: | BSIMAC |  |  |  | CSE |  |  |  | DeST |  |  |  | EnergyPlus |  |  |  | ESP-r |  |  |  | TRNSYS |  |  |  | TestSpec-Alt |  |  |  | Example Result Statistics |  |  |  |  | Tested Prg
[25 empty] | Alternative Values |  |  |  | Min | Max | Mean | (Max-Min)/
Case | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | Mo. | Day | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Mo. | Day | Hr
Average Annual Hourly Integrated |  |  |  |  | -3.9307 |  |  |  | -5.9 |  |  |  | -2.0216 |  |  |  | -5.17 |  |  |  | -5.0587 |  |  |  | -5.9 |  |  |  | -5.9 | -2.0216 | -4.6635 | 83.16% |  |  |  |  | 0 | 0
Minimum Annual Hourly Integrated |  |  |  |  | -46.2246 | Dec | 31 | 24 | -46.85 | Dec | 31 | 23 | -37.9798 | Dec | 31 | 24 | -46.9 | Dec | 31 | 23 | -46.1617 | Dec | 31 | 24 | -46.85 |  |  |  | -46.9 | -37.9798 | -45.161 | 19.75%
Maximum Annual Hourly Integrated |  |  |  |  | 30.0812 | Jun | 13 | 15 | 24.62 | Aug | 4 | 15 | 24.7268 | Aug | 4 | 16 | 26.7 | Aug | 4 | 15 | 26.0293 | Jun | 13 | 18 | 24.62 |  |  |  | 24.62 | 30.0812 | 26.1296 | 20.9%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables M1
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-M1. Monthly Heating Loads (kWh) | [12 empty] | Annual Sums Check (kWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0
[7 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | [9 empty] | Mean** (%) |  |  | 600 Heating
Jan | 663.99 | 655.585 | 672.684 | 711.8797 | 732 | 734.943 | 655.585 | 734.943 | 695.1803 | 11.42% |  | 0 | 4049.581 | 3992.755 | 4048.646 | 4324.3743 | 4364 | 4503.5533 | #REF! | #REF!
Feb | 653.26 | 626.2627 | 635.299 | 682.632 | 682 | 702.079 | 626.2627 | 702.079 | 663.5888 | 11.43% |  | 1
Mar | 433.508 | 435.7419 | 450.494 | 472.2167 | 481 | 495.001 | 433.508 | 495.001 | 461.3269 | 13.33% |  | 2
Apr | 511.036 | 456.9543 | 447.957 | 510.1244 | 479 | 517.287 | 447.957 | 517.287 | 487.0598 | 14.23% |  | 3
May | 112.769 | 127.7958 | 128 | 136.8192 | 139 | 150.732 | 112.769 | 150.732 | 132.5193 | 28.65% |  | 4
Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512 | 2.735 | 15.9512 | 10.9476 | 120.7% |  | 5
Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263 | 4.839 | 16.7263 | 11.5386 | 103% |  | 6
Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039 | 1.368 | 9.6039 | 6.9757 | 118.1% |  | 7
Sep | 51.756 | 74.3067 | 76.741 | 73.317 | 81 | 84.8239 | 51.756 | 84.8239 | 73.6574 | 44.89% |  | 8
Oct | 316.952 | 328.4088 | 324.148 | 347.7084 | 354 | 367.051 | 316.952 | 367.051 | 339.7114 | 14.75% |  | 9
Nov | 598.664 | 575.553 | 585.805 | 625.2596 | 629 | 645.809 | 575.553 | 645.809 | 610.0151 | 11.52% |  | 10
Dec | 698.704 | 681.9851 | 697.819 | 735.7303 | 750 | 763.546 | 681.9851 | 763.546 | 721.2974 | 11.31% |  | 11
Case 900 | [12 empty] | 900 Heating
Jan | 277.8 | 206.1043 | 275.307 | 255.8355 | 266 | 291.936 | 206.1043 | 291.936 | 262.1638 | 32.74% |  |  | 1726 | 1378.8913 | 1590.894 | 1663.6867 | 1585 | 1814.0316 | #REF! | #REF!
Feb | 307.4 | 243.2297 | 292.916 | 294.1814 | 283 | 322.141 | 243.2297 | 322.141 | 290.478 | 27.17%
Mar | 134.4 | 102.4399 | 119.976 | 125.5424 | 115 | 143.84 | 102.4399 | 143.84 | 123.5331 | 33.51%
Apr | 275.7 | 222.3692 | 214.166 | 268.6543 | 228 | 275.466 | 214.166 | 275.7 | 247.3926 | 24.87%
May | 20.1 | 33.3469 | 26.771 | 33.4139 | 29 | 37.5028 | 20.1 | 37.5028 | 30.0224 | 57.97%
Jun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
Jul | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
Aug | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
Sep | 2.1 | 0 | 0 | 0.11241 | 0 | 0.53697 | 0 | 2.1 | 0.45823 | 458.3%
Oct | 80.5 | 65.0694 | 63.591 | 81.0905 | 70 | 85.0098 | 63.591 | 85.0098 | 74.2101 | 28.86%
Nov | 298.2 | 251.5988 | 283.888 | 296.9874 | 286 | 318.242 | 251.5988 | 318.242 | 289.1527 | 23.05%
Dec | 329.8 | 254.733 | 314.279 | 307.8688 | 308 | 339.357 | 254.733 | 339.357 | 309.0063 | 27.39%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-M2. Monthly Sensible Cooling Loads (kWh)
Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | Statistics for Example Results |  |  |  | Tested Prg
[7 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | [9 empty] | Mean** (%) |  |  | 600 Cooling
Jan | 475.4 | 554.0235 | 417.93 | 521.798 | 523 | 495.012 | 417.93 | 554.0235 | 497.8606 | 27.34% |  | 0 | 5822 | 5913.1242 | 5432.086 | 6027.0394 | 6161 | 5779.524 | #REF! | #REF!
Feb | 349.2 | 394.2972 | 315.415 | 387.4981 | 398 | 367.404 | 315.415 | 398 | 368.6357 | 22.4% |  | 1
Mar | 450.3 | 474.3508 | 410.736 | 484.3611 | 489 | 457.384 | 410.736 | 489 | 461.022 | 16.98% |  | 2
Apr | 218.7 | 220.1356 | 230.168 | 240.4611 | 263 | 235.357 | 218.7 | 263 | 234.6369 | 18.88% |  | 3
May | 342.7 | 321.1602 | 338.582 | 339.9139 | 364 | 325.154 | 321.1602 | 364 | 338.585 | 12.65% |  | 4
Jun | 578.3 | 497.4498 | 526.439 | 539.605 | 550 | 516.057 | 497.4498 | 578.3 | 534.6418 | 15.12% |  | 5
Jul | 568.4 | 505.8671 | 525.149 | 536.3834 | 556 | 514.389 | 505.8671 | 568.4 | 534.3648 | 11.7% |  | 6
Aug | 658.2 | 606.5032 | 621.101 | 648.5013 | 674 | 634.136 | 606.5032 | 674 | 640.4069 | 10.54% |  | 7
Sep | 724.8 | 705.1929 | 672.084 | 733.708 | 743 | 710.474 | 672.084 | 743 | 714.8765 | 9.92% |  | 8
Oct | 628.4 | 676.133 | 611.126 | 675.2687 | 681 | 649.483 | 611.126 | 681 | 653.5685 | 10.69% |  | 9
Nov | 394.3 | 454.7409 | 377.147 | 437.6814 | 444 | 418.571 | 377.147 | 454.7409 | 421.0734 | 18.43% |  | 10
Dec | 433.3 | 503.27 | 386.209 | 481.8594 | 476 | 456.103 | 386.209 | 503.27 | 456.1236 | 25.66% |  | 11
Case 900 | [12 empty] | 900 Cooling
Jan | 73.3141 | 67.8041 | 33.493 | 53.2805 | 42 | 44.635 | 33.493 | 73.3141 | 52.4211 | 75.96% |  |  | 2714 | 2463.8258 | 2382.684 | 2488.7414 | 2485 | 2267.1274 | #REF! | #REF!
Feb | 24.0087 | 15.1117 | 4.724 | 12.3391 | 11 | 9.2434 | 4.724 | 24.0087 | 12.7378 | 151.4%
Mar | 86.3882 | 68.5488 | 40.898 | 65.3862 | 56 | 50.5508 | 40.898 | 86.3882 | 61.2953 | 74.21%
Apr | 29.344 | 12.3134 | 18.267 | 18.4694 | 22 | 16.0525 | 12.3134 | 29.344 | 19.4077 | 87.75%
May | 131.0941 | 117.8126 | 128.592 | 114.4874 | 125 | 98.3549 | 98.3549 | 131.0941 | 119.2235 | 27.46%
Jun | 447.4956 | 372.2992 | 408.473 | 401.3344 | 404 | 365.819 | 365.819 | 447.4956 | 399.9035 | 20.42%
Jul | 440.8962 | 380.4363 | 408.145 | 398.7064 | 410 | 365.513 | 365.513 | 440.8962 | 400.6161 | 18.82%
Aug | 532.6434 | 485.6761 | 510.152 | 510.3174 | 531 | 487.566 | 485.6761 | 532.6434 | 509.5592 | 9.217%
Sep | 517.8661 | 484.0294 | 466.106 | 492.837 | 492 | 458.859 | 458.859 | 517.8661 | 485.2829 | 12.16%
Oct | 296.188 | 305.5693 | 269.566 | 292.6655 | 281 | 260.853 | 260.853 | 305.5693 | 284.307 | 15.73%
Nov | 72.6701 | 80.4854 | 56.214 | 67.9828 | 63 | 60.1796 | 56.214 | 80.4854 | 66.7553 | 36.36%
Dec | 62.0916 | 73.7394 | 38.054 | 60.9353 | 48 | 49.5012 | 38.054 | 73.7394 | 55.3869 | 64.43%
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables M2
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-M3. Monthly Hourly Integrated Peak Heating Loads | [26 empty] | Annual Peaks Check (kWh)
Simulation Model: | BSIMAC |  |  | CSE |  |  | DeST |  |  | EnergyPlus |  |  | ESP-r |  |  | TRNSYS |  |  | Example Result Statistics |  |  |  |  | Tested Prg |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0
[19 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | kW | kW | Mean** (%) | kW | Day | Hr |  | 600 Heating
Jan | 3.1 | 29 | 7 | 3.0202 | 1 | 1 | 3.036 | 1 | 0 | 2.9776 | 1 | 3 | 3.23 | 1 | 1 | 3.3589 | 1 | 1 | 2.9776 | 3.3589 | 3.1204 | 12.22% |  |  |  | 0 | 3.255 | 3.0202 | 3.036 | 3.2044 | 3.23 | 3.3589 | #REF! | #REF!
Feb | 3.041 | 9 | 7 | 2.8997 | 9 | 6 | 2.922 | 9 | 5 | 3.0666 | 9 | 6 | 3.14 | 9 | 6 | 3.2252 | 9 | 6 | 2.8997 | 3.2252 | 3.0491 | 10.68% |  |  |  | 1
Mar | 2.275 | 2 | 7 | 2.0344 | 17 | 6 | 2.065 | 17 | 5 | 2.1146 | 17 | 6 | 2.23 | 17 | 6 | 2.287 | 17 | 6 | 2.0344 | 2.287 | 2.1677 | 11.65% |  |  |  | 2
Apr | 2.446 | 3 | 6 | 2.2073 | 11 | 6 | 2.238 | 11 | 5 | 2.3223 | 11 | 5 | 2.38 | 11 | 6 | 2.4572 | 11 | 6 | 2.2073 | 2.4572 | 2.3418 | 10.67% |  |  |  | 3
May | 1.645 | 3 | 5 | 1.5922 | 1 | 5 | 1.569 | 1 | 4 | 1.6241 | 1 | 5 | 1.75 | 1 | 5 | 1.778 | 1 | 5 | 1.569 | 1.778 | 1.6597 | 12.59% |  |  |  | 4
Jun | 0.805 | 9 | 5 | 0.77848 | 9 | 5 | 0.748 | 9 | 4 | 0.73243 | 9 | 5 | 0.76 | 10 | 5 | 0.8526 | 9 | 5 | 0.73243 | 0.8526 | 0.77942 | 15.42% |  |  |  | 5
Jul | 0.599 | 25 | 6 | 0.53975 | 26 | 5 | 0.512 | 26 | 4 | 0.51445 | 26 | 5 | 0.57 | 26 | 5 | 0.61893 | 26 | 5 | 0.512 | 0.61893 | 0.55902 | 19.13% |  |  |  | 6
Aug | 0.572 | 10 | 7 | 0.55338 | 17 | 6 | 0.532 | 17 | 5 | 0.47852 | 17 | 6 | 0.56 | 17 | 6 | 0.59085 | 17 | 6 | 0.47852 | 0.59085 | 0.54779 | 20.5% |  |  |  | 7
Sep | 1.229 | 28 | 24 | 1.1204 | 29 | 1 | 1.114 | 29 | 2 | 1.1295 | 28 | 24 | 1.19 | 29 | 1 | 1.2116 | 28 | 24 | 1.114 | 1.229 | 1.1657 | 9.865% |  |  |  | 8
Oct | 1.702 | 6 | 7 | 1.6237 | 15 | 6 | 1.619 | 9 | 5 | 1.682 | 15 | 5 | 1.77 | 9 | 6 | 1.8132 | 15 | 6 | 1.619 | 1.8132 | 1.7017 | 11.41% |  |  |  | 9
Nov | 3.255 | 26 | 8 | 2.8502 | 26 | 8 | 2.931 | 26 | 7 | 3.1061 | 26 | 7 | 3.11 | 26 | 7 | 3.2066 | 26 | 8 | 2.8502 | 3.255 | 3.0765 | 13.16% |  |  |  | 10
Dec | 3.171 | 31 | 24 | 2.9413 | 31 | 24 | 2.972 | 31 | 23 | 3.2044 | 31 | 24 | 3.17 | 31 | 24 | 3.2781 | 31 | 24 | 2.9413 | 3.2781 | 3.1228 | 10.79% |  |  |  | 11
Case 900 | [26 empty] | 900 Heating
Jan | 2.322 | 7 | 7 | 2.0774 | 1 | 5 | 2.178 | 1 | 4 | 1.9028 | 29 | 7 | 2.2 | 1 | 5 | 2.3786 | 1 | 5 | 1.9028 | 2.3786 | 2.1765 | 21.86% |  |  |  | 0 | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.63 | 2.7785 | #REF! | #REF!
Feb | 2.551 | 8 | 24 | 2.4434 | 9 | 6 | 2.453 | 9 | 5 | 2.6875 | 9 | 6 | 2.63 | 9 | 7 | 2.7785 | 9 | 7 | 2.4434 | 2.7785 | 2.5906 | 12.93% |  |  |  | 1
Mar | 1.774 | 16 | 7 | 1.6129 | 17 | 6 | 1.646 | 17 | 5 | 1.7443 | 17 | 6 | 1.76 | 17 | 7 | 1.8582 | 17 | 6 | 1.6129 | 1.8582 | 1.7326 | 14.16% |  |  |  | 2
Apr | 1.997 | 2 | 7 | 1.7706 | 3 | 4 | 1.725 | 3 | 3 | 2.0036 | 3 | 4 | 1.93 | 3 | 4 | 2.0359 | 3 | 4 | 1.725 | 2.0359 | 1.9104 | 16.28% |  |  |  | 3
May | 1.295 | 4 | 6 | 1.1425 | 1 | 5 | 1.124 | 1 | 5 | 1.2682 | 1 | 5 | 1.23 | 1 | 5 | 1.3242 | 1 | 5 | 1.124 | 1.3242 | 1.2307 | 16.27% |  |  |  | 4
Jun | 0 |  |  | 0 | 1 | 1 |  |  |  | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 31 | 0 | 0 | 0 | 0 | ---- |  |  |  | 5
Jul | 0 |  |  | 0 | 1 | 1 |  |  |  | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 31 | 0 | 0 | 0 | 0 | ---- |  |  |  | 6
Aug | 0 |  |  | 0 | 1 | 1 |  |  |  | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 31 | 0 | 0 | 0 | 0 | ---- |  |  |  | 7
Sep | 0.113 | 28 | 6 | 0 | 1 | 1 |  |  |  | 0.064157 | 29 | 7 | 0 | 1 | 1 | 0.19442 | 29 | 7 | 0 | 0.19442 | 0.074315 | 261.6% |  |  |  | 8
Oct | 1.201 | 6 | 7 | 1.1882 | 7 | 7 | 1.158 | 7 | 6 | 1.3258 | 7 | 7 | 1.21 | 7 | 7 | 1.3311 | 7 | 7 | 1.158 | 1.3311 | 1.2357 | 14.01% |  |  |  | 9
Nov | 2.427 | 1 | 7 | 2.0863 | 26 | 8 | 2.201 | 26 | 7 | 2.3161 | 26 | 7 | 2.28 | 26 | 8 | 2.4629 | 26 | 8 | 2.0863 | 2.4629 | 2.2956 | 16.4% |  |  |  | 10
Dec | 2.12 | 31 | 8 | 1.9268 | 31 | 8 | 1.981 | 9 | 6 | 2.1749 | 31 | 7 | 2.04 | 9 | 7 | 2.1801 | 9 | 7 | 1.9268 | 2.1801 | 2.0705 | 12.24% |  |  |  | 11
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-M4. Monthly Hourly Integrated Peak Sensible Cooling Loads
Simulation Model: | BSIMAC |  |  | CSE |  |  | DeST |  |  | EnergyPlus |  |  | ESP-r |  |  | TRNSYS |  |  | Example Result Statistics |  |  |  |  | Tested Prg
[19 empty] | Min | Max | Mean | (Max-Min)/
Case 600 | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | Day | Hr | kW | kW | kW | Mean** (%) | kW | Day | Hr |  | 600 Cooling
Jan | 5.65 | 22 | 15 | 6.481 | 22 | 14 | 5.422 | 22 | 14 | 6.3516 | 22 | 14 | 6.19 | 22 | 14 | 6.0457 | 22 | 14 | 5.422 | 6.481 | 6.0234 | 17.58% |  |  |  | 0 | 5.65 | 6.481 | 5.422 | 6.3516 | 6.19 | 6.0457 | #REF! | #REF!
Feb | 4.9211 | 15 | 15 | 5.3928 | 15 | 14 | 4.444 | 15 | 14 | 5.5373 | 2 | 14 | 5.42 | 2 | 14 | 5.1553 | 2 | 14 | 4.444 | 5.5373 | 5.1451 | 21.25% |  |  |  | 1
Mar | 4.4579 | 24 | 14 | 5.1483 | 24 | 13 | 4.252 | 9 | 14 | 5.0085 | 9 | 14 | 5.04 | 9 | 14 | 4.7399 | 9 | 14 | 4.252 | 5.1483 | 4.7744 | 18.77% |  |  |  | 2
Apr | 3.4735 | 12 | 14 | 4.0151 | 27 | 14 | 3.6 | 7 | 14 | 3.9307 | 12 | 14 | 4.04 | 12 | 14 | 3.8027 | 12 | 14 | 3.4735 | 4.04 | 3.8103 | 14.87% |  |  |  | 3
May | 2.7741 | 10 | 14 | 3.0796 | 21 | 14 | 2.894 | 10 | 14 | 3.0864 | 10 | 13 | 3.1 | 10 | 14 | 3.0405 | 21 | 14 | 2.7741 | 3.1 | 2.9958 | 10.88% |  |  |  | 4
Jun | 3.2526 | 26 | 15 | 3.2488 | 13 | 13 | 3.067 | 14 | 14 | 3.4487 | 13 | 13 | 3.43 | 13 | 14 | 3.3792 | 13 | 13 | 3.067 | 3.4487 | 3.3044 | 11.55% |  |  |  | 5
Jul | 3.3187 | 17 | 14 | 3.2903 | 17 | 14 | 3.155 | 29 | 13 | 3.6284 | 17 | 14 | 3.64 | 17 | 14 | 3.4967 | 17 | 14 | 3.155 | 3.64 | 3.4215 | 14.17% |  |  |  | 6
Aug | 4.1922 | 26 | 14 | 4.1195 | 8 | 14 | 4.038 | 29 | 13 | 4.672 | 26 | 14 | 4.7 | 29 | 14 | 4.6505 | 27 | 13 | 4.038 | 4.7 | 4.3954 | 15.06% |  |  |  | 7
Sep | 5.086 | 30 | 14 | 5.4503 | 2 | 14 | 4.911 | 30 | 13 | 5.7148 | 30 | 13 | 5.58 | 30 | 14 | 5.4199 | 30 | 14 | 4.911 | 5.7148 | 5.3603 | 15% |  |  |  | 8
Oct | 5.5767 | 18 | 14 | 6.2702 | 1 | 13 | 5.278 | 10 | 13 | 6.2221 | 18 | 14 | 6.07 | 18 | 14 | 5.9226 | 18 | 14 | 5.278 | 6.2702 | 5.8899 | 16.85% |  |  |  | 9
Nov | 5.4759 | 28 | 14 | 6.149 | 28 | 13 | 5.229 | 29 | 13 | 6.194 | 28 | 13 | 6.03 | 28 | 14 | 5.824 | 28 | 14 | 5.229 | 6.194 | 5.817 | 16.59% |  |  |  | 10
Dec | 5.537 | 1 | 14 | 6.45 | 1 | 14 | 5.294 | 1 | 13 | 6.251 | 1 | 14 | 6.12 | 1 | 14 | 5.9425 | 1 | 14 | 5.294 | 6.45 | 5.9324 | 19.49% |  |  |  | 11
Case 900 | [26 empty] | 900 Cooling
Jan | 1.982 | 22 | 16 | 2.2416 | 22 | 15 | 1.637 | 22 | 15 | 2.0779 | 22 | 15 | 1.81 | 22 | 16 | 1.8776 | 22 | 15 | 1.637 | 2.2416 | 1.9377 | 31.2% |  |  |  | 0 | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.9 | 2.9401 | #REF! | #REF!
Feb | 1.096 | 15 | 16 | 0.99617 | 15 | 15 | 0.588 | 15 | 15 | 0.97943 | 15 | 15 | 0.85 | 15 | 16 | 0.82938 | 15 | 15 | 0.588 | 1.096 | 0.88983 | 57.09% |  |  |  | 1
Mar | 1.508 | 10 | 15 | 1.4341 | 24 | 15 | 1.143 | 10 | 14 | 1.4931 | 11 | 14 | 1.27 | 10 | 15 | 1.4258 | 11 | 14 | 1.143 | 1.508 | 1.379 | 26.47% |  |  |  | 2
Apr | 1.093 | 7 | 15 | 0.63116 | 19 | 14 | 1.032 | 8 | 14 | 0.95262 | 7 | 15 | 0.95 | 8 | 15 | 0.83719 | 8 | 15 | 0.63116 | 1.093 | 0.916 | 50.42% |  |  |  | 3
May | 1.555 | 11 | 15 | 1.4272 | 21 | 14 | 1.446 | 11 | 14 | 1.5339 | 11 | 14 | 1.46 | 11 | 15 | 1.4645 | 11 | 14 | 1.4272 | 1.555 | 1.4811 | 8.626% |  |  |  | 4
Jun | 2.101 | 26 | 15 | 1.8967 | 14 | 14 | 1.873 | 14 | 14 | 1.9656 | 14 | 14 | 1.89 | 14 | 15 | 1.9742 | 14 | 14 | 1.873 | 2.101 | 1.9501 | 11.69% |  |  |  | 5
Jul | 2.14 | 17 | 15 | 1.943 | 17 | 14 | 1.83 | 17 | 14 | 2.0681 | 17 | 15 | 1.97 | 17 | 15 | 1.975 | 17 | 15 | 1.83 | 2.14 | 1.9877 | 15.6% |  |  |  | 6
Aug | 2.632 | 26 | 15 | 2.4852 | 5 | 14 | 2.212 | 29 | 14 | 2.5258 | 29 | 15 | 2.51 | 29 | 15 | 2.5337 | 29 | 15 | 2.212 | 2.632 | 2.4831 | 16.91% |  |  |  | 7
Sep | 2.961 | 30 | 15 | 3.1368 | 4 | 14 | 2.556 | 11 | 14 | 2.9888 | 11 | 15 | 2.81 | 11 | 15 | 2.8712 | 11 | 15 | 2.556 | 3.1368 | 2.8873 | 20.11% |  |  |  | 8
Oct | 3.039 | 1 | 15 | 3.3764 | 1 | 14 | 2.549 | 12 | 14 | 3.0404 | 1 | 14 | 2.9 | 12 | 15 | 2.9401 | 1 | 14 | 2.549 | 3.3764 | 2.9742 | 27.82% |  |  |  | 9
Nov | 1.982 | 6 | 15 | 2.2328 | 20 | 15 | 1.683 | 20 | 14 | 2.0018 | 20 | 15 | 1.94 | 20 | 15 | 1.9406 | 22 | 14 | 1.683 | 2.2328 | 1.9634 | 28% |  |  |  | 10
Dec | 2.069 | 1 | 15 | 2.1054 | 1 | 15 | 1.595 | 2 | 14 | 1.9682 | 2 | 15 | 1.67 | 2 | 15 | 1.6903 | 2 | 15 | 1.595 | 2.1054 | 1.8497 | 27.59% |  |  |  | 11
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables M3
ASHRAE Standard 140-2020, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-995 & 600FF-980FF
Note: The statistics in the tables below are based on the listed example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-M5. Monthly Load 600-900 Sensitivity Tests
ANNUAL HEATING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 386.19 | 449.4807 | 397.377 | 456.0442 | 466 | 443.007 | 386.19 | 466 | 433.0165 | 18.43%
Feb | 345.86 | 383.033 | 342.383 | 388.4505 | 399 | 379.938 | 342.383 | 399 | 373.1108 | 15.17%
Mar | 299.108 | 333.302 | 330.518 | 346.6743 | 366 | 351.161 | 299.108 | 366 | 337.7939 | 19.8%
Apr | 235.336 | 234.5851 | 233.791 | 241.4701 | 251 | 241.821 | 233.791 | 251 | 239.6672 | 7.18%
May | 92.669 | 94.449 | 101.229 | 103.4052 | 110 | 113.2292 | 92.669 | 113.2292 | 102.4969 | 20.06%
Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512 | 2.735 | 15.9512 | 10.9476 | 120.7%
Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263 | 4.839 | 16.7263 | 11.5386 | 103%
Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039 | 1.368 | 9.6039 | 6.9757 | 118.1%
Sep | 49.656 | 74.3067 | 76.741 | 73.2046 | 81 | 84.2869 | 49.656 | 84.2869 | 73.1992 | 47.31%
Oct | 236.452 | 263.3394 | 260.557 | 266.6179 | 284 | 282.0412 | 236.452 | 284 | 265.5012 | 17.91%
Nov | 300.464 | 323.9542 | 301.917 | 328.2722 | 343 | 327.567 | 300.464 | 343 | 320.8624 | 13.26%
Dec | 368.904 | 427.2521 | 383.54 | 427.8615 | 442 | 424.189 | 368.904 | 442 | 412.2911 | 17.73%
ANNUAL SENSIBLE COOLING [MWh] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 402.0859 | 486.2194 | 384.437 | 468.5175 | 481 | 450.377 | 384.437 | 486.2194 | 445.4395 | 22.85%
Feb | 325.1913 | 379.1855 | 310.691 | 375.159 | 387 | 358.1606 | 310.691 | 387 | 355.8979 | 21.44%
Mar | 363.9118 | 405.8019 | 369.838 | 418.9749 | 433 | 406.8332 | 363.9118 | 433 | 399.7267 | 17.28%
Apr | 189.356 | 207.8222 | 211.901 | 221.9916 | 241 | 219.3045 | 189.356 | 241 | 215.2292 | 23.99%
May | 211.6059 | 203.3476 | 209.99 | 225.4265 | 239 | 226.7991 | 203.3476 | 239 | 219.3615 | 16.25%
Jun | 130.8044 | 125.1506 | 117.966 | 138.2706 | 146 | 150.238 | 117.966 | 150.238 | 134.7383 | 23.95%
Jul | 127.5038 | 125.4308 | 117.004 | 137.6771 | 146 | 148.876 | 117.004 | 148.876 | 133.7486 | 23.83%
Aug | 125.5566 | 120.8271 | 110.949 | 138.1839 | 143 | 146.57 | 110.949 | 146.57 | 130.8478 | 27.22%
Sep | 206.9339 | 221.1635 | 205.978 | 240.871 | 251 | 251.615 | 205.978 | 251.615 | 229.5936 | 19.88%
Oct | 332.212 | 370.5637 | 341.56 | 382.6032 | 400 | 388.63 | 332.212 | 400 | 369.2615 | 18.36%
Nov | 321.6299 | 374.2554 | 320.933 | 369.6986 | 381 | 358.3914 | 320.933 | 381 | 354.318 | 16.95%
Dec | 371.2084 | 429.5306 | 348.155 | 420.9241 | 428 | 406.6018 | 348.155 | 429.5306 | 400.7366 | 20.31%
PEAK HEATING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 0.778 | 0.94282 | 0.858 | 1.0748 | 1.03 | 0.98026 | 0.778 | 1.0748 | 0.94397 | 31.44%
Feb | 0.49 | 0.45628 | 0.469 | 0.37915 | 0.51 | 0.4467 | 0.37915 | 0.51 | 0.45852 | 28.54%
Mar | 0.501 | 0.42158 | 0.419 | 0.37021 | 0.47 | 0.42882 | 0.37021 | 0.501 | 0.4351 | 30.06%
Apr | 0.449 | 0.43669 | 0.513 | 0.31865 | 0.45 | 0.42125 | 0.31865 | 0.513 | 0.43143 | 45.05%
May | 0.35 | 0.44976 | 0.445 | 0.35588 | 0.52 | 0.45382 | 0.35 | 0.52 | 0.42908 | 39.62%
Jun | 0.805 | 0.77848 | 0.748 | 0.73243 | 0.76 | 0.8526 | 0.73243 | 0.8526 | 0.77942 | 15.42%
Jul | 0.599 | 0.53975 | 0.512 | 0.51445 | 0.57 | 0.61893 | 0.512 | 0.61893 | 0.55902 | 19.13%
Aug | 0.572 | 0.55338 | 0.532 | 0.47852 | 0.56 | 0.59085 | 0.47852 | 0.59085 | 0.54779 | 20.5% |  | 0 | -0.40023 | -0.40371 | -0.38216 | 0.01327 | 6
Sep | 1.116 | 1.1204 | 1.114 | 1.0654 | 1.19 | 1.0172 | 1.0172 | 1.19 | 1.1038 | 15.66% |  | 7 | 0.63519 | 0.86207 | 0.75906 | 0.037066 | 7
Oct | 0.501 | 0.43546 | 0.461 | 0.35615 | 0.56 | 0.4821 | 0.35615 | 0.56 | 0.46595 | 43.75% |  | 7 | -1.2426 | -1.2329 | -1.1996 | 0.069211 | 8
Nov | 0.828 | 0.76387 | 0.73 | 0.78997 | 0.83 | 0.74371 | 0.73 | 0.83 | 0.78092 | 12.81% |  | 0 | 0.011624 | 0.015534 | -0.0003502 | 0.00124 | 9
Dec | 1.051 | 1.0145 | 0.991 | 1.0296 | 1.13 | 1.098 | 0.991 | 1.13 | 1.0523 | 13.21% |  | 7 | -1.2365 | -1.2364 | -1.1828 | 0.06368 | 1
PEAK SENSIBLE COOLING [kW] | [6 empty] | Statistics for Example Results
| BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS |  |  |  | (Max-Min)/ | Tested Prg
Month | [6 empty] | Min | Max | Mean | Mean** (%)
Jan | 3.668 | 4.2394 | 3.785 | 4.2737 | 4.38 | 4.1681 | 3.668 | 4.38 | 4.0857 | 17.43%
Feb | 3.8251 | 4.3966 | 3.856 | 4.5578 | 4.57 | 4.326 | 3.8251 | 4.57 | 4.2553 | 17.51%
Mar | 2.9499 | 3.7143 | 3.109 | 3.5155 | 3.77 | 3.3142 | 2.9499 | 3.77 | 3.3955 | 24.15%
Apr | 2.3805 | 3.3839 | 2.568 | 2.9781 | 3.09 | 2.9655 | 2.3805 | 3.3839 | 2.8943 | 34.67%
May | 1.2191 | 1.6524 | 1.448 | 1.5525 | 1.64 | 1.5759 | 1.2191 | 1.6524 | 1.5147 | 28.61%
Jun | 1.1516 | 1.3521 | 1.194 | 1.4832 | 1.54 | 1.405 | 1.1516 | 1.54 | 1.3543 | 28.68%
Jul | 1.1787 | 1.3473 | 1.325 | 1.5603 | 1.67 | 1.5217 | 1.1787 | 1.67 | 1.4338 | 34.26%
Aug | 1.5602 | 1.6343 | 1.826 | 2.1462 | 2.19 | 2.1168 | 1.5602 | 2.19 | 1.9122 | 32.94%
Sep | 2.125 | 2.3135 | 2.355 | 2.726 | 2.77 | 2.5488 | 2.125 | 2.77 | 2.473 | 26.08% |  | 0 | -2.079 | -2.548 | -2.4591 | -0.010291
Oct | 2.5377 | 2.8938 | 2.729 | 3.1817 | 3.17 | 2.9825 | 2.5377 | 3.1817 | 2.9158 | 22.09% |  | 0 | 0.417 | 0.44432 | 0.42125 | -0.0072513
Nov | 3.4939 | 3.9162 | 3.546 | 4.1922 | 4.09 | 3.8834 | 3.4939 | 4.1922 | 3.8536 | 18.12% |  | 0 | 0.339 | 0.57027 | 0.42213 | 0.024365
Dec | 3.468 | 4.3446 | 3.699 | 4.2828 | 4.45 | 4.2521 | 3.468 | 4.45 | 4.0828 | 24.05% |  | 0 | 0.649 | 0.67846 | 0.71889 | -0.014375
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## DATA for charts
Unformatted results for use in creating charts
Note: Enter tab name in row with purple background; data then flows here and elsewhere in this workbook as formulated.
| Tab Name==> | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | Trnsys | TestSpecAlt | K | K | K | K | K | K | K | K | K | YourData
| Simulation Model: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
Organization or Country:
| Label for Charts: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
| ANNUAL LOADS | [21 empty] | LOW MASS QUALIFICATION TESTS
| ANNUAL HEATING [MWH] | [21 empty] | ANNUAL HEATING [MWH]
0 | [17 empty] | 0 | MIN | MAX |  | CASES | [17 empty] | MIN | MAX
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE
105 | 395 Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 610-600 Low Mass, Heating S. Shade | 0.113 | 0.073669 | 0.097 | 0.050431 | 0.165 | 0.08851 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 620-600 Low Mass, Heating E&W Orientation | 0.32 | 0.10084 | 0.25 | 0.1607 | 0.1523 | 0.21543 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
70 | 600 South Windows | 4.05 | 3.9928 | 4.047 | 4.3244 | 4.362 | 4.5036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 630-620 Low Mass, Heating E&W Shade | 0.553 | 0.26235 | 0.38 | 0.29847 | 0.5363 | 0.4196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
71 | 610 S. Windows + Overhang | 4.163 | 4.0664 | 4.144 | 4.3748 | 4.527 | 4.5921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 640-600 Low Mass, Heating Heating Setback | -1.368 | -1.5895 | -1.428 | -1.6625 | -1.7076 | -1.8508 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
72 | 620 East & West Windows | 4.37 | 4.0936 | 4.297 | 4.4851 | 4.5143 | 4.719 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 4.923 | 4.3559 | 4.677 | 4.7835 | 5.0506 | 5.1386 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 660-600 Low-E Windows, Heating | -0.476 | -0.3908 | -0.226 | -0.61764 | -0.575 | -0.71389 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 2.682 | 2.4032 | 2.619 | 2.6618 | 2.6544 | 2.6528 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 670-600 Single-Pane Windows, Heating | 1.434 | 1.3074 | 1.526 | 1.2918 | 1.613 | 1.6363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 680-600 Case 600 with Greater Insulation | -1.831 | -2.2067 | -2.315 | -2.1447 | -2.2299 | -2.2173 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| New Cases 660 to 695 and 980 to 995 | [20 empty] | 685-600 Case 600 with 20/20 Tstat | 0.482 | 0.58167 | 0.599 | 0.55275 | 0.5415 | 0.53862 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | [18 empty] | MIN | MAX |  | 695-685 Case 685 with Greater Insulation | -1.823 | -2.1592 | -2.261 | -2.0752 | -2.1714 | -2.1504 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 980-900 Case 900 with Greater Insulation | -1.006 | -1.1331 | -1.325 | -1.2527 | -1.2336 | -1.3636 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
70 | 600 South Windows | 4.05 | 3.9928 | 4.047 | 4.3244 | 4.362 | 4.5036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 985-900 Case 900 with 20/20 Tstat | 1.075 | 0.74132 | 0.688 | 0.70563 | 0.6986 | 0.72238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
76 | 660 Low-E Windows | 3.574 | 3.602 | 3.821 | 3.7067 | 3.787 | 3.7897 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 995-985 Case 985 with Greater Insulation | -1.471 | -1.365 | -1.509 | -1.3628 | -1.3785 | -1.4594 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
77 | 670 Single-Pane Windows | 5.484 | 5.3002 | 5.573 | 5.6161 | 5.975 | 6.1399 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 2.219 | 1.7861 | 1.732 | 2.1797 | 2.1321 | 2.2863 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 4.532 | 4.5744 | 4.646 | 4.8771 | 4.9035 | 5.0422 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 2.709 | 2.4153 | 2.385 | 2.8019 | 2.7321 | 2.8917 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 1.726 | 1.3789 | 1.591 | 1.6637 | 1.5847 | 1.814 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 0.72 | 0.24577 | 0.266 | 0.41094 | 0.3511 | 0.45047 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 2.801 | 2.1202 | 2.279 | 2.3693 | 2.2833 | 2.5364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 1.33 | 0.75518 | 0.77 | 1.0065 | 0.9048 | 1.077 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | ANNUAL COOLING [MWH] | [17 empty] | RANGE | RANGE
[19 empty] | MIN | MAX |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 610-600 Low Mass, Cooling S. Shade | -1.523 | -1.5313 | -1.259 | -1.6943 | -1.9293 | -1.6627 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
114 | 800 High-Cond. Wall Elements | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 620-600 Low Mass, Cooling E&W Orientation | -1.418 | -1.8338 | -1.523 | -1.9675 | -1.9161 | -1.9389 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 1.726 | 1.3789 | 1.591 | 1.6637 | 1.5847 | 1.814 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 630-620 Low Mass, Cooling E&W Shade | -1.33 | -1.0589 | -1.122 | -1.2235 | -1.6504 | -1.2678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
82 | 910 S. Windows + Overhang | 2.163 | 1.6477 | 1.86 | 1.9557 | 2.0672 | 2.1318 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 640-600 Low Mass, Cooling Heating Setback | -0.018 | -0.26921 | -0.195 | -0.26394 | -0.2692 | -0.3023 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
83 | 920 East & West Windows | 3.5 | 2.9561 | 3.259 | 3.3365 | 3.2997 | 3.6067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 650-600 Low Mass, Cooling Night Ventilation | -1.193 | -1.2592 | -1.246 | -1.2103 | -1.2167 | -1.1472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
84 | 930 E&W Windows + Overhang & Fins | 4.27 | 3.5236 | 3.933 | 3.9938 | 4.2776 | 4.3841 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
85 | 940 Case 900 with Htg. Temp. Setback | 1.389 | 0.86324 | 1.149 | 1.0674 | 1.0147 | 1.1691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 660-600 Low-E Windows, Cooling | -2.808 | -2.5734 | -2.172 | -2.7955 | -2.9432 | -2.8133 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
86 | 950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 670-600 Single-Pane Windows, Cooling | 0.717 | 0.66462 | 0.522 | 0.59566 | 0.3585 | 0.41828 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
87 | 960 Sunspace | #N/A | 2.5221 | 2.771 | 2.689 | 2.6239 | 2.8595 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 680-600 Case 600 with Greater Insulation | 0.116 | 0.51669 | 0.5 | 0.41686 | 0.3676 | 0.53023 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 685-600 Case 600 with 20/20 Tstat | 3.308 | 2.9461 | 2.806 | 3.0918 | 2.9596 | 3.0718 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 695-685 Case 685 with Greater Insulation | -0.375 | 0.1149 | 0.148 | 0.052759 | 0.0276 | 0.18778 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
91 | 195 Solid Conduction | 4.217 | 3.9901 | 4.157 | 4.0696 | 3.9509 | 4.0939 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 980-900 Case 900 with Greater Insulation | 0.787 | 1.5314 | 1.375 | 1.2231 | 1.2868 | 1.2514 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 5.041 | 4.8135 | 5.226 | 5.1054 | 4.9204 | 5.1429 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 985-900 Case 900 with 20/20 Tstat | 4.559 | 3.7698 | 3.497 | 3.8704 | 3.7616 | 3.8463 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 5.627 | 5.9663 | 6.531 | 6.0466 | 6.3171 | 6.4295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 995-985 Case 985 with Greater Insulation | 0.209 | 0.9685 | 0.891 | 0.84367 | 0.8995 | 0.95032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 5.652 | 5.3066 | 5.697 | 5.4054 | 5.1811 | 5.4434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
95 | 220 In-Depth Base Case | 6.377 | 6.6663 | 7.178 | 6.4551 | 6.7257 | 6.8678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
96 | 230 Infiltration | 9.851 | 9.8124 | 10.417 | 9.9299 | 9.9385 | 10.2343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
97 | 240 Internal Gains | 5.116 | 5.4426 | 5.944 | 5.2794 | 5.5393 | 5.6572 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
98 | 250 Exterior Solar Absorptance | 4.733 | 5.0438 | 5.373 | 4.8991 | 4.935 | 5.1047 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
PEAK HEATING [KW]
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
[22 empty] | 610-600 Low Mass, Heating S. Shade | -0.089 | 0.000526 | 0.004 | -0.012584 | 0.005 | 0.00060921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 620-600 Low Mass, Heating E&W Orientation | -0.11 | 0.017627 | 0.033 | 0.024696 | 0.025 | 0.025699 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 630-620 Low Mass, Heating E&W Shade | 0.107 | 0.001512 | 0.004 | -0.022564 | 0.006 | 0.0029619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 640-600 Low Mass, Heating Heating Setback | 1.378 | 1.2022 | 1.623 | 1.3541 | 0.873 | 0.67965 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 660-600 Low-E Windows, Cooling | -0.635 | -0.26192 | -0.237 | -0.3733 | -0.382 | -0.40371 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 670-600 Single-Pane Windows, Cooling | 0.867 | 0.63519 | 0.777 | 0.6491 | 0.764 | 0.86207 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 680-600 Case 600 with Greater Insulation | -1.129 | -1.2426 | -1.224 | -1.152 | -1.206 | -1.2442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 685-600 Case 600 with 20/20 Tstat | -0.086 | 0.011624 | 0.019 | 0.018741 | 0.019 | 0.015534 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 695-685 Case 685 with Greater Insulation | -1.031 | -1.2365 | -1.199 | -1.1514 | -1.222 | -1.2567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 980-900 Case 900 with Greater Insulation | -0.858 | -1.1896 | -1.071 | -1.1497 | -1.16 | -1.1863 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 985-900 Case 900 with 20/20 Tstat | 0.203 | 0.008773 | 0.005 | 0.0079536 | 0.009 | 0.0069624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 995-985 Case 985 with Greater Insulation | -1.043 | -1.0826 | -0.996 | -1.0733 | -1.082 | -1.1235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | PEAK COOLING [KW] | [17 empty] | RANGE | RANGE
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
99 | 270 South Windows | #N/A | 4.3465 | 4.273 | 4.3854 | 4.5764 | 4.6312 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
100 | 280 Cavity Albedo | #N/A | 4.5249 | 4.619 | 4.5701 | 4.7381 | 4.8699 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 610-600 Low Mass, Cooling S. Shade | -0.184 | -0.048825 | -0.091 | -0.21703 | -0.259 | -0.17795 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
101 | 290 South Shading | #N/A | 4.4242 | 4.381 | 4.4244 | 4.7447 | 4.7248 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 620-600 Low Mass, Cooling E&W Orientation | -0.946 | -1.9882 | -1.467 | -1.5541 | -1.571 | -1.4575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
102 | 300 East/West Windows | #N/A | 4.3184 | 4.46 | 4.4245 | 4.6679 | 4.7256 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 630-620 Low Mass, Cooling E&W Shade | -0.583 | -0.49451 | -0.429 | -0.58526 | -0.651 | -0.63889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
103 | 310 East/West Shading | #N/A | 4.5803 | 4.846 | 4.6912 | 5.2396 | 5.1626 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 640-600 Low Mass, Cooling Heating Setback | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
104 | 320 Thermostat | #N/A | 3.6775 | 3.599 | 3.7712 | 3.9699 | 4.0311 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 650-600 Low Mass, Cooling Night Ventilation | -0.002 | -0.19129 | -0.377 | -0.21342 | -0.232 | -0.24825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 660-600 Low-E Windows, Cooling | -2.307 | -2.548 | -2.067 | -2.5812 | -2.663 | -2.5883 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 670-600 Single-Pane Windows, Cooling | 0.567 | 0.44432 | 0.417 | 0.45463 | 0.289 | 0.35556 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 680-600 Case 600 with Greater Insulation | 0.111 | 0.57027 | 0.439 | 0.41866 | 0.483 | 0.51086 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 685-600 Case 600 with 20/20 Tstat | 0.668 | 0.67846 | 0.649 | 0.7552 | 0.741 | 0.82169 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 695-685 Case 685 with Greater Insulation | -0.086 | 0.38129 | 0.284 | 0.22753 | 0.305 | 0.30772 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 980-900 Case 900 with Greater Insulation | 0.345 | 0.29156 | 0.374 | 0.40968 | 0.445 | 0.37249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 985-900 Case 900 with 20/20 Tstat | 0.938 | 0.84883 | 0.652 | 0.87434 | 0.84 | 0.94464 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 995-985 Case 985 with Greater Insulation | 0.152 | -0.001482 | 0.107 | 0.26266 | 0.218 | 0.2302 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
High Mass QUALIFICATION TESTS
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | ANNUAL HEATING [MWH] | [17 empty] | RANGE | RANGE
105 | 395 Low Mass Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
106 | 400 Low Mass High-Cond. Wall Elements | 5.906 | 6.5358 | 7.047 | 6.3478 | 6.61 | 6.7692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 900-600 Mass, Heating | -2.324 | -2.6139 | -2.456 | -2.6607 | -2.7773 | -2.6895 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
107 | 410 Low Mass Infiltration | 7.63 | 8.0451 | 8.661 | 8.0803 | 8.2122 | 8.4449 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 920-900 High Mass, Heating E&W Orientation | 1.774 | 1.5772 | 1.668 | 1.6728 | 1.715 | 1.7927 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 6.399 | 6.8345 | 7.433 | 6.9058 | 7.027 | 7.2364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 910-900 High Mass, Heating S. Shade | 0.437 | 0.26879 | 0.269 | 0.29205 | 0.4825 | 0.31776 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 930-920 High Mass, Heating E&W Shade | 0.77 | 0.56758 | 0.674 | 0.6573 | 0.9779 | 0.7774 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 4.1559 | 4.33 | 4.5001 | 4.5039 | 4.7207 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 940-900 High Mass, Heating Heating Setback | -0.337 | -0.51566 | -0.442 | -0.5963 | -0.57 | -0.6449 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Heating | 3.743 | 3.9904 | 3.375 | 3.9625 | 3.8503 | 3.8709 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Heating | 3.828 | 4.0555 | 3.873 | 4.1938 | 4.2625 | 4.2898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960-900 High Mass, Heating Sunspace | #N/A | 1.1432 | 1.18 | 1.0254 | 1.0392 | 1.0455 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.775 | 1.718
113 | 470 Const. Exterior Surf. Coefs., Heating | 4.042 | 3.8995 | 3.54 | 4.0939 | 3.9597 | 4.0746 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
114 | 800 High Mass High-Cond. Wall Elements | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
115 | 810 High Mass Cavity Albedo | #N/A | 2.0375 | 2.454 | 2.3418 | 2.185 | 2.6098 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ANNUAL COOLING [MWH]
0 | CASE# | [17 empty] | MIN | MAX |  | ANNUAL COOLING [MWH] | [17 empty] | RANGE | RANGE
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
105 | 395 Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 900-600 Mass, Cooling | -3.108 | -3.4493 | -3.049 | -3.5383 | -3.6741 | -3.5124 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 910-900 High Mass, Cooling S. Shade | -1.23 | -1.049 | -0.893 | -1.1053 | -1.2048 | -1.0763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
70 | 600 South Windows | 5.822 | 5.9131 | 5.432 | 6.027 | 6.1618 | 5.7795 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 920-900 High Mass, Cooling E&W Orientation | 0.414 | 0.32538 | 0.323 | 0.2421 | 0.3267 | 0.28174 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
71 | 610 S. Windows + Overhang | 4.299 | 4.3818 | 4.173 | 4.3328 | 4.2325 | 4.1168 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [18 empty] | 0 | 0
72 | 620 East & West Windows | 4.404 | 4.0793 | 3.909 | 4.0595 | 4.2457 | 3.8407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960-900 High Mass, Cooling Sunspace | #N/A | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 3.074 | 3.0204 | 2.787 | 2.836 | 2.5953 | 2.5729 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 930-920 High Mass, Cooling E&W Shade | -0.967 | -0.71422 | -0.798 | -0.81173 | -1.1606 | -0.87711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 5.804 | 5.6439 | 5.237 | 5.7631 | 5.8926 | 5.4772 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 940-900 High Mass, Cooling Heating Setback | -0.101 | -0.06725 | -0.04 | -0.06439 | -0.0601 | -0.06367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 4.629 | 4.6539 | 4.186 | 4.8168 | 4.9451 | 4.6323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 950-900 High Mass, Cooling Night Ventilation | -2.128 | -1.8658 | -1.765 | -1.7818 | -1.8317 | -1.6255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 960-900 High Mass, Cooling Sunspace | #N/A | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
New Cases 660 to 695 and 980 to 995
[19 empty] | MIN | MAX
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE
70 | 600 South Windows | 5.822 | 5.9131 | 5.432 | 6.027 | 6.1618 | 5.7795 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
76 | 660 Low-E Windows | 3.014 | 3.3397 | 3.26 | 3.2315 | 3.2186 | 2.9663 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
77 | 670 Single-Pane Windows | 6.539 | 6.5777 | 5.954 | 6.6227 | 6.5203 | 6.1978 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 5.938 | 6.4298 | 5.932 | 6.4439 | 6.5294 | 6.3098 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 9.13 | 8.8592 | 8.238 | 9.1188 | 9.1214 | 8.8513 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 8.755 | 8.9741 | 8.386 | 9.1716 | 9.149 | 9.0391 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.714 | 2.4638 | 2.383 | 2.4887 | 2.4877 | 2.2671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 3.501 | 3.9953 | 3.758 | 3.7118 | 3.7745 | 3.5185 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 7.273 | 6.2336 | 5.88 | 6.3592 | 6.2493 | 6.1135 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 7.482 | 7.2022 | 6.771 | 7.2029 | 7.1488 | 7.0638 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | MIN | MAX
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE
114 | 800 High-Cond. Wall Elements | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.714 | 2.4638 | 2.383 | 2.4887 | 2.4877 | 2.2671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | PEAK HEATING [KW] | [17 empty] | RANGE | RANGE
82 | 910 S. Windows + Overhang | 1.484 | 1.4149 | 1.49 | 1.3835 | 1.2829 | 1.1909 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
83 | 920 East & West Windows | 3.128 | 2.7892 | 2.706 | 2.7308 | 2.8144 | 2.5489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
84 | 930 E&W Windows + Overhang & Fins | 2.161 | 2.075 | 1.908 | 1.9191 | 1.6538 | 1.6718 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 900-600 Mass, Heating | -0.704 | -0.57684 | -0.582 | -0.51694 | -0.595 | -0.58042 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
85 | 940 Case 900 with Htg. Temp. Setback | 2.613 | 2.3966 | 2.343 | 2.4244 | 2.4276 | 2.2035 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 910-900 High Mass, Heating S. Shade | 0.21 | 0.025635 | 0.021 | 0.011437 | 0.051 | 0.020717 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
86 | 950 Case 900 with Night Ventilation | 0.586 | 0.59803 | 0.618 | 0.70692 | 0.656 | 0.64162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 920-900 High Mass, Heating E&W Orientation | 0.344 | 0.069036 | 0.06 | 0.08269 | 0.073 | 0.085796 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
87 | 960 Sunspace | #N/A | 0.92578 | 0.909 | 0.90712 | 0.9496 | 0.78896 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 930-920 High Mass, Heating E&W Shade | 0.073 | 0.024542 | 0.036 | 0.014719 | 0.059 | 0.03614 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 940-900 High Mass, Heating Heating Setback | 1.331 | 0.60852 | 1.206 | 0.45528 | 0.489 | 0.62635 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 960-900 High Mass, Heating Sunspace | #N/A | -0.31135 | -0.368 | -0.42812 | -0.432 | -0.47808 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
91 | 195 Solid Conduction | 0.712 | 0.60552 | 0.628 | 0.61152 | 0.611 | 0.59153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 0.839 | 0.80024 | 0.835 | 0.81408 | 0.8004 | 0.78844 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 0.688 | 0.50307 | 0.496 | 0.5599 | 0.5185 | 0.45918 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [18 empty] | RANGE | RANGE
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 0.952 | 0.94579 | 0.922 | 0.87747 | 0.8948 | 0.85047 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | PEAK COOLING [KW] | [17 empty] | RANGE | RANGE
95 | 220 In-Depth Base Case | 0.803 | 0.6106 | 0.55 | 0.6099 | 0.5762 | 0.49766 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX
96 | 230 Infiltration | 1.184 | 0.99134 | 0.929 | 0.99121 | 0.955 | 0.89664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 900-600 Mass, Cooling | -2.611 | -3.1046 | -2.866 | -3.3111 | -3.297 | -3.1057 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
97 | 240 Internal Gains | 1.287 | 0.98237 | 0.876 | 0.97875 | 0.9218 | 0.83378 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 910-900 High Mass, Cooling S. Shade | -0.546 | -0.65436 | -0.453 | -0.81835 | -0.684 | -0.85903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
98 | 250 Exterior Solar Absorptance | 3.612 | 3.429 | 3.471 | 3.1816 | 3.4668 | 2.9038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 920-900 High Mass, Cooling E&W Orientation | 0.442 | -0.31975 | 0.154 | 0.21988 | 0.203 | 0.21408 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 930-920 High Mass, Cooling E&W Shade | -0.429 | -0.39486 | -0.375 | -0.47881 | -0.605 | -0.54103 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99 | 270 South Windows | #N/A | 7.2708 | 6.698 | 7.5215 | 7.3086 | 7.2885 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
100 | 280 Cavity Albedo | #N/A | 4.9963 | 4.215 | 5.1829 | 5.2058 | 4.8081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 940-900 High Mass, Cooling Heating Setback | 0.119 | 0 | 0 | -0.00048524 | -0.005 | -0.0024478 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
101 | 290 South Shading | #N/A | 5.6097 | 5.31 | 5.7425 | 5.3206 | 5.4612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 950-900 High Mass, Cooling Night Ventilation | -0.673 | -1.0129 | -0.502 | -0.65292 | -0.694 | -0.70368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
102 | 300 East/West Windows | #N/A | 5.0551 | 4.805 | 5.152 | 5.0381 | 4.913 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960-900 High Mass, Cooling Sunspace | #N/A | -1.9993 | -1.189 | -1.5605 | -1.493 | -1.6016 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
103 | 310 East/West Shading | #N/A | 3.7519 | 3.402 | 3.6695 | 3.1279 | 3.3242 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
104 | 320 Thermostat | #N/A | 4.8585 | 4.42 | 4.986 | 4.9131 | 4.7877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Low Mass Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
106 | 400 Low Mass High-Cond. Wall Elements | 0.063 | 0.023304 | 0.017 | 0.030566 | 0.0244 | 0.012683 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
107 | 410 Low Mass Infiltration | 0.096 | 0.048491 | 0.041 | 0.057269 | 0.0523 | 0.03512 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 0.228 | 0.14062 | 0.119 | 0.15257 | 0.1419 | 0.10944 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 3.9853 | 3.458 | 4.085 | 4.4141 | 3.7412 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Cooling | 6.172 | 5.689 | 6.161 | 6.5073 | 6.6132 | 6.5307 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Cooling | 6.26 | 5.9398 | 5.929 | 6.4746 | 6.7291 | 6.2434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Low Mass PRIMITIVE DIAGNOSTIC TESTS
113 | 470 Const. Exterior Surf. Coefs., Cooling | 5.987 | 5.6439 | 5.649 | 6.0294 | 6.0054 | 6.0559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
114 | 800 High Mass High-Cond. Wall Elements | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | CASES
115 | 810 High Mass Cavity Albedo | #N/A | 1.4807 | 1.357 | 1.5078 | 1.6056 | 1.2945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ANNUAL HEATING [MWH]
[22 empty] | 200-195 Heating Surface Convection | 0.824 | 0.82337 | 1.069 | 1.0358 | 0.9695 | 1.0489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [20 empty] | 210-200 Heating Ext IR (Int IR "off") | 0.586 | 1.1529 | 1.305 | 0.94118 | 1.3967 | 1.2866 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 220-215 Heating Ext IR (Int IR "on") | 0.725 | 1.3597 | 1.481 | 1.0497 | 1.5446 | 1.4244 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | COUNTRY: | [17 empty] | RANGE | RANGE |  | 215-200 Heating Int IR (Ext IR "off") | 0.611 | 0.49316 | 0.471 | 0.30004 | 0.2607 | 0.30051 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
KW | CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX | AVERAGE | 220-210 Heating Int IR (Ext IR "on") | 0.75 | 0.70003 | 0.647 | 0.40857 | 0.4086 | 0.43834 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Solid Conduction | 1.948 | 2.1574 | 2.085 | 1.9517 | 2.09 | 2.1613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 3.3 | 3.2539 | 3.36 | 3.3163 | 3.285 | 3.4088 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
70 | 600 South Windows | 3.255 | 3.0202 | 3.035 | 3.2044 | 3.228 | 3.3589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 230-220 Heating Infiltration | 3.474 | 3.146 | 3.239 | 3.4747 | 3.2128 | 3.3665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
71 | 610 S. Windows + Overhang | 3.166 | 3.0208 | 3.039 | 3.1918 | 3.233 | 3.3595 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 240-220 Heating Internal Gains | -1.261 | -1.2237 | -1.234 | -1.1758 | -1.1864 | -1.2106 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
72 | 620 East & West Windows | 3.145 | 3.0379 | 3.068 | 3.2291 | 3.253 | 3.3846 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 250-220 Heating Ext Solar Absorptance | -1.644 | -1.6225 | -1.805 | -1.556 | -1.7907 | -1.7631 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 3.252 | 3.0394 | 3.072 | 3.2066 | 3.259 | 3.3876 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 270-220 Heating South Windows | #N/A | -2.3199 | -2.905 | -2.0698 | -2.1493 | -2.2367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 4.633 | 4.2225 | 4.658 | 4.5585 | 4.101 | 4.0385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 280-270 Heating Cavity Albedo | #N/A | 0.17846 | 0.346 | 0.18472 | 0.1617 | 0.23873 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 290-270 Heating South Shading | #N/A | 0.077715 | 0.108 | 0.039046 | 0.1683 | 0.09362 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 300-270 Heating E&W Windows | #N/A | -0.028118 | 0.187 | 0.039197 | 0.0915 | 0.09447 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| New Cases 660 to 695 and 980 to 995 | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
[19 empty] | MIN | MAX |  | 320-270 Heating Thermostat | #N/A | -0.66901 | -0.674 | -0.61416 | -0.6065 | -0.60003 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 310-300 Heating E&W Shading | #N/A | 0.26199 | 0.386 | 0.26662 | 0.5717 | 0.43695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
70 | 600 South Windows | 3.255 | 3.0202 | 3.035 | 3.2044 | 3.228 | 3.3589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
76 | 660 Low-E Windows | 2.62 | 2.7583 | 2.798 | 2.8311 | 2.846 | 2.9552 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
77 | 670 Single-Pane Windows | 4.122 | 3.6554 | 3.812 | 3.8535 | 3.992 | 4.221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 2.126 | 1.7776 | 1.811 | 2.0524 | 2.022 | 2.1147 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 3.169 | 3.0319 | 3.054 | 3.2232 | 3.247 | 3.3744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 2.138 | 1.7953 | 1.855 | 2.0718 | 2.025 | 2.1177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.633 | 2.7785 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 1.693 | 1.2538 | 1.382 | 1.5378 | 1.473 | 1.5921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 2.754 | 2.4522 | 2.458 | 2.6954 | 2.642 | 2.7854 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 1.711 | 1.3696 | 1.462 | 1.6221 | 1.56 | 1.662 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | RANGE | RANGE
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX | AVERAGE
114 | 800 High-Cond. Wall Elements | 2.957 | 2.7776 | 2.864 | 2.9237 | 2.84 | 2.9669 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.633 | 2.7785 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
82 | 910 S. Windows + Overhang | 2.761 | 2.469 | 2.474 | 2.6989 | 2.684 | 2.7992 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
83 | 920 East & West Windows | 2.895 | 2.5124 | 2.513 | 2.7702 | 2.706 | 2.8643 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ANNUAL COOLING [MWH]
84 | 930 E&W Windows + Overhang & Fins | 2.968 | 2.537 | 2.549 | 2.7849 | 2.765 | 2.9004 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
85 | 940 Case 900 with Htg. Temp. Setback | 3.882 | 3.0519 | 3.659 | 3.1428 | 3.122 | 3.4048 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | CASES | [17 empty] | MIN | MAX
86 | 950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 200-195 Cooling Surface Convection | 0.127 | 0.19471 | 0.207 | 0.20256 | 0.1894 | 0.19691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
87 | 960 Sunspace | #N/A | 2.132 | 2.085 | 2.2594 | 2.201 | 2.3004 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 210-200 Cooling Ext IR (Int IR "off") | -0.151 | -0.29717 | -0.339 | -0.25418 | -0.2819 | -0.32926 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 220-215 Cooling Ext IR (Int IR "on") | -0.149 | -0.33519 | -0.372 | -0.26756 | -0.3186 | -0.35281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 215-200 Cooling Int IR (Ext IR "off") | 0.113 | 0.14556 | 0.087 | 0.063388 | 0.0944 | 0.062024 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
91 | 195 Solid Conduction | 1.802 | 1.7907 | 1.799 | 1.7944 | 1.802 | 1.7959 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 0.115 | 0.10753 | 0.054 | 0.050007 | 0.0577 | 0.038475 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 2.272 | 2.226 | 2.308 | 2.3413 | 2.275 | 2.3527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 2.374 | 2.629 | 2.605 | 2.5646 | 2.671 | 2.7498 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 230-220 Cooling Infiltration | 0.381 | 0.38074 | 0.379 | 0.38131 | 0.3788 | 0.39898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 2.521 | 2.42 | 2.52 | 2.4778 | 2.39 | 2.4894 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 240-220 Cooling Internal Gains | 0.484 | 0.37177 | 0.326 | 0.36884 | 0.3456 | 0.33612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
95 | 220 In-Depth Base Case | 2.631 | 2.8394 | 2.863 | 2.692 | 2.788 | 2.8786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 250-220 Cooling Ext Solar Abs. | 2.809 | 2.8184 | 2.921 | 2.5717 | 2.8906 | 2.4062 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
96 | 230 Infiltration | 4.219 | 4.1329 | 4.223 | 4.3161 | 4.16 | 4.3153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 270-220 Cooling South Windows | #N/A | 6.6602 | 6.148 | 6.9116 | 6.7324 | 6.7908 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
97 | 240 Internal Gains | 2.431 | 2.6514 | 2.685 | 2.5071 | 2.605 | 2.6931 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 280-270 Cooling Cavity Albedo | #N/A | -2.2745 | -2.483 | -2.3386 | -2.1028 | -2.4804 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
98 | 250 Exterior Solar Absorptance | 2.631 | 2.8371 | 2.855 | 2.6874 | 2.78 | 2.8744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 320-270 Cooling Thermostat | #N/A | -2.4123 | -2.278 | -2.5356 | -2.3955 | -2.5008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE | 290-270 Cooling South Shading | #N/A | -1.6611 | -1.388 | -1.779 | -1.988 | -1.8273 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99 | 270 South Windows | #N/A | 2.6114 | 2.56 | 2.5966 | 2.748 | 2.8432 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 300-270 Cooling E&W Windows | #N/A | -2.2158 | -1.893 | -2.3695 | -2.2705 | -2.3755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
100 | 280 Cavity Albedo | #N/A | 2.6122 | 2.568 | 2.602 | 2.752 | 2.8487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 310-300 Cooling E&W Shading | #N/A | -1.3032 | -1.403 | -1.4825 | -1.9102 | -1.5887 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
101 | 290 South Shading | #N/A | 2.6115 | 2.561 | 2.5834 | 2.75 | 2.8434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | PEAK HEATING [KW]
102 | 300 East/West Windows | #N/A | 2.6141 | 2.589 | 2.6031 | 2.766 | 2.8536 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
103 | 310 East/West Shading | #N/A | 2.6149 | 2.592 | 2.5801 | 2.771 | 2.8563 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 200-195 Heating Surface Convection | 0.47 | 0.43534 | 0.509 | 0.54692 | 0.473 | 0.5568 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
104 | 320 Thermostat | #N/A | 2.609 | 2.546 | 2.5735 | 2.733 | 2.8335 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | CASES
105 | 395 Low Mass Solid Conduction | 1.948 | 2.1574 | 2.085 | 1.9517 | 2.09 | 2.1613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 210-200 Heating Ext IR (Int IR "off") | 0.102 | 0.40294 | 0.297 | 0.22323 | 0.396 | 0.39706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
106 | 400 Low Mass High-Cond. Wall Elements | 2.559 | 2.8394 | 2.863 | 2.692 | 2.788 | 2.8786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 220-215 Heating Ext IR (Int IR "on") | 0.11 | 0.41938 | 0.343 | 0.21421 | 0.398 | 0.3892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
107 | 410 Low Mass Infiltration | 3.338 | 3.4407 | 3.543 | 3.504 | 3.473 | 3.5969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 220-210 Heating Int IR (Ext IR "on") | 0.257 | 0.2104 | 0.258 | 0.12747 | 0.117 | 0.12878 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 3.138 | 3.2562 | 3.365 | 3.3191 | 3.29 | 3.4115 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 215-200 Heating Int IR (Ext IR "off") | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 3.3 | 3.2539 | 3.36 | 3.3163 | 3.285 | 3.4088 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 3.0272 | 3.06 | 3.2187 | 3.237 | 3.3743 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Heating | 2.989 | 2.9783 | 2.753 | 3.0998 | 3.042 | 3.0373 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Heating | 3.055 | 2.9714 | 2.98 | 3.0911 | 3.101 | 3.1597 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
113 | 470 Const. Exterior Surf. Coefs., Heating | 3.118 | 3.0007 | 2.807 | 3.2067 | 3.169 | 3.2315 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 230-220 Heating Infiltration | 1.588 | 1.2935 | 1.36 | 1.6241 | 1.372 | 1.4367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
114 | 800 High Mass High-Cond. Wall Elements | 2.957 | 2.7776 | 2.864 | 2.9237 | 2.84 | 2.9669 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 240-220 Heating Internal Gains | -0.2 | -0.18795 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
115 | 810 High Mass Cavity Albedo | #N/A | 2.5001 | 2.512 | 2.749 | 2.695 | 2.8447 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 250-220 Heating Ext Solar Absorpance | 0 | -0.002311 | -0.008 | -0.0046183 | -0.008 | -0.0042134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [20 empty] | 270-220 Heating South Windows | #N/A | -0.228 | -0.303 | -0.09541 | -0.04 | -0.035333 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 280-270 Heating Cavity Albedo | #N/A | 0.000866 | 0.008 | 0.005384 | 0.004 | 0.005441 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | COUNTRY: | [17 empty] | RANGE | RANGE |  | 320-270 Heating Thermostat | #N/A | -0.002429 | -0.014 | -0.023142 | -0.015 | -0.0097238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
KW | CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX | AVERAGE | 290-270 Heating South Shading | #N/A | 7.1e-05 | 0.001 | -0.013189 | 0.002 | 0.00016606 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Solid Conduction | 0.547 | 0.3575 | 0.308 | 0.37747 | 0.294 | 0.2652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 High-Cond. Wall Elements | 2.167 | 1.8398 | 1.84 | 1.9294 | 1.874 | 1.7041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 215-210 | 0.147 | -0.20898 | -0.085 | -0.086742 | -0.281 | -0.26042 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
70 | 600 South Windows | 5.65 | 6.481 | 5.422 | 6.3516 | 6.193 | 6.0457 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 300-270 Heating E&W Windows | #N/A | 0.002675 | 0.029 | 0.0065091 | 0.018 | 0.010408 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
71 | 610 S. Windows + Overhang | 5.466 | 6.4322 | 5.331 | 6.1345 | 5.934 | 5.8678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 310-300 Heating E&W Shading | #N/A | 0.00082 | 0.003 | -0.023064 | 0.005 | 0.0026624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
72 | 620 East & West Windows | 4.704 | 4.4928 | 3.955 | 4.7974 | 4.622 | 4.5883 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
73 | 630 E&W Windows + Overhang & Fins | 4.121 | 3.9983 | 3.526 | 4.2122 | 3.971 | 3.9494 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
74 | 640 Case 600 with Htg. Temp. Setback | 5.65 | 6.429 | 5.365 | 6.2974 | 6.127 | 5.9671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
75 | 650 Case 600 with Night Ventilation | 5.648 | 6.2897 | 5.045 | 6.1381 | 5.961 | 5.7975 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
New Cases 660 to 695 and 980 to 995
[19 empty] | MIN | MAX
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | RANGE | RANGE | AVERAGE
70 | 600 South Windows | 5.65 | 6.481 | 5.422 | 6.3516 | 6.193 | 6.0457 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
76 | 660 Low-E Windows | 3.343 | 3.933 | 3.355 | 3.7703 | 3.53 | 3.4574 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
77 | 670 Single-Pane Windows | 6.217 | 6.9253 | 5.839 | 6.8062 | 6.482 | 6.4013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
78 | 680 Case 600 with Greater Insulation | 5.761 | 7.0513 | 5.861 | 6.7702 | 6.676 | 6.5566 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
79 | 685 Case 600 with 20/20 Tstat | 6.318 | 7.1594 | 6.071 | 7.1068 | 6.934 | 6.8674 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
80 | 695 Case 685 with Greater Insulation | 6.232 | 7.5407 | 6.355 | 7.3343 | 7.239 | 7.1752 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.896 | 2.9401 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
88 | 980 Case 900 with Greater Insulation | 3.384 | 3.668 | 2.93 | 3.4501 | 3.341 | 3.3126 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
89 | 985 Case 900 with 20/20 Tstat | 3.977 | 4.2253 | 3.208 | 3.9148 | 3.736 | 3.8847 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
90 | 995 Case 985 with Greater Insulation | 4.129 | 4.2238 | 3.315 | 4.1774 | 3.954 | 4.1149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PEAK COOLING [KW]
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
[22 empty] | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | FINLAND | DATA
[22 empty] | 200-195 Cooling Surface Convection | 0.153 | 0.22092 | 0.266 | 0.26648 | 0.254 | 0.26541 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 210-200 Cooling Ext IR (Int IR "off") | -0.078 | -0.26955 | -0.302 | -0.22309 | -0.321 | -0.37477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 220-215 Cooling Ext IR (Int IR on) | -0.057 | -0.26079 | -0.346 | -0.2159 | -0.354 | -0.38409 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | [21 empty] | 0 | 0
114 | 800 High-Cond. Wall Elements | 1.286 | 1.1019 | 1.157 | 1.0458 | 1.052 | 0.93559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 215-200 Cooling Int IR (Ext IR "off") | 0.122 | 0.15407 | 0.147 | 0.092921 | 0.168 | 0.093176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
81 | 900 South Windows | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.896 | 2.9401 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 220-210 Cooling Int IR (Ext IR "on") | 0.143 | 0.16283 | 0.103 | 0.1001 | 0.135 | 0.083849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
82 | 910 S. Windows + Overhang | 2.493 | 2.7221 | 2.103 | 2.2221 | 2.212 | 2.081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 230-220 Cooling Infiltration | 0.658 | 0.61968 | 0.694 | 0.6564 | 0.689 | 0.72555 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
83 | 920 East & West Windows | 3.481 | 3.0567 | 2.71 | 3.2603 | 3.099 | 3.1541 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 240-220 Cooling Internal Gains | 0.198 | 0.18623 | 0.178 | 0.18145 | 0.18 | 0.18157 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
84 | 930 E&W Windows + Overhang & Fins | 3.052 | 2.6618 | 2.335 | 2.7815 | 2.494 | 2.6131 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 250-220 Cooling Ext Solar Absorpance | 1.577 | 1.6815 | 1.711 | 1.6821 | 2.022 | 1.72 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
85 | 940 Case 900 with Htg. Temp. Setback | 3.158 | 3.3764 | 2.556 | 3.04 | 2.891 | 2.9376 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 270-220 Cooling South Windows | #N/A | 5.9025 | 4.792 | 5.6543 | 5.601 | 5.6695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
86 | 950 Case 900 with Night Ventilation | 2.366 | 2.3635 | 2.054 | 2.3875 | 2.202 | 2.2364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
87 | 960 Sunspace | #N/A | 1.3771 | 1.367 | 1.4799 | 1.403 | 1.3385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 280-270 Cavity Albedo | #N/A | -2.2459 | -2.064 | -2.1116 | -1.937 | -2.2376 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 320-270 Thermostat | #N/A | -0.53772 | -0.528 | -0.62971 | -0.62 | -0.68806 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX | AVERAGE | 290-270 South Shading | #N/A | -0.13883 | -0.093 | -0.24426 | -0.202 | -0.23557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
91 | 195 Solid Conduction | 1.118 | 0.99425 | 0.973 | 1.041 | 0.944 | 0.99351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 300-270 E&W Windows | #N/A | -2.8478 | -2.137 | -2.3633 | -2.392 | -2.3592 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
92 | 200 Surface Convection Int IR="off" Ext IR="off" | 1.271 | 1.2152 | 1.239 | 1.3075 | 1.198 | 1.2589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 310-300 E&W Shading | #N/A | -0.36725 | -0.443 | -0.50594 | -0.603 | -0.57679 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
93 | 210 Infrared Radiation Int IR="off" Ext IR="on" | 1.193 | 0.94562 | 0.937 | 1.0844 | 0.877 | 0.88416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
94 | 215 Infrared Radiation Int IR="on" Ext IR="off" | 1.393 | 1.3692 | 1.386 | 1.4004 | 1.366 | 1.3521 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Low Mass REALISTIC DIAGNOSTIC TESTS
95 | 220 In-Depth Base Case | 1.336 | 1.1085 | 1.04 | 1.1845 | 1.012 | 0.96801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ANNUAL HEATING [MWH]
96 | 230 Infiltration | 1.994 | 1.7281 | 1.734 | 1.8409 | 1.701 | 1.6936 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
97 | 240 Internal Gains | 1.534 | 1.2947 | 1.218 | 1.3659 | 1.192 | 1.1496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
98 | 250 Exterior Solar Absorptance | 2.913 | 2.79 | 2.751 | 2.8666 | 3.034 | 2.688 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 400-395 Low Mass, Heating Surf. Conv. & IR | 1.341 | 1.6808 | 1.902 | 1.7066 | 1.7443 | 1.8611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg | MIN | MAX | AVERAGE | 410-400 Low Mass, Heating Infiltration | 1.724 | 1.5093 | 1.614 | 1.7325 | 1.6022 | 1.6757 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99 | 270 South Windows | #N/A | 7.011 | 5.832 | 6.8388 | 6.613 | 6.6375 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 420-410 Low Mass, Heating Int. Gains | -1.231 | -1.2106 | -1.228 | -1.1745 | -1.1852 | -1.2086 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
100 | 280 Cavity Albedo | #N/A | 4.7651 | 3.768 | 4.7272 | 4.676 | 4.3999 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 600-430 Low Mass, Heating S. Window | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
101 | 290 South Shading | #N/A | 6.8722 | 5.739 | 6.5946 | 6.411 | 6.4019 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 430-420 Low Mass, Heating Ext. Solar Abs. | -1.228 | -1.3804 | -1.479 | -1.2857 | -1.4821 | -1.3858 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
102 | 300 East/West Windows | #N/A | 4.1631 | 3.695 | 4.4755 | 4.221 | 4.2782 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 440-600 Low Mass, Heating Cavity Albedo | #N/A | 0.16318 | 0.283 | 0.17569 | 0.1419 | 0.21713 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
103 | 310 East/West Shading | #N/A | 3.7959 | 3.252 | 3.9695 | 3.618 | 3.7015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ANNUAL COOLING [MWH]
104 | 320 Thermostat | #N/A | 6.4733 | 5.304 | 6.2091 | 5.993 | 5.9494 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
105 | 395 Low Mass Solid Conduction | 0.547 | 0.3575 | 0.308 | 0.37747 | 0.294 | 0.2652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | CASES | [16 empty] | 0
106 | 400 Low Mass High-Cond. Wall Elements | 0.798 | 0.49365 | 0.457 | 0.60691 | 0.456 | 0.37199 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0.042 | 0.015542 | 0.011 | 0.020185 | 0.0189 | 0.0091667 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
107 | 410 Low Mass Infiltration | 1.011 | 0.69988 | 0.709 | 0.82785 | 0.624 | 0.60368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 410-400 Low Mass, Cooling Infiltration | 0.033 | 0.025188 | 0.024 | 0.026703 | 0.0279 | 0.022437 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
108 | 420 Low Mass Internal Gains | 1.208 | 0.90853 | 0.917 | 1.0325 | 0.836 | 0.81407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
109 | 430 Low Mass Ext. Shortwave Absorptance | 2.167 | 1.8398 | 1.84 | 1.9294 | 1.874 | 1.7041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
110 | 440 Low Mass Cavity Albedo | #N/A | 4.6655 | 3.766 | 4.686 | 4.679 | 4.3076 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 215-200 | 0.113 | 0.14556 | 0.087 | 0.063388 | 0.0944 | 0.062024 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
111 | 450 Const. Int.&Ext. Surf. Coefs., Cooling | 5.812 | 6.1798 | 6.063 | 6.4663 | 6.501 | 6.3134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
112 | 460 Const. Interior Surf. Coefs., Cooling | 5.804 | 6.2429 | 5.902 | 6.3742 | 6.304 | 6.0689 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
113 | 470 Const. Exterior Surf. Coefs., Cooling | 5.695 | 6.3877 | 5.57 | 6.4436 | 6.407 | 6.32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
114 | 800 High Mass High-Cond. Wall Elements | 1.286 | 1.1019 | 1.157 | 1.0458 | 1.052 | 0.93559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 420-410 Low Mass, Cooling Int. Gains | 0.132 | 0.092126 | 0.078 | 0.095302 | 0.0896 | 0.074316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
115 | 810 High Mass Cavity Albedo | #N/A | 2.4105 | 1.94 | 2.2702 | 2.179 | 2.1129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 430-420 Low Mass, Cooling Ext Solar Abs. | 0.856 | 0.76554 | 0.825 | 0.70305 | 0.8108 | 0.62959 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| FREE-FLOAT TEMPERATURE OUTPUT | [20 empty] | 600-430 Low Mass, Cooling S. Window | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [20 empty] | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.9278 | -1.974 | -1.942 | -1.7477 | -2.0384 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | PEAK HEATING [KW] --Charts not created directly here; these addresses are referenced by "BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL" below
0 | COUNTRY:
TMP (C) | CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C)
[19 empty] | MIN | MAX | AVERAGE |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
130 | 600FF - Low Mass Building with South Windows | 63.4 | 68.3608 | 65 | 63.8408 | 64.6 | 62.3692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 400-395 Low Mass, Heating Surf. Conv. & IR | 0.611 | 0.68193 | 0.778 | 0.74028 | 0.698 | 0.71723 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
131 | 900FF - High Mass Building with South Windows | 46 | 45.1138 | 44.46 | 44.2922 | 44.3 | 43.2522 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 410-400 Low Mass, Heating Infiltration | 0.779 | 0.60131 | 0.68 | 0.81203 | 0.685 | 0.71836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
132 | 650FF Case 600FF with Night Ventilation | 62.1 | 66.8465 | 62.59 | 62.469 | 63.3 | 61.1332 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 215-200 | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
133 | 950FF Case 900FF with Night Ventilation | 37.1 | 36.7765 | 36.37 | 36.6805 | 36.4 | 36.1267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 420-410 Low Mass, Heating Int. Gains | -0.2 | -0.18445 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
134 | 680FF Case 600FF with More Insulation | 72.5 | 78.5143 | 74.97 | 70.1447 | 72.2 | 69.7742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 430-420 Low Mass, Heating Ext Solar Abs. | 0.162 | -0.002354 | -0.005 | -0.002869 | -0.005 | -0.0026383 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
135 | 980FF Case 900FF with More Insulation | 49.7 | 52.2464 | 52.81 | 49.6221 | 50.2 | 48.5406 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 600-430 Low Mass, Heating S. Window | -0.045 | -0.23365 | -0.325 | -0.11183 | -0.057 | -0.049923 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
136 | 960 Sunspace | #N/A | 48.9033 | 53.18 | 49.8773 | 49.5 | 48.0966 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 440-600 Low Mass, Heating Cavity Albedo | #N/A | 0.006973 | 0.025 | 0.014228 | 0.009 | 0.015399 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | PEAK COOLING [KW]
0 | COUNTRY: | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
TMP (C) | CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) |  |  |  | CASES
[22 empty] | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0.251 | 0.13615 | 0.149 | 0.22943 | 0.162 | 0.10678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | MIN | MAX | AVERAGE | 410-400 Low Mass, Cooling Infiltration | 0.213 | 0.20623 | 0.252 | 0.22094 | 0.168 | 0.2317 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 420-410 Low Mass, Cooling Int. Gains | 0.197 | 0.20865 | 0.208 | 0.20469 | 0.212 | 0.21039 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
130 | 600FF - Low Mass Building with South Windows | -9.9 | -12.8904 | -13.52 | -12.5613 | -13.5 | -13.8442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 430-420 Low Mass, Cooling Ext. Solar Abs. | 0.959 | 0.93129 | 0.923 | 0.89683 | 1.038 | 0.89001 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
131 | 900FF - High Mass Building with South Windows | 0.6 | 2.1647 | 1.31 | 1.2424 | 1.6 | 0.63931 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 600-430 Low Mass, Cooling S. Window | 3.483 | 4.6412 | 3.582 | 4.4222 | 4.319 | 4.3417 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
132 | 650FF Case 600FF with Night Ventilation | -16.7 | -17.7616 | -17.37 | -17.0758 | -17.5 | -17.5067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.8155 | -1.656 | -1.6656 | -1.514 | -1.7382 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
133 | 950FF Case 900FF with Night Ventilation | -13.2 | -13.2443 | -13.36 | -12.8122 | -12.5 | -12.7995 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
134 | 680FF Case 600FF with More Insulation | -5.7 | -6.1966 | -6.89 | -7.0523 | -7.2 | -8.0736 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
135 | 980FF Case 900FF with More Insulation | 7.3 | 12.5361 | 12.4 | 9.917 | 10.5 | 9.4717 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
136 | 960 Sunspace | #N/A | 8.0165 | 6.74 | 5.0931 | 5 | 4.2376 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | High Mass DIAGNOSTIC TESTS
| AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [20 empty] | ANNUAL HEATING [MWH]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | [20 empty] | CASES
TMP (C) | CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) |  |  |  | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.03 | -0.54834 | -0.551 | -0.50457 | -0.5651 | -0.48107 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
130 | 600FF - Low Mass Building with South Windows | 26.1 | 25.5736 | 25.26 | 24.9173 | 25.26 | 24.2578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 900-800 High Mass, Heating S. Window | -3.415 | -3.5268 | -3.812 | -3.4519 | -3.3951 | -3.5554 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
131 | 900FF - High Mass Building with South Windows | 25.5 | 25.6921 | 25.25 | 25.1213 | 25.34 | 24.4623 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 900-810 High Mass, Heating Int. Sol. Abs. | #N/A | -0.65862 | -0.863 | -0.67814 | -0.6003 | -0.79572 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
132 | 650FF Case 600FF with Night Ventilation | 17.6 | 18.4599 | 18.04 | 18.4195 | 18.93 | 18.402 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 910-610 Mass, Heating w/ S. Shade | -2 | -2.4187 | -2.284 | -2.4191 | -2.4598 | -2.4603 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
133 | 950FF Case 900FF with Night Ventilation | 15 | 14.7096 | 14.35 | 14.789 | 14.78 | 14.6786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 920-620 Mass, Heating w/ E&W Window | -0.87 | -1.1375 | -1.038 | -1.1486 | -1.2146 | -1.1123 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
134 | 680FF Case 600FF with More Insulation | 31.8 | 33.1103 | 33.3 | 30.9584 | 31.71 | 30.1869 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 930-630 Mass, Heating w/ E&W Shade | -0.653 | -0.8323 | -0.744 | -0.78974 | -0.773 | -0.75448 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
135 | 980FF Case 900FF with More Insulation | 30.7 | 33.2952 | 33.3 | 31.1618 | 31.84 | 30.492 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 940-640 Mass, Heating w/ Heating Setback | -1.293 | -1.54 | -1.47 | -1.5945 | -1.6397 | -1.4836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
136 | 960 Sunspace | #N/A | 28.5573 | 29.45 | 27.7427 | 27.74 | 26.7976 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SOLAR RADIATION
| ANNUAL INCIDENT TOTAL | [20 empty] | ANNUAL COOLING [MWH]
| CASE 600 | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
CASES
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.611 | -0.52633 | -0.582 | -0.48209 | -0.5613 | -0.45694 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 900-800 High Mass, Cooling S. Window | 2.241 | 2.084 | 2.021 | 2.1152 | 2.0963 | 1.985 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
155 | 600 HORZ. | 1670 | 1662.5278 | 1667.158 | 1664.3425 | 1665.18 | 1668.98 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 900-810 High Mass, Cooling Int. Sol. Abs. | #N/A | 0.98312 | 1.026 | 0.98095 | 0.8821 | 0.97261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
156 | 600 NORTH | 453 | 399.0475 | 477.31 | 438.241 | 432.12 | 440.165 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 910-610 Mass, Cooling w/ S. Shade | -2.815 | -2.9669 | -2.683 | -2.9493 | -2.9496 | -2.9259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
157 | 600 EAST | 1061 | 1026.9874 | 1016.676 | 1062.1572 | 1054.24 | 1067.94 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 920-620 Mass, Cooling w/ E&W Window | -1.276 | -1.2901 | -1.203 | -1.3287 | -1.4313 | -1.2918 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
158 | 600 SOUTH | 1387 | 1316.9162 | 1290.593 | 1370.4819 | 1363.1 | 1384.23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 930-630 Mass, Cooling w/ E&W Shade | -0.913 | -0.94541 | -0.879 | -0.91693 | -0.9415 | -0.90111 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
159 | 600 WEST | 997 | 903.0665 | 905.722 | 967.278 | 961.18 | 974.473 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 940-640 Mass, Cooling w/ Heating Setback | -3.191 | -3.2473 | -2.894 | -3.3387 | -3.465 | -3.2738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 950-650 Mass, Cooling w/ Night Vent | -4.043 | -4.0559 | -3.568 | -4.1099 | -4.2891 | -3.9907 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | PEAK HEATING [KW] | [17 empty] | 0 | 0
| = | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
CASES
| SOLAR RADIATION | [20 empty] | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.343 | -0.47625 | -0.496 | -0.3926 | -0.445 | -0.44187 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| UNSHADED ANNUAL TRANSMITTED | [20 empty] | 900-800 High Mass, Heating S. Window | -0.406 | -0.33425 | -0.411 | -0.23616 | -0.207 | -0.18847 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 900-810 High Mass, Heating Int. Sol. Abs. | #N/A | -0.056746 | -0.059 | -0.061545 | -0.062 | -0.066177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 910-610 Mass, Heating w/ S. Shade | -0.405 | -0.55173 | -0.565 | -0.49292 | -0.549 | -0.56031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | COUNTRY: | [20 empty] | 920-620 Mass, Heating w/ E&W Window | -0.25 | -0.52543 | -0.555 | -0.45894 | -0.547 | -0.52032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
kWh/m2 | CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | MIN | MAX |  | 930-630 Mass, Heating w/ E&W Shade | -0.284 | -0.5024 | -0.523 | -0.42166 | -0.494 | -0.48714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 940-640 Mass, Heating w/ Heating Setback | -0.751 | -1.1705 | -0.999 | -1.4158 | -0.979 | -0.63372 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
163 | 600 SOUTH | 820 | 825.5194 | 805.046 | 804.0205 | 813.88 | 822.589 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
166 | 620 WEST | 598 | #N/A | 569.394 | 581.0395 | 591.88 | 623.797 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
164 | 660 SOUTH, Low-E | 447 | 501.3136 | 506.461 | 435.995 | 442.7 | 448.493 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
165 | 670 SOUTH, Single Pane | 1037 | 987.8182 | 994.318 | 1024.2026 | 1028.35 | 1039.23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PEAK COOLING [KW] --Charts not created directly here; these addresses are referenced by "BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - PEAK" below
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
CASES
[22 empty] | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.881 | -0.73794 | -0.683 | -0.88353 | -0.822 | -0.76849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| SOLAR RADIATION | [20 empty] | 900-800 High Mass, Cooling S. Window | 1.753 | 2.2746 | 1.399 | 1.9946 | 1.844 | 2.0045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| SHADED ANNUAL TRANSMITTED | [20 empty] | 900-810 High Mass, Cooling Int. Sol. Abs. | #N/A | 0.96595 | 0.616 | 0.77023 | 0.717 | 0.8272 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | 910-610 Mass, Cooling w/ S. Shade | -2.973 | -3.7101 | -3.228 | -3.9124 | -3.722 | -3.7868 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CODENAME: | [20 empty] | 920-620 Mass, Cooling w/ E&W Window | -1.223 | -1.4361 | -1.245 | -1.5371 | -1.523 | -1.4341 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| COUNTRY: | [20 empty] | 930-630 Mass, Cooling w/ E&W Shade | -1.069 | -1.3365 | -1.191 | -1.4307 | -1.477 | -1.3363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
kWh/m2 | CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | MIN | MAX |  | 940-640 Mass, Cooling w/ Heating Setback | -2.492 | -3.0526 | -2.809 | -3.2574 | -3.236 | -3.0295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 950-650 Mass, Cooling w/ Night Vent | -3.282 | -3.9262 | -2.991 | -3.7506 | -3.759 | -3.5611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
170 | 610 SOUTH | 641 | 665.2609 | 663.345 | 646.1319 | 631.33 | 661.81 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
171 | 630 WEST | 438 | #N/A | 399.173 | 419.3545 | 389.67 | 445.549 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SOLAR RADIATION
ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS
CODENAME:
COUNTRY:
| CASE# | [17 empty] | MIN | MAX
0 | = | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
math | 600 SOUTH | 0.5912 | 0.62686 | 0.62378 | 0.58667 | 0.59708 | 0.59426 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
math | 620 WEST | 0.5998 | #N/A | 0.62866 | 0.6007 | 0.61578 | 0.64014 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
math | 660 SOUTH, Low-E | 0.32228 | 0.38067 | 0.39243 | 0.31813 | 0.32477 | 0.324 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
math | 670 SOUTH, Single Pane | 0.74766 | 0.7501 | 0.77043 | 0.74733 | 0.75442 | 0.75076 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SOLAR RADIATION
ANNUAL OVERHANG AND FIN SHADING COEFFICIENT
CODENAME:
COUNTRY:
| CASE# | [17 empty] | MIN | MAX
0 | test | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
math | (1 - Case610 / Case600) SOUTH | 0.21829 | 0.19413 | 0.17602 | 0.19637 | 0.2243 | 0.19545 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
math | (1 - Case630 / Case620) WEST | 0.26756 | #N/A | 0.29895 | 0.27827 | 0.34164 | 0.28575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SKY TEMPERATURE, CASE 600
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
178 | Average | #N/A | -3.9307 | -5.9 | -2.0216 | -5.17 | -5.0587 | -5.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
178 | Minimum | #N/A | -46.2246 | -46.85 | -37.9798 | -46.9 | -46.1617 | -46.85 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
178 | Maximum | #N/A | 30.0812 | 24.62 | 24.7268 | 26.7 | 26.0293 | 24.62 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | NOT USED TO GENERATE CHARTS |  |  |  |  | NOT USED TO GENERATE CHARTS |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS
[34 empty] | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
[22 empty] | ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [11 empty] | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | RANGE | RANGE
[22 empty] | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | MIN | MAX
[22 empty] | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | JAN 04 | 2 | 4.307 | 1904-01-01 | 2 | 4.037 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.354 | JAN 04 | 2 |  |  |  | 3.437 | 4.354
[22 empty] | CASE# | KW | DATE | HR | HR | KW | DATE | HR | KW | DATE | HR | KW | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.037 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.354 | JAN 04 | 2 |  |  |  | 3.437 | 4.354
[22 empty] | 600 | 3.437 | 1993-01-04 | 5 | 5 | 3.94 | JAN 04 | 5 | 4.045 | JAN 04 | 5 | 4.258 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.277 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 |  |  |  | 3.591 | 4.379
[22 empty] | 610 | 3.437 | 1993-01-04 | 5 | 5 | 3.941 | JAN 04 | 5 | 4.034 | JAN 04 | 5 | 4.258 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.278 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 |  |  |  | 3.592 | 4.278
[22 empty] | 620 | 3.591 | 1993-01-04 | 6 | 6 | 3.941 | JAN 04 | 5 | 4.046 | JAN 04 | 5 | 4.277 | JAN 04 | 8 | 8.078 | 1904-01-01 | 8 | 6.347 | JAN 04 | 8 | 5.7222 | Jan-04 | 8 | 6.954 | JAN 04 | 8 |  |  |  | 5.232 | 6.954
[22 empty] | 630 | 3.592 | 1993-01-04 | 7 | 7 | 3.941 | JAN 04 | 5 | 4.025 | JAN 04 | 5 | 4.28 | USA KW: 0; UK-BRE KW: 0; SPAIN KW: 0; BEL/UK KW: 0
[22 empty] | 640 | 5.232 | 1993-01-04 | 7 | 7 | 5.486 | JAN 04 | 8 | 5.943 | JAN 04 | 8 | 6.53 | JAN 04 | 7 | 4.081 | 1904-01-01 | 7 | 3.608 | JAN 04 | 8 | 3.5167 | Jan-04 | 7 | 3.797 | JAN 04 | 7 |  |  |  | 2.85 | 3.797
[22 empty] | 650 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 | JAN 04 | 7 | 4.083 | 1904-01-01 | 7 | 3.618 | JAN 04 | 8 | 3.5361 | Jan-04 | 7 | 3.801 | JAN 04 | 7 |  |  |  | 2.858 | 3.801
[22 empty] | 900 | 2.85 | 1993-01-04 | 7 | 7 | 3.453 | JAN 04 | 7 | 3.557 | JAN 04 | 7 | 3.76 | JAN 04 | 7 | 4.156 | 1904-01-01 | 7 | 4.029 | JAN 04 | 7 | 3.7083 | Jan-04 | 7 | 4.061 | JAN 04 | 7 |  |  |  | 3.308 | 4.061
[22 empty] | 910 | 2.858 | 1993-01-04 | 7 | 7 | 3.456 | JAN 04 | 7 | 3.564 | JAN 04 | 7 | 3.764 | JAN 04 | 7 | 4.165 | 1904-01-01 | 7 | 4.064 | JAN 04 | 7 | 3.7444 | Jan-04 | 7 | 4.188 | JAN 04 | 8 |  |  |  | 3.355 | 4.064
[22 empty] | 920 | 3.308 | 1993-01-04 | 7 | 7 | 3.703 | JAN 04 | 7 | 3.805 | JAN 04 | 7 | 4.013 | JAN 04 | 8 | 9.923 | 1904-01-01 | 8 | 6.117 | JAN 04 | 8 | 5.1222 | Jan-03 | 9 | 6.428 | JAN 04 | 8 |  |  |  | 3.98 | 6.428
[22 empty] | 930 | 3.355 | 1993-01-04 | 7 | 7 | 3.732 | JAN 04 | 7 | 3.832 | JAN 04 | 7 | 4.042 | USA KW: 0; UK-BRE KW: 0; SPAIN KW: 0; BEL/UK KW: 0
| HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MAY 4 | [20 empty] | 940 | 3.98 | 1993-01-04 | 7 | 7 | 5.028 | JAN 04 | 8 | 5.665 | JAN 04 | 8 | 6.116 | JAN 04 | 8 | 2.896 | 1904-01-01 | 8 | 2.852 | JAN 04 | 8 | 2.522 | Jan-04 | 8 | 2.779 | JAN 04 | 8 |  |  |  | 2.41 | 2.896
| CASE 600 OR 900 | [20 empty] | 950 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 | USA DATE: JAN 04; USA HR: 7; USA KW: 3.738; UK-BRE DATE: Feb-06; UK-BRE HR: 2; UK-BRE KW: 3.799; SPAIN DATE: JAN 04; SPAIN HR: 8; BEL/UK KW: 4.296; FINLAND DATE: JAN 04; FINLAND HR: 7
| SOUTH SURFACE | [20 empty] | 960 | 2.41 | 1993-01-04 | 7 | 7 | 2.751 | JAN 04 | 8 | 2.727 | JAN 04 | 8 | 2.863 | JAN 04 | 3 | 2.235 | 1904-01-01 | 3 | 2.221 | JAN 04 | 4 | 2.1856 | Jan-04 | 3 | 2.263 | JAN 04 | 3
| (USE COLUMN B ONLY) | [20 empty] | 990 | 2.769 | 1993-02-06 | 2 | 2 | 3.734 | JAN 04 | 7 | 3.427 | JAN 04 | 7 | 3.681 |  |  | 3.047 | 1904-01-01 | 3 | 2.999 | JAN 04 | 2 | 2.9694 | Jan-04 | 5 | 3.382 | JAN 04 | 2
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 195 | 2.004 | 1993-01-04 | 2 | 2 | 2.186 | JAN 04 | 8 | 2.32 | JAN 04 | 3 | 2.385 |  |  | 3.077 | 1904-01-01 | 3 | 3.02 | JAN 04 | 2 | 2.9806 | Jan-04 | 5 | 3.325 | JAN 04 | 2
0 | COUNTRY: | [20 empty] | 200 | 2.651 | 1993-01-04 | 5 | 5 | 2.973 | JAN 04 | 5 | [6 empty] | 3.65 | 1904-01-01 | 2 | 3.307 | JAN 04 | 6 | 3.2944 | Jan-04 | 6 | 3.458 | JAN 04 | 8
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210 | 2.701 | 1993-01-04 | 5 | 5 | 2.973 | JAN 04 | 5 |  |  |  |  | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.348 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 215 | 2.787 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 |  |  |  |  | JAN 04 | 2 | 5.293 | 1904-01-01 | 2 | 5.159 | JAN 04 | 2 | 4.8917 | Jan-04 | 6 | 5.107 | JAN 04 | 2
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 220 | 2.867 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 3.509 | 1904-01-01 | 2 | 3.159 | JAN 04 | 8 | 3.1528 | Jan-04 | 6 | 3.333 | JAN 04 | 8
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 230 | 4.386 | 1993-01-04 | 5 | 5 | 4.984 | JAN 04 | 2 | 4.994 | JAN 04 | 2 | 5.279 | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.525 | JAN 04 | 2
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 240 | 2.685 | 1993-01-04 | 5 | 5 | 3.1 | JAN 04 | 5 | 3.282 | JAN 04 | 5 | 3.495 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.738 | JAN 04 | 2
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 250 | 2.866 | 1993-01-04 | 5 | 5 | 3.279 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.759 | JAN 04 | 2
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 270 | 2.863 | 1993-01-04 | 5 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.67 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3278 | Jan-04 | 6 | 3.738 | JAN 04 | 2
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 280 | 2.864 | 1993-01-04 | 5 | 5 | 3.278 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.599 | JAN 04 | 5 | 3.3278 | Jan-04 | 6 | 3.77 | JAN 04 | 2
235 | 6 | 9.31 | 9.0004 | 9 | 10.9831 | 9.22 | 7.7154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 290 | 2.863 | 1993-01-04 | 5 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.67 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.599 | JAN 04 | 5 | 3.3278 | Jan-04 | 6 | 3.771 | JAN 04 | 2
236 | 7 | 36.36 | 36.0015 | 36 | 33.8229 | 31.59 | 31.2881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 300 | 3.014 | 1993-01-04 | 6 | 6 | 3.276 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.735 | JAN 04 | 3
237 | 8 | 66.16 | 66.6028 | 66.6 | 59.9654 | 57.22 | 58.0581 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 310 | 3.015 | 1993-01-04 | 6 | 6 | 3.277 | JAN 04 | 5 |  |  |  | 3.672 | JAN 04 | 3 | 2.391 | 1904-01-01 | 3 | 2.263 | JAN 04 | 4 | 2.2211 | Jan-04 | 8 | 2.27 | JAN 04 | 3
238 | 9 | 93.88 | 94.8038 | 94.8 | 84.3926 | 82.11 | 83.1431 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 320 | 2.861 | 1993-01-04 | 5 | 5 | 3.275 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.342 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2
239 | 10 | 116.03 | 117.0048 | 117 | 108.1146 | 105.56 | 103.6598 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 395 | 2.062 | 1993-01-04 | 7 | 7 | 2.209 | JAN 04 | 8 | 2.328 | JAN 04 | 3 | 2.385 | JAN 04 | 2 | 4.501 | 1904-01-01 | 2 | 4.227 | JAN 04 | 2 | 4.1139 | Jan-04 | 6 | 4.314 | JAN 04 | 2
240 | 11 | 156.44 | 157.8065 | 157.8 | 139.6057 | 137.73 | 141.3514 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 400 | 2.867 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 | 3.476 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 4.301 | 1904-01-01 | 2 | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.126 | JAN 04 | 2
241 | 12 | 165.66 | 166.8069 | 166.8 | 149.4359 | 149.3 | 150.3411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 410 | 3.625 | 1993-01-04 | 5 | 5 | 4.124 | JAN 04 | 5 | 4.233 | JAN 04 | 5 | 4.487 | JAN 04 | 2 | 4.301 | 1904-01-01 | 2 | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.137 | JAN 04 | 2
242 | 13 | 165.04 | 166.2068 | 166.2 | 147.9223 | 148.6 | 149.7167 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 420 | 3.443 | 1993-01-04 | 5 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.041 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.376 | JAN 04 | 2
243 | 14 | 154 | 155.4066 | 155.4 | 136.7123 | 137.97 | 138.9957 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 134.48 | 136.2054 | 136.2 | 117.6082 | 119.2 | 120.4472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 430 | 3.442 | 1993-01-04 | 5 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 | 4.188 | 1904-01-01 | 8 | 3.902 | JAN 04 | 8 | 3.7861 | Jan-04 | 7 | 3.939 | JAN 04 | 7
245 | 16 | 106.77 | 108.6046 | 108.6 | 90.0007 | 92.17 | 94.7457 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 440 | 3.439 | 1993-01-04 | 5 | 5 | 3.942 | JAN 04 | 5 |  |  |  | 4.277 | JAN 04 | 7 | 4.115 | 1904-01-01 | 7 | 3.709 | JAN 04 | 8 | 3.6056 | Jan-04 | 7 | 3.963 | JAN 04 | 7
246 | 17 | 62.05 | 62.4026 | 62.4 | 53.2617 | 55.39 | 54.3851 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 800 | 3.227 | 1993-01-04 | 5 | 5 | 3.793 | JAN 04 | 7 | 3.909 | JAN 04 | 7 | 4.138
247 | 18 | 32.2 | 31.8013 | 31.8 | 26.165 | 28.16 | 27.594 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 810 | 2.979 | 1993-01-04 | 7 | 7 | 3.566 | JAN 04 | 7 |  |  |  | 3.915 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
248 | 19 | 6.81 | 6.6003 | 6.6 | 5.4293 | 7.34 | 5.6434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA; RANGE MIN: RANGE; RANGE MAX: RANGE
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | KW | DATE | HR | KW | DATE | HR | MIN | MAX
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | OCT 16 | 14 | 7.551 | 1916-10-01 | 13 | 6.286 | NOV 25 | -6.194 | 6.4861 | Oct-16 | 14 | 6.812 | OCT 17 | 14 |  |  |  | 5.965 | 6.812
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASE# | KW | DATE | HR | HR | KW | DATE | HR | KW | DATE | HR | KW | NOV 25 | 14 | 7.215 | 1925-11-01 | 13 | 6.17 | NOV 25 | -5.669 | 5.675 | 1992-11-25 | 14 | 6.146 | OCT 17 | 14 |  |  |  | 5.669 | 6.146
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 600 | 6.194 | 1993-10-17 | 13 | 13 | 5.965 | OCT 16 | 14 | 6.656 | OCT 16 | 13 | 6.827 | JUL 26 | 17 | 4.959 | 1902-07-01 | 10 | 4.297 | JUL 26 | -3.634 | 4.275 | 1992-07-26 | 17 | 5.096 | JUL 26 | 16 |  |  |  | 3.634 | 5.096
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 610 | 5.669 | 1993-11-25 | 13 | 13 | 5.824 | NOV 25 | 14 | 6.064 | JAN 13 | 14 | 6.371 | JUL 26 | 17 | 4.4 | 1902-07-01 | 9 | 3.665 | JUL 26 | -3.072 | 3.6083 | 1992-07-26 | 17 | 3.546 | JUN 30 | 17 |  |  |  | 3.072 | 3.704
| = | = | = | = | = | = | = | = | = | [12 empty] | 620 | 3.634 | 1993-07-26 | 16 | 16 | 4.075 | JUL 26 | 17 | 4.43 | JUL 26 | 17 | 4.593 | OCT 16 | 14 | 7.537 | 1916-10-01 | 13 | 6.25 | NOV 25 | -6.161 | 6.4417 | Oct-16 | 14 | 6.771 | OCT 17 | 14
[22 empty] | 630 | 3.072 | 1993-07-26 | 16 | 16 | 3.704 | JUL 26 | 17 | 3.588 | JUL 26 | 17 | 4.116 | OCT 16 | 14 | 7.458 | 1916-10-01 | 13 | 6.143 | NOV 25 | -6.031 | 6.3778 | Oct-17 | 14 | 6.679 | OCT 17 | 14 |  |  |  | 5.831 | 6.679
[22 empty] | 640 | 6.161 | 1993-10-17 | 13 | 13 | 5.892 | OCT 16 | 14 | 6.576 | OCT 16 | 14 | 6.776 | OCT 17 | 14 | 4.901 | 1917-10-01 | 14 | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 |  |  |  | 2.888 | 3.5667
[22 empty] | 650 | 6.031 | 1993-10-17 | 13 | 13 | 5.831 | OCT 16 | 14 | 6.516 | OCT 16 | 14 | 6.671 | OCT 17 | 15 | 3.973 | 1917-10-01 | 15 | 2.786 | OCT 17 | -1.896 | 2.7917 | Oct-17 | 15 | 3.147 | OCT 17 | 15 |  |  |  | 1.896 | 3.147
[22 empty] | 900 | 2.888 | 1993-10-17 | 14 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | JUL 26 | 17 | 3.777 | 1926-07-01 | 17 | 3.071 | JUL 26 | -2.385 | 3.05 | 1992-07-26 | 17 | 3.505 | JUL 26 | 17 |  |  |  | 2.385 | 3.505
[22 empty] | 910 | 1.896 | 1993-10-17 | 15 | 15 | 2.5 | OCT 21 | 15 | 2.336 | OCT 17 | 15 | 3.277 | JUL 26 | 17 | 3.203 | 1926-07-01 | 17 | 2.486 | JUL 26 | -1.873 | 2.4983 | 1992-07-26 | 17 | 2.304 | JUN 30 | 17 |  |  |  | 1.873 | 2.546
[22 empty] | 920 | 2.385 | 1993-07-26 | 16 | 16 | 2.933 | JUL 26 | 17 | 3.109 | JUL 26 | 17 | 3.487 | OCT 17 | 14 | 4.901 | 1917-10-01 | 14 | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15
[22 empty] | 930 | 1.873 | 1993-07-26 | 17 | 17 | 2.546 | JUL 26 | 17 | 2.388 | JUL 26 | 18 | 3.08 | SEP 02 | 14 | 3.848 | 1902-09-01 | 15 | 2.677 | SEP 02 | -2.033 | 2.6861 | Sep-02 | 15 | 2.867 | SEP 02 | 14 |  |  |  | 2.033 | 2.867
| HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MAY 4 | [20 empty] | 940 | 2.888 | 1993-10-17 | 14 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | JUL 26 | 16 | 1.306 | 1926-07-01 | 16 | 1.179 | JUL 26 | 16 | 1.378 | 1992-07-26 | 16 | 1.403 | JUL 26 | 16 |  |  |  | 0.953 | 1.403
| CASE 600 OR 900 | [20 empty] | 950 | 2.033 | 1993-09-02 | 14 | 14 | 2.621 | SEP 02 | 15 | 2.664 | SEP 2 | 15 | 3.17 | USA DATE: SEP 02; USA HR: 14; USA KW: 3.525; UK-BRE DATE: 1917-10-01; UK-BRE HR: 14; UK-BRE KW: 1.859; SPAIN DATE: NOV 25; SPAIN HR: 14; BEL/UK KW: 2.779; FINLAND DATE: SEP 02; FINLAND HR: 14
| WEST SURFACE | [20 empty] | 960 | 0.953 | 1993-08-16 | 16 | 16 | 1.144 | JUL 26 | 16 | 1.057 | JUL 26 | 16 | 1.37 | JUL 26 | 16 | 0.806 | 1926-07-01 | 16 | 0.799 | JUL 26 | -0.651 | 0.79139 | 1992-07-26 | 16 | 0.79 | JUL 26 | 16
| (USE COLUMN B ONLY) | [20 empty] | 990 | 2.422 | 1993-10-17 | 14 | 14 | 2.912 | SEP 02 | 14 | 3.436 | OCT 17 | 13 | 2.819 |  |  | 1.111 | 1926-07-01 | 15 | 1.105 | JUL 26 | -0.863 | 1.1006 | 1992-07-26 | 16 | 1.126 | JUL 26 | 15
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 195 | 0.651 | 1993-07-26 | 15 | 15 | 0.728 | JUL 26 | 16 | 0.616 | JUL 27 | 15 | 0.853 |  |  | 1.101 | 1926-07-01 | 15 | 1.097 | JUL 26 | -0.476 | 1.0678 | 1992-07-26 | 16 | 1.142 | JUL 26 | 15
0 | COUNTRY: | [20 empty] | 200 | 0.863 | 1993-08-16 | 14 | 14 | 1.017 | JUL 26 | 15 | [6 empty] | 1.347 | 1926-07-01 | 15 | 1.216 | JUL 26 | -1.007 | 1.1836 | 1992-07-26 | 16 | 1.192 | JUL 26 | 15
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210 | 0.476 | 1993-08-16 | 16 | 16 | 1.017 | JUL 26 | 15 |  |  |  |  | JUL 26 | 15 | 1.342 | 1926-07-01 | 15 | 1.215 | JUL 26 | -0.56 | 1.1789 | 1992-07-26 | 16 | 1.213 | JUL 26 | 15
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 215 | 1.007 | 1993-08-11 | 14 | 14 | 1.166 | JUL 26 | 15 |  |  |  |  | JUL 26 | 15 | 1.878 | 1926-07-01 | 15 | 1.7 | JUL 26 | -1.059 | 1.7078 | 1992-07-26 | 16 | 1.749 | JUL 26 | 15
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 220 | 0.56 | 1993-07-27 | 15 | 15 | 1.166 | JUL 26 | 15 | 0.937 | JUL 27 | 14 | 1.34 | JUL 26 | 15 | 1.542 | 1926-07-01 | 15 | 1.398 | JUL 26 | -0.739 | 1.3614 | 1992-07-26 | 16 | 1.397 | JUL 26 | 15
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 230 | 1.059 | 1993-07-27 | 15 | 15 | 1.646 | JUL 26 | 15 | 1.455 | JUL 27 | 14 | 1.875 | AUG 26 | 14 | 2.582 | 1911-08-01 | 12 | 2.258 | AUG 26 | -3.36 | 3.2278 | Sep-05 | 13 | 4.912 | SEP 05 | 12
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 240 | 0.739 | 1993-07-27 | 15 | 15 | 1.347 | JUL 26 | 15 | 1.119 | JUL 27 | 14 | 1.54 | OCT 16 | 14 | 7.967 | 1925-11-01 | 13 | 6.819 | NOV 25 | -6.356 | 6.7639 | Oct-17 | 14 | 6.867 | OCT 16 | 14
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 250 | 3.36 | 1993-09-05 | 12 | 12 | 3.036 | SEP 05 | 12 | 2.605 | SEP 5 | 11 | 2.59 | OCT 16 | 14 | 5.759 | 1916-10-01 | 13 | 4.63 | NOV 25 | -4.444 | 4.7861 | Oct-16 | 14 | 5.236 | OCT 16 | 14
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 270 | 6.356 | 1993-11-25 | 13 | 13 | 6.641 | NOV 25 | 14 |  |  |  | 7.163 | NOV 25 | 14 | 7.793 | 1923-12-01 | 13 | 6.7 | NOV 25 | -6.269 | 6.2028 | 1992-11-25 | 14 | 6.621 | NOV 25 | 14
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 280 | 4.444 | 1993-10-17 | 13 | 13 | 4.631 | NOV 25 | 13 |  |  |  | 5.22 | JUL 26 | 17 | 5.072 | 1902-07-01 | 10 | 4.336 | JUL 26 | -3.404 | 4.2778 | 1992-07-26 | 17 | 4.929 | JUL 26 | 17
235 | 6 | 9.31 | 9.0004 | 9 | 10.9831 | 9.22 | 7.7154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 290 | 6.269 | 1993-01-13 | 13 | 13 | 6.555 | NOV 25 | 14 |  |  |  | 6.91 | JUL 26 | 17 | 4.666 | 1902-07-01 | 9 | 3.669 | JUL 26 | -2.848 | 3.5889 | 1992-07-26 | 17 | 3.425 | JUN 30 | 17
236 | 7 | 36.36 | 36.0015 | 36 | 33.8229 | 31.59 | 31.2881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 300 | 3.404 | 1993-07-26 | 16 | 16 | 4.093 | JUL 26 | 17 |  |  |  | 4.642 | OCT 16 | 14 | 7.332 | 1925-11-01 | 13 | 6.183 | NOV 25 | -5.701 | 6.1778 | Oct-17 | 14 | 6.141 | OCT 16 | 14
237 | 8 | 66.07 | 66.6028 | 66.6 | 59.7762 | 56.9 | 57.9409 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 310 | 2.848 | 1993-07-26 | 16 | 16 | 3.749 | JUN 30 | 17 |  |  |  | 4.186 | JUL 26 | 17 | 0.421 | 1926-07-01 | 16 | 0.356 | JUL 26 | 18 | 0.3625 | 1992-07-26 | 18 | 0.345 | JUL 26 | 18
238 | 9 | 92.71 | 94.8038 | 94.8 | 83.0745 | 80.12 | 81.9063 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 320 | 5.701 | 1993-11-25 | 13 | 13 | 5.946 | NOV 25 | 14 |  |  |  | 6.484 | JUL 26 | 16 | 0.712 | 1926-07-01 | 15 | 0.612 | JUL 26 | 17 | 0.61333 | 1992-07-26 | 17 | 0.572 | JUL 26 | 17
239 | 10 | 113.11 | 117.0048 | 117 | 104.629 | 100.9 | 100.6192 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 395 | 0 |  |  |  | 0.362 | JUL 26 | 18 | 0 |  |  | 0.394 | JUL 26 | 15 | 0.863 | 1926-07-01 | 15 | 0.724 | JUL 26 | -0.035 | 0.74306 | 1992-07-26 | 17 | 0.71 | JUL 26 | 17
240 | 11 | 148.79 | 157.8065 | 157.8 | 132.0397 | 128.06 | 133.4601 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 400 | 0 |  |  |  | 0.581 | JUL 26 | 17 | 0.265 | JUL 27 | 17 | 0.666 | JUL 26 | 15 | 1.078 | 1926-07-01 | 15 | 0.938 | JUL 26 | -0.258 | 0.93778 | 1992-07-26 | 16 | 0.921 | JUL 26 | 15
241 | 12 | 158.81 | 166.8069 | 166.8 | 140.236 | 137.41 | 140.7836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 410 | 0.035 | 1993-07-27 | 16 | 16 | 0.699 | JUL 26 | 17 | 0.413 | JUL 27 | 17 | 0.814 | JUL 26 | 15 | 1.779 | 1911-08-01 | 13 | 1.575 | JUL 26 | -1.493 | 1.7983 | 1992-09-05 | 13 | 2.578 | SEP 05 | 12
242 | 13 | 159.18 | 166.2068 | 166.2 | 142.6342 | 141.06 | 143.6691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 420 | 0.258 | 1993-07-27 | 15 | 15 | 0.923 | JUL 26 | 15 | 0.631 | JUL 27 | 15 | 1.047 | OCT 16 | 14 | 5.615 | 1916-10-01 | 13 | 4.465 | OCT 16 | -4.546 | 4.6861 | Oct-16 | 14 | 5.278 | OCT 17 | 14
243 | 14 | 154.61 | 155.4066 | 155.4 | 137.7338 | 138.78 | 139.5313 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 140.01 | 136.2054 | 136.2 | 123.3077 | 126.87 | 126.0353 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 430 | 1.493 | 1993-08-16 | 14 | 14 | 1.772 | AUG 26 | 14 | 1.427 | AUG 16 | 14 | 1.762 | JUL 27 | 14 | 1.382 | 1927-07-01 | 14 | 1.028 | JUL 27 | -0.585 | 0.98278 | Aug-16 | 14 | 1.358 | SEP 05 | 12
245 | 16 | 114.38 | 108.6046 | 108.6 | 96.8707 | 103.03 | 102.5145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 440 | 4.546 | 1993-10-17 | 13 | 13 | 4.424 | OCT 16 | 14 |  |  |  | 5.053 | SEP 02 | 14 | 3.624 | 1902-09-01 | 14 | 2.432 | SEP 02 | -1.852 | 2.3436 | Sep-02 | 14 | 2.862 | SEP 02 | 14
246 | 17 | 63.55 | 62.4026 | 62.4 | 54.9349 | 61.13 | 56.0031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 800 | 0.585 | 1993-07-27 | 14 | 14 | 0.967 | AUG 16 | 14 | 0.743 | JUL 28 | 14 | 1.352
247 | 18 | 32.2 | 31.8013 | 31.8 | 26.165 | 28.89 | 27.594 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 810 | 1.852 | 1993-09-02 | 14 | 14 | 2.357 | AUG 26 | 14 |  |  |  | 2.991
248 | 19 | 6.81 | 6.6003 | 6.6 | 5.4293 | 7.34 | 5.6434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | FREE-FLOAT TEMPERATURE OUTPUT | [11 empty] | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | OCT 16 | 15 | 69.81 | 1916-10-01 | 16 | 64.9 | OCT 16 | 16 | 65.25 | Oct-17 | 16 | 65.25 | OCT 15 | 16
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASE# | TMP (C) | DATE | HR | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | SEP 02 | 15 | 43.44 | 1902-09-01 | 16 | 43 | SEP 02 | 15 | 42.46 | Oct-17 | 15 | 43.17 | SEP 15 | 15
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 600FF | 64.929 | 1993-10-17 | 15 | 15 | 65.11 | OCT 16 | 15 | 69.5 | OCT 17 | 15 | 68.6 | OCT 16 | 15 | 68.49 | 1916-10-01 | 16 | 63.3 | OCT 16 | 16 | 63.74 | Oct-17 | 16 | 63.82 | OCT 16 | 16
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 900FF | 41.812 | 1993-10-17 | 15 | 15 | 43.44 | SEP 02 | 16 | 42.7 | SEP 02 | 15 | 44.8 | SEP 02 | 15 | 35.65 | 1902-09-01 | 16 | 36.1 | SEP 02 | 16 | 35.67 | Sep-02 | 15 | 37.58 | SEP 15 | 16
[22 empty] | 650FF | 63.236 | 1993-10-17 | 15 | 15 | 63.45 | OCT 16 | 15 | 68.2 | OCT 17 | 15 | 67 | OCT 17 | 15 | 51.21 | 1917-10-01 | 16 | 50.2 | OCT 17 | 15 | 55.34 | Oct-17 | 15 | 48.92 | OCT 15 | 15
[22 empty] | 950FF | 35.54 | 1993-09-02 | 16 | 16 | 36.23 | SEP 02 | 16 | 35.9 | SEP 02 | 16 | 38.5
[22 empty] | 960 | 48.943 | 1993-10-17 | 15 | 15 | 48.88 | OCT 06 | 15 | 49 | OCT 17 | 15 | 51 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
[22 empty] | MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
[22 empty] | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR
[22 empty] | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | JAN 04 | 7 | -9.96 | 1920-01-01 | 24 | -17.8 | JAN 04 | 8 | -17.81 | Jan-04 | 7 | -18.47 | JAN 08 | 9
[22 empty] | CASE# | TMP (C) | DATE | HR | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | JAN 04 | 8 | -3.94 | 1904-01-01 | 8 | -4 | JAN 04 | 8 | -6.38 | Jan-04 | 8 | -5.64 | JAN 08 | 9
| HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 14 | [20 empty] | 600FF | -15.565 | 1993-01-04 | 7 | 7 | -17.05 | JAN 04 | 8 | -18.8 | JAN 04 | 8 | -18 | JAN 04 | 2 | -9.97 | 1916-01-01 | 6 | -22.9 | JAN 04 | 2 | -22.83 | Jan-04 | 7 | -22.91 | JAN 02 | 23
| CASE 600 | [20 empty] | 900FF | -1.647 | 1993-01-04 | 8 | 8 | -3.15 | JAN 04 | 8 | -4.3 | JAN 04 | 8 | -4.5 | JAN 04 | 7 | -9.83 | 1908-12-01 | 1 | -20.2 | JAN 04 | 7 | -19.34 | Jan-04 | 7 | -19.96 | JAN 07 | 22
| SOUTH SURFACE | [20 empty] | 650FF | -22.564 | 1993-01-04 | 6 | 6 | -22.96 | JAN 04 | 7 | -21.6 | JAN 04 | 2 | -23 | FEB 06 | 7 | 2.22 | 1906-02-01 | 7 | 1.4 | FEB 06 | 6 | -2.82 | Jan-04 | 8 | -0.39 | FEB 05 | 7
| (USE COLUMN B ONLY) | [20 empty] | 950FF | -19.484 | 1993-01-04 | 6 | 6 | -20.04 | JAN 04 | 7 | -18.6 | JAN 04 | 7 | -19.7
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 960 | 2.729 | 1993-02-06 | 6 | 6 | 1.63 | FEB 06 | 7 | 3.9 | FEB 06 | 7 | 3.1 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
0 | COUNTRY: | [20 empty] | AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | USA KW: TMP (C); UK-BRE KW: TMP (C); SPAIN KW: TMP (C); BEL/UK KW: TMP (C); FINLAND KW: TMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | USA KW: 25.93; UK-BRE KW: 25.2; SPAIN KW: 24.49; BEL/UK KW: 24.22
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | CASE# | TMP (C) |  |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) | USA KW: 25.72; UK-BRE KW: 25.2; SPAIN KW: 24.47; BEL/UK KW: 24.45
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 600FF | 25.126 |  |  |  | 25.43 |  |  | 24.6 |  |  | 25.48 | USA KW: 19.62; UK-BRE KW: 18.4; SPAIN KW: 17.99; BEL/UK KW: 18.36
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 900FF | 25.453 |  |  |  | 25.93 |  |  | 24.7 |  |  | 25.49 | USA KW: 14.29; UK-BRE KW: 14; SPAIN KW: 14.53; BEL/UK KW: 14.64
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 650FF | 18.234 |  |  |  | 18.69 |  |  | 19.1 |  |  | 18.96 | USA KW: 28.54; UK-BRE KW: 28; SPAIN KW: 28.96; BEL/UK KW: 26.43
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 950FF | 14.14 |  |  |  | 14.26 |  |  | 14.3 |  |  | 14.97
234 | 5 | 0 | 0.54029 | 0.7 | 2.825 | 1.27 | 1.0886 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 960 | 27.49 |  |  |  | 27.72 |  |  | 28 |  |  | 28.69
235 | 6 | 25.87 | 15.3297 | 20.5 | 27.0562 | 24.28 | 25.7932 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 52.6 | 34.4328 | 46 | 55.3885 | 52.29 | 53.3893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 79.83 | 55.5566 | 73.4 | 82.404 | 79.31 | 80.1937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - ANNUAL
238 | 9 | 166.73 | 139.4762 | 164.1 | 179.1211 | 166.72 | 178.5571 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | ANNUAL HEATING AND ANNUAL SENSIBLE COOLING [MWH]
239 | 10 | 296.45 | 272.6453 | 294.38 | 305.7869 | 295.8 | 304.6694 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
240 | 11 | 390.91 | 372.0415 | 390.75 | 396.7139 | 390.25 | 398.8477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
241 | 12 | 441.65 | 427.7583 | 443.74 | 443.5116 | 441.16 | 449.7855 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.03 | -0.54834 | -0.551 | -0.50457 | -0.5651 | -0.48107 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
242 | 13 | 445.59 | 433.4522 | 448.17 | 442.6572 | 444.52 | 452.8075 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.611 | -0.52633 | -0.582 | -0.48209 | -0.5613 | -0.45694 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
243 | 14 | 401.73 | 389.6588 | 403.38 | 394.8902 | 400.86 | 408.8874 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 900-600 Mass, Heating | -2.324 | -2.6139 | -2.456 | -2.6607 | -2.7773 | -2.6895 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
244 | 15 | 312.89 | 300.3721 | 314 | 303.1678 | 312.83 | 320.8144 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 900-600 Mass, Cooling | -3.108 | -3.4493 | -3.049 | -3.5383 | -3.6741 | -3.5124 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
245 | 16 | 187.67 | 174.1119 | 189.16 | 175.5288 | 187.96 | 197.5898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 940-640 Mass, Heating w/ Heating Setback | -1.293 | -1.54 | -1.47 | -1.5945 | -1.6397 | -1.4836 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
246 | 17 | 83.9 | 64.3006 | 77.4 | 81.5142 | 85.41 | 83.9625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 950-650 Mass, Cooling w/ Night Vent | -4.043 | -4.0559 | -3.568 | -4.1099 | -4.2891 | -3.9907 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
247 | 18 | 57.72 | 39.0057 | 50.1 | 54.8088 | 56.38 | 57.4921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 30.17 | 18.8437 | 23.9 | 26.2621 | 28.15 | 29.6492 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 1.841 | 2 | 2.3496 | 3.31 | 3.1157 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - PEAK
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | PEAK HEATING AND SENSIBLE COOLING [MWH]
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 800-430 Mass, Heating w/ High Cond. Wall El. | -0.343 | -0.47625 | -0.496 | -0.3926 | -0.445 | -0.44187 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 800-430 Mass, Cooling w/ High Cond. Wall El. | -0.881 | -0.73794 | -0.683 | -0.88353 | -0.822 | -0.76849 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 900-600 Mass, Heating | -0.704 | -0.57684 | -0.582 | -0.51694 | -0.595 | -0.58042 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 900-600 Mass, Cooling | -2.611 | -3.1046 | -2.866 | -3.3111 | -3.297 | -3.1057 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 940-640 Mass, Heating w/ Heating Setback | -0.751 | -1.1705 | -0.999 | -1.4158 | -0.979 | -0.63372 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 950-650 Mass, Cooling w/ Night Vent | -3.282 | -3.9262 | -2.991 | -3.7506 | -3.759 | -3.5611 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
BESTEST IN-DEPTH CASES 195 TO 220 DELTA CHART - ANNUAL
| HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 14 | [20 empty] | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
| CASE 600 | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
| WEST SURFACE | [20 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
| (USE COLUMN B ONLY) | [20 empty] | 200-195 Heating Surface Convection | 0.824 | 0.82337 | 1.069 | 1.0358 | 0.9695 | 1.0489 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 200-195 Cooling Surface Convection | 0.127 | 0.19471 | 0.207 | 0.20256 | 0.1894 | 0.19691 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 | COUNTRY: | [20 empty] | 210-200 Heating Ext IR (Int IR "off") | 0.586 | 1.1529 | 1.305 | 0.94118 | 1.3967 | 1.2866 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210-200 Cooling Ext IR (Int IR "off") | -0.151 | -0.29717 | -0.339 | -0.25418 | -0.2819 | -0.32926 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 220-215 Heating Ext IR (Int IR "on") | 0.725 | 1.3597 | 1.481 | 1.0497 | 1.5446 | 1.4244 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 220-215 Cooling Ext IR (Int IR "on") | -0.149 | -0.33519 | -0.372 | -0.26756 | -0.3186 | -0.35281 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 215-200 Heating Int IR (Ext IR "off") | 0.611 | 0.49316 | 0.471 | 0.30004 | 0.2607 | 0.30051 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 220-210 Heating Int IR (Ext IR "on") | 0.75 | 0.70003 | 0.647 | 0.40857 | 0.4086 | 0.43834 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0.54029 | 0.7 | 2.825 | 1.27 | 1.0886 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST IN-DEPTH CASES 195 TO 220 DELTA CHART - PEAK
235 | 6 | 25.87 | 15.3297 | 20.5 | 27.0562 | 24.28 | 25.7932 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | PEAK HEATING AND SENSIBLE COOLING [MWH]
236 | 7 | 52.6 | 34.4328 | 46 | 55.3885 | 52.29 | 53.3893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
237 | 8 | 79.83 | 55.5479 | 73.4 | 81.9746 | 78.93 | 80.1937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
238 | 9 | 101.35 | 75.5077 | 98.8 | 104.1185 | 101.39 | 102.9649 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 200-195 Heating Surface Convection | 0.47 | 0.43534 | 0.509 | 0.54692 | 0.473 | 0.5568 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
239 | 10 | 117.44 | 91.9039 | 119.2 | 119.4839 | 117.25 | 118.7803 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 200-195 Cooling Surface Convection | 0.153 | 0.22092 | 0.266 | 0.26648 | 0.254 | 0.26541 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
240 | 11 | 126.74 | 103.7499 | 133.6 | 128.2458 | 126.5 | 127.9971 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 210-200 Cooling Ext IR (Int IR "off") | -0.078 | -0.26955 | -0.302 | -0.22309 | -0.321 | -0.37477 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
241 | 12 | 130.36 | 110.2849 | 141.3 | 131.5461 | 130.19 | 131.6306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 220-215 Cooling Ext IR (Int IR on) | -0.057 | -0.26079 | -0.346 | -0.2159 | -0.354 | -0.38409 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
242 | 13 | 238.98 | 207.6793 | 238.46 | 258.9316 | 238.72 | 238.8366 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 215-200 Heating Int IR (Ext IR "off") | 0.249 | 0.19396 | 0.212 | 0.13649 | 0.115 | 0.13665 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
243 | 14 | 475.13 | 443.3988 | 460.58 | 491.6517 | 471.42 | 475.03 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 215-200 Cooling Int IR (Ext IR "off") | 0.122 | 0.15407 | 0.147 | 0.092921 | 0.168 | 0.093176 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
244 | 15 | 672.39 | 644.8859 | 644.63 | 683.8576 | 668.03 | 673.0005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 220-210 Heating Int IR (Ext IR "on") | 0.257 | 0.2104 | 0.258 | 0.12747 | 0.117 | 0.12878 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
245 | 16 | 809.04 | 787.9666 | 771.27 | 811.9781 | 802.57 | 809.0801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 220-210 Cooling Int IR (Ext IR "on") | 0.143 | 0.16283 | 0.103 | 0.1001 | 0.135 | 0.083849 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
246 | 17 | 861.62 | 850.1509 | 818.34 | 853.4406 | 852.47 | 861.5066 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 806.87 | 805.1397 | 758.2 | 778.077 | 789.03 | 806.2411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 578.91 | 590.3427 | 525.64 | 527.4004 | 555.16 | 588.0142 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST IN-DEPTH CASES 220 TO 270 DELTA CHART - ANNUAL
249 | 20 | 0 | 78.5987 | 19.69 | 70.2141 | 94.52 | 83.7153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 230-220 Heating Infiltration | 3.474 | 3.146 | 3.239 | 3.4747 | 3.2128 | 3.3665 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 230-220 Cooling Infiltration | 0.381 | 0.38074 | 0.379 | 0.38131 | 0.3788 | 0.39898 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 240-220 Heating Internal Gains | -1.261 | -1.2237 | -1.234 | -1.1758 | -1.1864 | -1.2106 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 240-220 Cooling Internal Gains | 0.484 | 0.37177 | 0.326 | 0.36884 | 0.3456 | 0.33612 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
| Note: Hourly incident solar on horizontal surface is further down (after the hourly heating and cooling load data tables). | [20 empty] | 250-220 Heating Ext Solar Absorptance | -1.644 | -1.6225 | -1.805 | -1.556 | -1.7907 | -1.7631 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 250-220 Cooling Ext Solar Abs. | 2.809 | 2.8184 | 2.921 | 2.5717 | 2.8906 | 2.4062 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 270-220 Heating South Windows | #N/A | -2.3199 | -2.905 | -2.0698 | -2.1493 | -2.2367 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 270-220 Cooling South Windows | #N/A | 6.6602 | 6.148 | 6.9116 | 6.7324 | 6.7908 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
| HOURLY FREE FLOAT TEMPERATURE DATA | [20 empty] | BESTEST IN-DEPTH CASES 220 TO 270 DELTA CHART - PEAK
| CASE 600FF FEB 1 | [20 empty] | PEAK HEATING AND SENSIBLE COOLING [MWH]
| (USE COLUMN B ONLY) | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | COUNTRY: | [20 empty] | 230-220 Heating Infiltration | 1.588 | 1.2935 | 1.36 | 1.6241 | 1.372 | 1.4367 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 230-220 Cooling Infiltration | 0.658 | 0.61968 | 0.694 | 0.6564 | 0.689 | 0.72555 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 240-220 Heating Internal Gains | -0.2 | -0.18795 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 240-220 Cooling Internal Gains | 0.198 | 0.18623 | 0.178 | 0.18145 | 0.18 | 0.18157 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
294 | 1 | 13 | 7.3199 | 4.4672 | 5.443 | 6 | 4.8678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 250-220 Cooling Ext Solar Absorpance | 1.577 | 1.6815 | 1.711 | 1.6821 | 2.022 | 1.72 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
295 | 2 | 10.3 | 5.475 | 2.8568 | 3.8072 | 4.1 | 3.1842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 270-220 Cooling South Windows | #N/A | 5.9025 | 4.792 | 5.6543 | 5.601 | 5.6695 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
296 | 3 | 7.9 | 3.8429 | 1.4091 | 2.3742 | 2.48 | 1.7232 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
297 | 4 | 5.7 | 2.3514 | -0.016476 | 1.0857 | 0.99 | 0.38989 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
298 | 5 | 3.8 | 1.0503 | -1.2245 | -0.0051534 | -0.3 | -0.73229 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST IN-DEPTH CASES 270 TO 320 DELTA CHART - ANNUAL
299 | 6 | 2.1 | -0.033328 | -2.2862 | -0.89643 | -1.35 | -1.6653 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
300 | 7 | 0.7 | -1.0231 | -3.193 | -1.7104 | -2.34 | -2.5318 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
301 | 8 | 0.1 | -0.98405 | -3.3337 | -1.4759 | -2.4 | -1.339 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
302 | 9 | 1.7 | 2.4994 | -0.19628 | 2.7076 | 1.57 | 4.1068 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 280-270 Cooling Cavity Albedo | #N/A | -2.2745 | -2.483 | -2.3386 | -2.1028 | -2.4804 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
303 | 10 | 6.1 | 9.5334 | 6.8013 | 9.9288 | 9.22 | 11.9724 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 320-270 Heating Thermostat | #N/A | -0.66901 | -0.674 | -0.61416 | -0.6065 | -0.60003 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
304 | 11 | 12.5 | 17.965 | 15.6352 | 18.7293 | 18.48 | 20.6983 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 320-270 Cooling Thermostat | #N/A | -2.4123 | -2.278 | -2.5356 | -2.3955 | -2.5008 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
305 | 12 | 20.2 | 26.9295 | 25.0661 | 28.01 | 28.14 | 29.8333 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 290-270 Cooling South Shading | #N/A | -1.6611 | -1.388 | -1.779 | -1.988 | -1.8273 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
306 | 13 | 28.5 | 35.5894 | 34.0622 | 36.5705 | 37.38 | 38.2109 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 300-270 Cooling E&W Windows | #N/A | -2.2158 | -1.893 | -2.3695 | -2.2705 | -2.3755 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
307 | 14 | 36.1 | 42.8259 | 41.1697 | 43.3942 | 44.87 | 44.2314 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 310-300 Heating E&W Shading | #N/A | 0.26199 | 0.386 | 0.26662 | 0.5717 | 0.43695 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
308 | 15 | 41.9 | 47.0783 | 46.07 | 46.9798 | 48.81 | 47.0105 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 310-300 Cooling E&W Shading | #N/A | -1.3032 | -1.403 | -1.4825 | -1.9102 | -1.5887 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
309 | 16 | 45.4 | 48.2109 | 48.1263 | 47.5927 | 49.81 | 46.9306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
310 | 17 | 46.3 | 45.9023 | 46.582 | 44.8818 | 47.28 | 43.4741 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
311 | 18 | 44 | 39.9832 | 41.232 | 38.7015 | 40.93 | 36.5383 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
312 | 19 | 39.5 | 33.3 | 34.5581 | 32.1639 | 33.48 | 29.6668 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL
313 | 20 | 34.4 | 27.5274 | 28.7453 | 26.2951 | 27.37 | 24.2082 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
314 | 21 | 29.3 | 22.5321 | 23.5942 | 21.5268 | 22.09 | 19.2617 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
315 | 22 | 24.6 | 18.1055 | 18.976 | 17.0314 | 17.43 | 15.0331 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
316 | 23 | 20.2 | 14.1487 | 14.9392 | 13.2781 | 13.28 | 11.2196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 400-395 Low Mass, Heating Surf. Conv. & IR | 1.341 | 1.6808 | 1.902 | 1.7066 | 1.7443 | 1.8611 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
317 | 24 | 16.3 | 10.8188 | 11.505 | 10.2079 | 9.82 | 8.1223 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 410-400 Low Mass, Heating Infiltration | 1.724 | 1.5093 | 1.614 | 1.7325 | 1.6022 | 1.6757 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 420-410 Low Mass, Heating Int. Gains | -1.231 | -1.2106 | -1.228 | -1.1745 | -1.1852 | -1.2086 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 430-420 Low Mass, Heating Ext. Solar Abs. | -1.228 | -1.3804 | -1.479 | -1.2857 | -1.4821 | -1.3858 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 430-420 Low Mass, Cooling Ext Solar Abs. | 0.856 | 0.76554 | 0.825 | 0.70305 | 0.8108 | 0.62959 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 600-430 Low Mass, Heating S. Window | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 600-430 Low Mass, Cooling S. Window | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 440-600 Low Mass, Heating Cavity Albedo | #N/A | 0.16318 | 0.283 | 0.17569 | 0.1419 | 0.21713 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.9278 | -1.974 | -1.942 | -1.7477 | -2.0384 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 810-900 High Mass, Heating Cavity Albedo | #N/A | 0.65862 | 0.863 | 0.67814 | 0.6003 | 0.79572 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
[22 empty] | 810-900 High Mass, Cooling Cavity Albedo | #N/A | -0.98312 | -1.026 | -0.98095 | -0.8821 | -0.97261 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
HOURLY FREE FLOAT TEMPERATURE DATA
| CASE 900FF FEB 1 | [20 empty] | BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL
| (USE COLUMN B ONLY) | [20 empty] | PEAK HEATING AND SENSIBLE COOLING [MWH]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | COUNTRY: | [20 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 400-395 Low Mass, Heating Surf. Conv. & IR | 0.611 | 0.68193 | 0.778 | 0.74028 | 0.698 | 0.71723 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0.251 | 0.13615 | 0.149 | 0.22943 | 0.162 | 0.10678 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 410-400 Low Mass, Heating Infiltration | 0.779 | 0.60131 | 0.68 | 0.81203 | 0.685 | 0.71836 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
294 | 1 | 15.4 | 14.7379 | 11.7017 | 12.938 | 13.28 | 12.3543 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 410-400 Low Mass, Cooling Infiltration | 0.213 | 0.20623 | 0.252 | 0.22094 | 0.168 | 0.2317 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
295 | 2 | 14.8 | 14.2075 | 11.245 | 12.4251 | 12.7 | 11.8184 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 420-410 Low Mass, Heating Int. Gains | -0.2 | -0.18445 | -0.178 | -0.18492 | -0.183 | -0.18548 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
296 | 3 | 14.2 | 13.7002 | 10.7932 | 11.9298 | 12.17 | 11.3192 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 420-410 Low Mass, Cooling Int. Gains | 0.197 | 0.20865 | 0.208 | 0.20469 | 0.212 | 0.21039 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
297 | 4 | 13.6 | 13.1833 | 10.3008 | 11.432 | 11.64 | 10.8039 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 430-420 Low Mass, Cooling Ext. Solar Abs. | 0.959 | 0.93129 | 0.923 | 0.89683 | 1.038 | 0.89001 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
298 | 5 | 13 | 12.7111 | 9.9029 | 10.9913 | 11.15 | 10.3478 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 600-430 Low Mass, Cooling S. Window | 3.483 | 4.6412 | 3.582 | 4.4222 | 4.319 | 4.3417 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
299 | 6 | 12.4 | 12.2668 | 9.4738 | 10.5804 | 10.72 | 9.9295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 440-600 Low Mass, Cooling Cavity Albedo | #N/A | -1.8155 | -1.656 | -1.6656 | -1.514 | -1.7382 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
300 | 7 | 11.8 | 11.8353 | 9.0975 | 10.1741 | 10.25 | 9.4998 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 810-900 High Mass, Cooling Cavity Albedo | #N/A | -0.96595 | -0.616 | -0.77023 | -0.717 | -0.8272 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
301 | 8 | 11.2 | 11.941 | 8.9582 | 10.3241 | 10.14 | 9.799 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST Indepth South Window Delta Annual Cooling and Heating
302 | 9 | 11.8 | 13.2165 | 9.8876 | 11.7504 | 11.22 | 11.4018 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
303 | 10 | 13.4 | 15.2859 | 11.7551 | 13.8083 | 13.19 | 13.4628 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 600-430 Low Mass, Heating S. Window | -1.121 | -1.4613 | -1.907 | -1.2958 | -1.1829 | -1.347 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
304 | 11 | 15.7 | 17.5497 | 13.9547 | 15.9577 | 15.41 | 15.5991 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 600-430 Low Mass, Cooling S. Window | 4.738 | 5.007 | 4.488 | 5.1714 | 5.2091 | 5.0405 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
305 | 12 | 18.4 | 19.8553 | 16.2133 | 18.2069 | 17.71 | 17.9031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 900-800 High Mass, Heating S. Window | -3.415 | -3.5268 | -3.812 | -3.4519 | -3.3951 | -3.5554 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
306 | 13 | 21.3 | 22.0025 | 18.3357 | 20.4419 | 20.03 | 20.0527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 900-800 High Mass, Cooling S. Window | 2.241 | 2.084 | 2.021 | 2.1152 | 2.0963 | 1.985 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A; SPAIN DATE: #N/A; SPAIN HR: #N/A
307 | 14 | 23.2 | 23.2661 | 19.6982 | 22.0116 | 21.78 | 21.5258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
308 | 15 | 24.8 | 23.5646 | 20.6912 | 22.7239 | 22.59 | 22.2103 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
309 | 16 | 25.4 | 23.5055 | 21.0435 | 22.8195 | 22.89 | 22.2681 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
310 | 17 | 24.6 | 22.7021 | 20.5729 | 22.102 | 22.44 | 21.5145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST BASIC Window Types (Delta) Annual Heating and Cooling
311 | 18 | 23.5 | 20.9392 | 19.2453 | 20.4887 | 21.07 | 19.867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
312 | 19 | 22.6 | 19.7278 | 18.0354 | 19.2192 | 19.67 | 18.5155 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
313 | 20 | 21.9 | 18.9536 | 17.2201 | 18.324 | 18.77 | 17.6825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 660-600 Low-E Windows, Heating | -0.476 | -0.3908 | -0.226 | -0.61764 | -0.575 | -0.71389 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
314 | 21 | 20.8 | 18.2399 | 16.476 | 17.5351 | 17.93 | 16.825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 660-600 Low-E Windows, Cooling | -2.808 | -2.5734 | -2.172 | -2.7955 | -2.9432 | -2.8133 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
315 | 22 | 20 | 17.5304 | 15.7483 | 16.7569 | 17.11 | 16.0591 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 670-600 Single-Pane Windows, Heating | 1.434 | 1.3074 | 1.526 | 1.2918 | 1.613 | 1.6363 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
316 | 23 | 19.2 | 16.8299 | 15.107 | 15.9944 | 16.31 | 15.2703 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 670-600 Single-Pane Windows, Cooling | 0.717 | 0.66462 | 0.522 | 0.59566 | 0.3585 | 0.41828 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
317 | 24 | 18.1 | 16.228 | 14.5494 | 15.3612 | 15.65 | 14.6249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
BESTEST BASIC Window Types (Delta) Peak Heating and Cooling
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | 660-600 Low-E Windows, Heating | -0.635 | -0.26192 | -0.237 | -0.3733 | -0.382 | -0.40371 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 660-600 Low-E Windows, Cooling | -2.307 | -2.548 | -2.067 | -2.5812 | -2.663 | -2.5883 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 670-600 Single-Pane Windows, Heating | 0.867 | 0.63519 | 0.777 | 0.6491 | 0.764 | 0.86207 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 670-600 Single-Pane Windows, Cooling | 0.567 | 0.44432 | 0.417 | 0.45463 | 0.289 | 0.35556 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FFV JULY 14
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | BESTEST BASIC Insulation (Delta) Annual Heating and Cooling
0 | COUNTRY: | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 680-600 600 with Greater Insulation, Heating | -1.831 | -2.2067 | -2.315 | -2.1447 | -2.2299 | -2.2173 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 680-600 600 with Greater Insulation, Cooling | 0.116 | 0.51669 | 0.5 | 0.41686 | 0.3676 | 0.53023 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
294 | 1 | 21.7 | 19.8311 | 19.6725 | 19.8711 | 19.86 | 20.0209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 685-600 600 with 20/20 Tstat, Heating | 0.482 | 0.58167 | 0.599 | 0.55275 | 0.5415 | 0.53862 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
295 | 2 | 20.1 | 19.0165 | 18.88 | 19.0627 | 19.01 | 18.7675 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 685-600 600 with 20/20 Tstat, Cooling | 3.308 | 2.9461 | 2.806 | 3.0918 | 2.9596 | 3.0718 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
296 | 3 | 19 | 18.1137 | 17.7669 | 18.14 | 18.1 | 18.213 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 695-685 685 with Greater Insulation, Heating | -1.823 | -2.1592 | -2.261 | -2.0752 | -2.1714 | -2.1504 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
297 | 4 | 17.8 | 16.994 | 16.6508 | 17.0158 | 16.97 | 16.7605 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 695-685 685 with Greater Insulation, Cooling | -0.375 | 0.1149 | 0.148 | 0.052759 | 0.0276 | 0.18778 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
298 | 5 | 16.6 | 15.8658 | 15.4711 | 15.8836 | 15.83 | 15.8849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 980-900 900 with Greater Insulation, Heating | -1.006 | -1.1331 | -1.325 | -1.2527 | -1.2336 | -1.3636 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
299 | 6 | 16.6 | 16.1929 | 17.1247 | 16.3875 | 16.09 | 16.0945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 980-900 900 with Greater Insulation, Cooling | 0.787 | 1.5314 | 1.375 | 1.2231 | 1.2868 | 1.2514 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
300 | 7 | 18.2 | 18.4147 | 19.397 | 18.7611 | 18.49 | 18.6396 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 985-900 900 with 20/20 Tstat, Heating | 1.075 | 0.74132 | 0.688 | 0.70563 | 0.6986 | 0.72238 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
301 | 8 | 20.3 | 20.1417 | 20.5125 | 20.8898 | 20.94 | 20.6119 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 985-900 900 with 20/20 Tstat, Cooling | 4.559 | 3.7698 | 3.497 | 3.8704 | 3.7616 | 3.8463 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
302 | 9 | 22.3 | 22.2539 | 22.8099 | 23.2971 | 23.29 | 23.2169 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 995-985 985 with Greater Insulation, Heating | -1.471 | -1.365 | -1.509 | -1.3628 | -1.3785 | -1.4594 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
303 | 10 | 24.9 | 25.3076 | 25.8855 | 26.426 | 26.23 | 26.4995 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 995-985 985 with Greater Insulation, Cooling | 0.209 | 0.9685 | 0.891 | 0.84367 | 0.8995 | 0.95032 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
304 | 11 | 28.3 | 29.4735 | 29.838 | 30.6202 | 30.05 | 30.7733 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
305 | 12 | 32.3 | 34.0869 | 34.1747 | 35.2192 | 34.64 | 35.1804 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
306 | 13 | 36.2 | 38.0756 | 38.3724 | 39.1876 | 38.99 | 39.0337 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
307 | 14 | 39.7 | 41.1874 | 41.8987 | 42.1006 | 42.49 | 41.924 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST BASIC Insulation (Delta) Peak Heating and Cooling
308 | 15 | 42.5 | 43.0949 | 44.2829 | 44.2085 | 44.77 | 43.5674 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
309 | 16 | 44.4 | 43.7728 | 45.2962 | 44.886 | 45.78 | 43.8561 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
310 | 17 | 45.4 | 43.4747 | 45.2885 | 44.6042 | 45.65 | 43.3487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 680-600 600 with Greater Insulation, Heating | -1.129 | -1.2426 | -1.224 | -1.152 | -1.206 | -1.2442 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
311 | 18 | 41.7 | 42.6822 | 44.6098 | 43.7421 | 44.91 | 42.3948 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 680-600 600 with Greater Insulation, Cooling | 0.111 | 0.57027 | 0.439 | 0.41866 | 0.483 | 0.51086 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
312 | 19 | 35.5 | 34.1248 | 33.257 | 34.4834 | 38.29 | 33.6127 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 685-600 600 with 20/20 Tstat, Heating | -0.086 | 0.011624 | 0.019 | 0.018741 | 0.019 | 0.015534 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
313 | 20 | 31.7 | 30.7295 | 30.0661 | 30.8554 | 31.6 | 29.6146 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 685-600 600 with 20/20 Tstat, Cooling | 0.668 | 0.67846 | 0.649 | 0.7552 | 0.741 | 0.82169 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
314 | 21 | 28.6 | 27.846 | 27.4122 | 27.9576 | 28.34 | 27.9251 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 695-685 685 with Greater Insulation, Heating | -1.031 | -1.2365 | -1.199 | -1.1514 | -1.222 | -1.2567 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
315 | 22 | 26.5 | 25.8648 | 25.8257 | 25.9916 | 26.14 | 25.3141 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 695-685 685 with Greater Insulation, Cooling | -0.086 | 0.38129 | 0.284 | 0.22753 | 0.305 | 0.30772 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
316 | 23 | 25 | 24.4442 | 24.2308 | 24.5462 | 24.6 | 24.6473 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 980-900 900 with Greater Insulation, Heating | -0.858 | -1.1896 | -1.071 | -1.1497 | -1.16 | -1.1863 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
317 | 24 | 23.5 | 22.9121 | 22.4527 | 22.9825 | 22.99 | 22.567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 980-900 900 with Greater Insulation, Cooling | 0.345 | 0.29156 | 0.374 | 0.40968 | 0.445 | 0.37249 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
| = | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 985-900 900 with 20/20 Tstat, Heating | 0.203 | 0.008773 | 0.005 | 0.0079536 | 0.009 | 0.0069624 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 985-900 900 with 20/20 Tstat, Cooling | 0.938 | 0.84883 | 0.652 | 0.87434 | 0.84 | 0.94464 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 995-985 985 with Greater Insulation, Heating | -1.043 | -1.0826 | -0.996 | -1.0733 | -1.082 | -1.1235 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 995-985 985 with Greater Insulation, Cooling | 0.152 | -0.001482 | 0.107 | 0.26266 | 0.218 | 0.2302 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
HOURLY FREE FLOAT TEMPERATURE DATA
| CASE 950FFV JULY 14 | [20 empty] | BASIC INSULATION MASS EFFECT DELTA CHART - ANNUAL
| (USE COLUMN B ONLY) | [20 empty] | ANNUAL HEATING AND ANNUAL SENSIBLE COOLING [MWH]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
0 | COUNTRY: | [20 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 980-680 Mass, Heating with Greater Insulation | -1.499 | -1.5403 | -1.466 | -1.7687 | -1.781 | -1.8358 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 980-680 Mass, Cooling with Greater Insulation | -2.437 | -2.4346 | -2.174 | -2.7321 | -2.7549 | -2.7912 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 985-685 Mass, Heating with 20/20 Tstat | -1.731 | -2.4542 | -2.367 | -2.5078 | -2.6202 | -2.5058 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
294 | 1 | 23.4 | 21.2148 | 20.9717 | 21.2303 | 21.37 | 21.1154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 985-685 Mass, Cooling with 20/20 Tstat | -1.857 | -2.6256 | -2.358 | -2.7596 | -2.8721 | -2.7378 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
295 | 2 | 22.2 | 20.7077 | 20.4879 | 20.7155 | 20.84 | 20.5424 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 995-695 Mass, Heating w/ > Insul. & 20/20 Tstat | -1.379 | -1.6601 | -1.615 | -1.7954 | -1.8273 | -1.8147 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
296 | 3 | 21.3 | 20.0478 | 19.6293 | 20.0299 | 20.18 | 19.9172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 995-695 Mass, Cooling w/ > Insul. & 20/20 Tstat | -1.273 | -1.772 | -1.615 | -1.9687 | -2.0002 | -1.9753 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
297 | 4 | 20.3 | 19.188 | 18.7479 | 19.1593 | 19.31 | 19.0113 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
298 | 5 | 19.3 | 18.2994 | 17.7906 | 18.2535 | 18.4 | 18.1384 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
299 | 6 | 19.3 | 18.5567 | 19.3484 | 18.6317 | 18.55 | 18.3188 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
300 | 7 | 20.5 | 20.0938 | 21.0886 | 20.2686 | 20.13 | 19.9757 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BASIC INSULATION MASS EFFECT DELTA CHART - ANNUAL
301 | 8 | 22.1 | 22.4421 | 23.1543 | 22.8727 | 22.07 | 22.5701 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | PEAK HEATING AND ANNUAL SENSIBLE COOLING [MWH]
302 | 9 | 23.4 | 23.5009 | 23.8657 | 24.4046 | 24.04 | 24.209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
303 | 10 | 24.5 | 24.6745 | 24.7959 | 25.569 | 25.3 | 25.0426 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
304 | 11 | 25.8 | 26.1394 | 25.9168 | 26.9141 | 26.65 | 26.5298 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 980-680 Mass, Heating with Greater Insulation | -0.433 | -0.52385 | -0.429 | -0.51458 | -0.549 | -0.52258 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
305 | 12 | 27.4 | 27.5275 | 27.0556 | 28.1778 | 27.92 | 27.7048 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 980-680 Mass, Cooling with Greater Insulation | -2.377 | -3.3833 | -2.931 | -3.3201 | -3.335 | -3.244 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
306 | 13 | 28.7 | 28.5007 | 28.1472 | 29.1272 | 28.96 | 28.7071 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 985-685 Mass, Heating with 20/20 Tstat | -0.415 | -0.57969 | -0.596 | -0.52772 | -0.605 | -0.58899 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
307 | 14 | 29.8 | 29.1549 | 29.0149 | 29.8598 | 29.78 | 29.4146 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 985-685 Mass, Cooling with 20/20 Tstat | -2.341 | -2.9342 | -2.863 | -3.192 | -3.198 | -2.9827 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
308 | 15 | 30.6 | 29.3989 | 29.5372 | 30.2902 | 30.31 | 29.8578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 995-695 Mass, Heating w/ > Insul. & 20/20 Tstat | -0.427 | -0.42577 | -0.393 | -0.44966 | -0.465 | -0.45573 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
309 | 16 | 31 | 29.2893 | 29.7074 | 30.4309 | 30.52 | 29.9484 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 995-695 Mass, Cooling w/ > Insul. & 20/20 Tstat | -2.103 | -3.3169 | -3.04 | -3.1569 | -3.285 | -3.0602 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
310 | 17 | 31.4 | 29.1458 | 29.7175 | 30.4338 | 30.55 | 29.9561 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
311 | 18 | 31 | 29.0474 | 29.6094 | 30.3524 | 30.53 | 29.8951 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
312 | 19 | 30.3 | 28.666 | 28.4499 | 29.0273 | 29.51 | 28.9728 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
313 | 20 | 29.1 | 27.3534 | 26.9749 | 27.6463 | 27.82 | 27.553 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
314 | 21 | 28.1 | 26.0894 | 25.7654 | 26.3384 | 26.48 | 26.2179 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
315 | 22 | 27 | 25.2973 | 25.2338 | 25.5339 | 25.61 | 25.3225 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
316 | 23 | 26 | 24.6727 | 24.4091 | 24.8642 | 24.95 | 24.6889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
317 | 24 | 24.9 | 23.7451 | 23.2527 | 23.8852 | 23.99 | 23.7105 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | BESTEST IN-DEPTH Surface Heat Transfer (Delta) Annual Heating and Cooling
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | 450-600 Const. Int.&Ext. Surf. Coefs., Heating | -0.307 | -0.0023157 | -0.672 | -0.3619 | -0.5117 | -0.63264 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 450-600 Const. Int.&Ext. Surf. Coefs., Cooling | 0.35 | -0.22415 | 0.729 | 0.48022 | 0.4514 | 0.75118 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 460-600 Const. Interior Surf. Coefs., Heating | -0.222 | 0.062755 | -0.174 | -0.13062 | -0.0995 | -0.21378 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 460-600 Const. Interior Surf. Coefs., Cooling | 0.438 | 0.026684 | 0.497 | 0.44757 | 0.5673 | 0.46383 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 460-450 Auto Exterior Surf. H.T., Heating | 0.085 | 0.065071 | 0.498 | 0.23127 | 0.4122 | 0.41886 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
| HOURLY FREE FLOAT TEMPERATURE DATA | [20 empty] | 460-450 Auto Exterior Surf. H.T., Cooling | 0.088 | 0.25083 | -0.232 | -0.03265 | 0.1159 | -0.28735 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
| CASE 680FF JULY 14 | [20 empty] | 470-600 Const. Exterior Surf. Coefs., Heating | -0.008 | -0.093264 | -0.507 | -0.23051 | -0.4023 | -0.42893 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
| (USE COLUMN B ONLY) | [20 empty] | 470-600 Const. Exterior Surf. Coefs., Cooling | 0.165 | -0.26923 | 0.217 | 0.0023448 | -0.1564 | 0.27637 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 470-450 Auto Interior Surf. H.T., Heating | 0.299 | -0.090948 | 0.165 | 0.13138 | 0.1094 | 0.20371 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
0 | COUNTRY: | [20 empty] | 470-450 Auto Interior Surf. H.T., Cooling | -0.185 | -0.045084 | -0.512 | -0.47787 | -0.6078 | -0.47481 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
294 | 1 | 27.4 | 19.3025 | 16.0238 | 15.3461 | 16.32 | 14.4417 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST IN-DEPTH Surface Heat Transfer (Delta) Peak Heating and Cooling
295 | 2 | 24 | 17.2859 | 14.3021 | 13.4846 | 14.25 | 12.548 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
296 | 3 | 20.8 | 15.4125 | 12.6782 | 11.7774 | 12.37 | 10.8267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
297 | 4 | 17.8 | 13.6262 | 11.0975 | 10.1946 | 10.6 | 9.1997 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 450-600 Const. Int.&Ext. Surf. Coefs., Heating | -0.266 | -0.041917 | -0.282 | -0.10461 | -0.186 | -0.32158 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
298 | 5 | 15 | 11.9969 | 9.689 | 8.775 | 9.01 | 7.7578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 450-600 Const. Int.&Ext. Surf. Coefs., Cooling | 0.162 | -0.30121 | 0.641 | 0.11476 | 0.308 | 0.26769 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
299 | 6 | 12.4 | 10.5252 | 8.334 | 7.5063 | 7.61 | 6.48 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 460-600 Const. Interior Surf. Coefs., Heating | -0.2 | -0.04888 | -0.055 | -0.11337 | -0.127 | -0.19922 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
300 | 7 | 10.1 | 9.1662 | 7.1316 | 6.3475 | 6.29 | 5.2952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 460-600 Const. Interior Surf. Coefs., Cooling | 0.154 | -0.23813 | 0.48 | 0.0226 | 0.111 | 0.023202 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
301 | 8 | 8.7 | 8.8545 | 6.5882 | 6.2878 | 5.9 | 6.1093 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 460-450 Auto Exterior Surf. H.T., Heating | 0.066 | -0.006963 | 0.227 | -0.0087666 | 0.059 | 0.12236 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
302 | 9 | 9.5 | 11.6688 | 8.9979 | 10.0373 | 9.12 | 11.026 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 460-450 Auto Exterior Surf. H.T., Cooling | -0.008 | 0.063083 | -0.161 | -0.09216 | -0.197 | -0.24449 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
303 | 10 | 13.1 | 17.8327 | 15.0347 | 16.5873 | 15.82 | 18.4242 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 470-600 Const. Exterior Surf. Coefs., Heating | -0.137 | -0.019557 | -0.228 | 0.0023118 | -0.059 | -0.1274 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
304 | 11 | 19.1 | 25.8327 | 23.1553 | 24.697 | 24.43 | 26.9441 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 470-600 Const. Exterior Surf. Coefs., Cooling | 0.045 | -0.093327 | 0.148 | 0.092071 | 0.214 | 0.27425 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
305 | 12 | 26.7 | 34.849 | 32.2721 | 33.6544 | 33.78 | 36.1278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 470-450 Auto Interior Surf. H.T., Heating | 0.129 | 0.02236 | 0.054 | 0.10692 | 0.127 | 0.19418 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
306 | 13 | 35.2 | 43.9435 | 41.4162 | 42.5122 | 43.16 | 44.8321 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 470-450 Auto Interior Surf. H.T., Cooling | -0.117 | 0.20788 | -0.493 | -0.022689 | -0.094 | 0.0065584 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
307 | 14 | 43.4 | 51.6986 | 49.1534 | 49.7746 | 51.16 | 51.5938 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
308 | 15 | 50.2 | 57.0436 | 55.1901 | 54.3914 | 56.13 | 55.5469 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
309 | 16 | 55.1 | 59.5967 | 58.6456 | 56.3144 | 58.45 | 56.7937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
310 | 17 | 57.3 | 58.7261 | 58.7506 | 54.9811 | 57.42 | 54.6584 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST BASIC Shading and Window Orientation (Delta) Annual Heating and Cooling
311 | 18 | 56.3 | 54.2792 | 55.2721 | 50.2114 | 52.78 | 49.111 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
312 | 19 | 53 | 49.0597 | 50.4057 | 44.9265 | 47.02 | 43.4177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
313 | 20 | 48.8 | 44.294 | 45.8603 | 39.9705 | 42.06 | 38.6121 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 610-600 Low Mass, S.Shade Heating | 0.113 | 0.073669 | 0.097 | 0.050431 | 0.165 | 0.08851 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
314 | 21 | 44.3 | 39.9085 | 41.5737 | 35.6029 | 37.49 | 34.0685 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 610-600 Low Mass, S.Shade Cooling | -1.523 | -1.5313 | -1.259 | -1.6943 | -1.9293 | -1.6627 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
315 | 22 | 39.8 | 35.8862 | 37.5376 | 31.6493 | 33.3 | 30.1063 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 910-900 High Mass, S. Shade Heating | 0.437 | 0.26879 | 0.269 | 0.29205 | 0.4825 | 0.31776 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
316 | 23 | 35.4 | 32.1123 | 33.8308 | 28.034 | 29.35 | 26.2987 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 910-900 High Mass, S. Shade Cooling | -1.23 | -1.049 | -0.893 | -1.1053 | -1.2048 | -1.0763 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
317 | 24 | 31.2 | 28.6933 | 30.4633 | 24.8425 | 25.88 | 22.9692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 620-600 Low Mass, E&W Or., Heating | 0.32 | 0.10084 | 0.25 | 0.1607 | 0.1523 | 0.21543 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | = |  |  |  | 620-600 Low Mass, E&W Or., Cooling | -1.418 | -1.8338 | -1.523 | -1.9675 | -1.9161 | -1.9389 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 920-900 High Mass, E&W Or., Heating | 1.774 | 1.5772 | 1.668 | 1.6728 | 1.715 | 1.7927 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 920-900 HIgh Mass, E&W Or., Cooling | 0.414 | 0.32538 | 0.323 | 0.2421 | 0.3267 | 0.28174 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 630-620 Low Mass, E&W Shd., Heating | 0.553 | 0.26235 | 0.38 | 0.29847 | 0.5363 | 0.4196 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 630-620 Low Mass, E&W Shd., Cooling | -1.33 | -1.0589 | -1.122 | -1.2235 | -1.6504 | -1.2678 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 930-920 High Mass, E&W Shd., Heating | 0.77 | 0.56758 | 0.674 | 0.6573 | 0.9779 | 0.7774 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 930-920 High Mass, E&W Shd., Cooling | -0.967 | -0.71422 | -0.798 | -0.81173 | -1.1606 | -0.87711 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 980FF JULY 14
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | BESTEST BASIC Shading and Window Orientation (Delta) Peak Heating and Cooling
0 | COUNTRY: | [21 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = |  |  |  | 610-600 Low Mass, S.Shade Heating | -0.089 | 0.000526 | 0.004 | -0.012584 | 0.005 | 0.00060921 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg |  |  |  | 610-600 Low Mass, S.Shade Cooling | -0.184 | -0.048825 | -0.091 | -0.21703 | -0.259 | -0.17795 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
294 | 1 | 26.6 | 27.6665 | 24.2654 | 22.7451 | 23.79 | 22.2363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 910-900 High Mass, S. Shade Heating | 0.21 | 0.025635 | 0.021 | 0.011437 | 0.051 | 0.020717 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
295 | 2 | 25.8 | 27.1526 | 23.841 | 22.2438 | 23.19 | 21.7134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 910-900 High Mass, S. Shade Cooling | -0.546 | -0.65436 | -0.453 | -0.81835 | -0.684 | -0.85903 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
296 | 3 | 24.9 | 26.66 | 23.4157 | 21.7632 | 22.68 | 21.2323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 620-600 Low Mass, E&W Or., Heating | -0.11 | 0.017627 | 0.033 | 0.024696 | 0.025 | 0.025699 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
297 | 4 | 24 | 26.1515 | 22.967 | 21.2816 | 22.16 | 20.7325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 620-600 Low Mass, E&W Or., Cooling | -0.946 | -1.9882 | -1.467 | -1.5541 | -1.571 | -1.4575 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
298 | 5 | 23.2 | 25.6862 | 22.6075 | 20.8555 | 21.69 | 20.2913 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 920-900 High Mass, E&W Or., Heating | 0.344 | 0.069036 | 0.06 | 0.08269 | 0.073 | 0.085796 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
299 | 6 | 22.4 | 25.2544 | 22.1993 | 20.459 | 21.27 | 19.892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 920-900 HIgh Mass, E&W Or., Cooling | 0.442 | -0.31975 | 0.154 | 0.21988 | 0.203 | 0.21408 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
300 | 7 | 21.8 | 24.8308 | 21.8506 | 20.0788 | 20.84 | 19.4952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 630-620 Low Mass, E&W Shd., Heating | 0.107 | 0.001512 | 0.004 | -0.022564 | 0.006 | 0.0029619 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
301 | 8 | 21.4 | 24.9686 | 21.7274 | 20.2516 | 20.76 | 19.8079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 630-620 Low Mass, E&W Shd., Cooling | -0.583 | -0.49451 | -0.429 | -0.58526 | -0.651 | -0.63889 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
302 | 9 | 22 | 26.3146 | 22.6222 | 21.6585 | 21.86 | 21.363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 930-920 High Mass, E&W Shd., Heating | 0.073 | 0.024542 | 0.036 | 0.014719 | 0.059 | 0.03614 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
303 | 10 | 23.5 | 28.2183 | 24.3831 | 23.5492 | 23.76 | 23.32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 930-920 High Mass, E&W Shd., Cooling | -0.429 | -0.39486 | -0.375 | -0.47881 | -0.605 | -0.54103 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
304 | 11 | 25.5 | 30.208 | 26.4423 | 25.5857 | 25.83 | 25.378 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
305 | 12 | 27.8 | 32.2226 | 28.5594 | 27.7875 | 28.05 | 27.6309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
306 | 13 | 30.2 | 34.0812 | 30.5625 | 29.9726 | 30.34 | 29.7398 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
307 | 14 | 32.3 | 35.3862 | 31.8566 | 31.4705 | 32.04 | 31.1593 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
308 | 15 | 33.8 | 35.9936 | 32.861 | 32.0838 | 32.66 | 31.7177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | BESTEST BASIC Thermostat, Ventilation and Sunspace (Delta) Annual Heating and Cooling
309 | 16 | 34.6 | 36.0431 | 33.2429 | 32.1996 | 32.9 | 31.761 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
310 | 17 | 34 | 35.2665 | 32.828 | 31.4583 | 32.38 | 30.9917 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
311 | 18 | 32.9 | 33.6073 | 31.5769 | 29.8322 | 30.99 | 29.3415 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 640-600 Low Mass, Tstat Setback, Heating | -1.368 | -1.5895 | -1.428 | -1.6625 | -1.7076 | -1.8508 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
312 | 19 | 32 | 32.4976 | 30.4417 | 28.6662 | 29.68 | 28.1322 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 940-900 High Mass, Tstat Setback, Heating | -0.337 | -0.51566 | -0.442 | -0.5963 | -0.57 | -0.6449 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
313 | 20 | 31.2 | 31.7818 | 29.6795 | 27.8593 | 28.9 | 27.3891 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 650-600 Low Mass, Night Vent, Cooling | -1.193 | -1.2592 | -1.246 | -1.2103 | -1.2167 | -1.1472 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
314 | 21 | 30.3 | 31.126 | 28.995 | 27.1608 | 28.17 | 26.6361 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 950-900 High Mass, Night Vent, Cooling | -2.128 | -1.8658 | -1.765 | -1.7818 | -1.8317 | -1.6255 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
315 | 22 | 29.4 | 30.5149 | 28.3418 | 26.4922 | 27.47 | 26.0008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 960-900 High Mass, Sunspace, Heating | #N/A | 1.1432 | 1.18 | 1.0254 | 1.0392 | 1.0455 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
316 | 23 | 28.4 | 29.9001 | 27.7806 | 25.8183 | 26.76 | 25.3028 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 960-900 High Mass, Sunspace, Cooling | #N/A | -1.538 | -1.474 | -1.5816 | -1.5381 | -1.4782 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
317 | 24 | 27.4 | 29.355 | 27.2948 | 25.2512 | 26.21 | 24.7283 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
BESTEST BASIC Thermostat, Ventilation and Sunspace (Delta) Peak Heating and Cooling
[23 empty] | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | CASES | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | USA DATE: 0; USA HR: 0; USA KW: 0; UK-BRE DATE: 0; UK-BRE HR: 0; UK-BRE KW: Tested Prg
[22 empty] | 640-600 Low Mass, Tstat Setback, Heating | 1.378 | 1.2022 | 1.623 | 1.3541 | 0.873 | 0.67965 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 940-900 High Mass, Tstat Setback, Heating | 1.331 | 0.60852 | 1.206 | 0.45528 | 0.489 | 0.62635 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 650-600 Low Mass, Night Vent, Cooling | -0.002 | -0.19129 | -0.377 | -0.21342 | -0.232 | -0.24825 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
[22 empty] | 950-900 High Mass, Night Vent, Cooling | -0.673 | -1.0129 | -0.502 | -0.65292 | -0.694 | -0.70368 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
| FREE-FLOAT CASES | [20 empty] | 960-900 High Mass, Sunspace, Heating | #N/A | -0.31135 | -0.368 | -0.42812 | -0.432 | -0.47808 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
| HOURLY ANNUAL ZONE TEMPERATURE BIN DATA | [20 empty] | 960-900 High Mass, Sunspace, Cooling | #N/A | -1.9993 | -1.189 | -1.5605 | -1.493 | -1.6016 | #N/A | #N/A | #N/A | #N/A | #N/A | USA DATE: #N/A; USA HR: #N/A; USA KW: #N/A; UK-BRE DATE: #N/A; UK-BRE HR: #N/A; UK-BRE KW: #N/A
CASE 900FF
(USE COLUMN B ONLY)
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
# HOURS | TEMP (C) | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS
| = | = | = | = | = | = | = | = | = | [8 empty] | =
330 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
331 | -49 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
332 | -48 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
333 | -47 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
334 | -46 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
335 | -45 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
336 | -44 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
337 | -43 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
338 | -42 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
339 | -41 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
340 | -40 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
341 | -39 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
342 | -38 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
343 | -37 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
344 | -36 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
345 | -35 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
346 | -34 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
347 | -33 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
348 | -32 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
349 | -31 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
350 | -30 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
351 | -29 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
352 | -28 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
353 | -27 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
354 | -26 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
355 | -25 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
356 | -24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
357 | -23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
358 | -22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
359 | -21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
360 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
361 | -19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
362 | -18 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
363 | -17 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
364 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
365 | -15 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
366 | -14 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
367 | -13 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
368 | -12 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
369 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
370 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
371 | -9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
372 | -8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
373 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
374 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
375 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
376 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
377 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
378 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
379 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
380 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
381 | 1 | 13 | 0 | 3 | 4 | 3 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
382 | 2 | 32 | 4 | 8 | 4 | 6 | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
383 | 3 | 41 | 7 | 19 | 20 | 19 | 25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
384 | 4 | 57 | 23 | 32 | 21 | 29 | 24 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
385 | 5 | 63 | 25 | 31 | 39 | 29 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
386 | 6 | 67 | 36 | 42 | 51 | 43 | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
387 | 7 | 87 | 44 | 60 | 63 | 66 | 74 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
388 | 8 | 97 | 65 | 110 | 71 | 74 | 75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
389 | 9 | 104 | 74 | 95 | 83 | 96 | 102 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
390 | 10 | 155 | 98 | 112 | 128 | 110 | 142 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
391 | 11 | 151 | 117 | 155 | 164 | 141 | 184 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
392 | 12 | 142 | 148 | 190 | 218 | 200 | 212 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
393 | 13 | 156 | 211 | 230 | 185 | 203 | 192 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
394 | 14 | 170 | 206 | 229 | 197 | 196 | 204 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
395 | 15 | 166 | 208 | 244 | 253 | 238 | 289 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
396 | 16 | 211 | 255 | 291 | 269 | 271 | 255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
397 | 17 | 199 | 288 | 297 | 241 | 271 | 278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
398 | 18 | 211 | 253 | 334 | 312 | 310 | 351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
399 | 19 | 257 | 329 | 337 | 321 | 340 | 323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
400 | 20 | 318 | 365 | 313 | 337 | 323 | 317 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
401 | 21 | 263 | 323 | 324 | 305 | 319 | 326 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
402 | 22 | 269 | 327 | 267 | 324 | 319 | 306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
403 | 23 | 273 | 316 | 253 | 302 | 285 | 291 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
404 | 24 | 260 | 283 | 252 | 276 | 272 | 280 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
405 | 25 | 308 | 286 | 241 | 296 | 270 | 292 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
406 | 26 | 339 | 299 | 254 | 283 | 270 | 288 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
407 | 27 | 330 | 287 | 241 | 313 | 272 | 330 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
408 | 28 | 341 | 319 | 264 | 302 | 318 | 310 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
409 | 29 | 409 | 340 | 297 | 326 | 296 | 356 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
410 | 30 | 382 | 362 | 298 | 356 | 327 | 383 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
411 | 31 | 426 | 417 | 331 | 386 | 363 | 385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
412 | 32 | 433 | 429 | 377 | 366 | 374 | 411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
413 | 33 | 391 | 417 | 384 | 399 | 403 | 379 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
414 | 34 | 332 | 390 | 411 | 374 | 390 | 338 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
415 | 35 | 291 | 335 | 363 | 315 | 336 | 265 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
416 | 36 | 244 | 272 | 315 | 253 | 292 | 232 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
417 | 37 | 184 | 210 | 255 | 209 | 237 | 161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
418 | 38 | 167 | 150 | 208 | 152 | 178 | 113 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
419 | 39 | 145 | 77 | 132 | 118 | 117 | 71 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
420 | 40 | 102 | 60 | 75 | 64 | 71 | 39 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
421 | 41 | 76 | 40 | 45 | 34 | 45 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
422 | 42 | 41 | 30 | 24 | 17 | 21 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
423 | 43 | 27 | 21 | 12 | 7 | 14 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
424 | 44 | 22 | 11 | 5 | 2 | 3 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
425 | 45 | 5 | 3 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
426 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
427 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
428 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
429 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
430 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
431 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
432 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
433 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
434 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
435 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
436 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
437 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
438 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
439 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
440 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
441 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
442 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
443 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
444 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
445 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
446 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
447 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
448 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
449 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
450 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
451 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
452 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
453 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
454 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
455 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
456 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
457 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
458 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
459 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
460 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
461 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
462 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
463 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
464 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
465 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
466 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
467 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
468 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
469 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
470 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
471 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
472 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
473 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
474 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
475 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
476 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
477 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
478 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = |  | ======== | = | = | [8 empty] | =
| = | = | = | = | = |  | ======== | = | = | [8 empty] | =
| = | = | = | = | = |  | = | = | = | [8 empty] | =
| = | = | = | = | = |  | = | = | = | [8 empty] | =
Data Tables for Figures 47 to 50 to allow Different labels for Series [Note (2019Aug01): Rows 1030 to 1050 appear to be orphaned, not used in charts]
Heating
0
0 | Heating | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 4.565 | 4.855 | 5.145 | 4.6412 | 4.8657 | 4.9081 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 430 Low Mass High Cond. Wall El. | 5.171 | 5.454 | 5.954 | 5.6201 | 5.5449 | 5.8505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 800 High Mass High Cond. Wall El. | 5.141 | 4.9057 | 5.403 | 5.1156 | 4.9798 | 5.3695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Cooling | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 0.021 | 0.007762 | 0.006 | 0.01038 | 0.0055 | 0.0035162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 430 Low Mass High Cond. Wall El. | 1.084 | 0.90616 | 0.944 | 0.85562 | 0.9527 | 0.73902 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 800 High Mass High Cond. Wall El. | 0.473 | 0.37983 | 0.362 | 0.37353 | 0.3914 | 0.28208 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Peak Heating | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 1.948 | 2.1574 | 2.085 | 1.9517 | 2.09 | 2.1613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 430 Low Mass High Cond. Wall El. | 3.3 | 3.2539 | 3.36 | 3.3163 | 3.285 | 3.4088 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 800 High Mass High Cond. Wall El. | 2.957 | 2.7776 | 2.864 | 2.9237 | 2.84 | 2.9669 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Peak Cooling | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
ref | 395 Low Mass Solid Conduction | 0.547 | 0.3575 | 0.308 | 0.37747 | 0.294 | 0.2652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 430 Low Mass High Cond. Wall El. | 2.167 | 1.8398 | 1.84 | 1.9294 | 1.874 | 1.7041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ref | 800 High Mass High Cond. Wall El. | 1.286 | 1.1019 | 1.157 | 1.0458 | 1.052 | 0.93559 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MONTHLY HEATING & COOLING LOAD DATA
Case 600
Monthly Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 663.99 | 655.585 | 672.684 | 711.8797 | 732 | 734.943
1 | Feb | 653.26 | 626.2627 | 635.299 | 682.632 | 682 | 702.079
2 | Mar | 433.508 | 435.7419 | 450.494 | 472.2167 | 481 | 495.001
3 | Apr | 511.036 | 456.9543 | 447.957 | 510.1244 | 479 | 517.287
4 | May | 112.769 | 127.7958 | 128 | 136.8192 | 139 | 150.732
5 | Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512
6 | Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263
7 | Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039
8 | Sep | 51.756 | 74.3067 | 76.741 | 73.317 | 81 | 84.8239
9 | Oct | 316.952 | 328.4088 | 324.148 | 347.7084 | 354 | 367.051
10 | Nov | 598.664 | 575.553 | 585.805 | 625.2596 | 629 | 645.809
11 | Dec | 698.704 | 681.9851 | 697.819 | 735.7303 | 750 | 763.546
| sum | 4049.581 | 3992.755 | 4048.646 | 4324.3743 | 4364 | 4503.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 475.4 | 554.0235 | 417.93 | 521.798 | 523 | 495.012
1 | Feb | 349.2 | 394.2972 | 315.415 | 387.4981 | 398 | 367.404
2 | Mar | 450.3 | 474.3508 | 410.736 | 484.3611 | 489 | 457.384
3 | Apr | 218.7 | 220.1356 | 230.168 | 240.4611 | 263 | 235.357
4 | May | 342.7 | 321.1602 | 338.582 | 339.9139 | 364 | 325.154
5 | Jun | 578.3 | 497.4498 | 526.439 | 539.605 | 550 | 516.057
6 | Jul | 568.4 | 505.8671 | 525.149 | 536.3834 | 556 | 514.389
7 | Aug | 658.2 | 606.5032 | 621.101 | 648.5013 | 674 | 634.136
8 | Sep | 724.8 | 705.1929 | 672.084 | 733.708 | 743 | 710.474
9 | Oct | 628.4 | 676.133 | 611.126 | 675.2687 | 681 | 649.483
10 | Nov | 394.3 | 454.7409 | 377.147 | 437.6814 | 444 | 418.571
11 | Dec | 433.3 | 503.27 | 386.209 | 481.8594 | 476 | 456.103
| sum | 5822 | 5913.1242 | 5432.086 | 6027.0394 | 6161 | 5779.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 3.1 | 3.0202 | 3.036 | 2.9776 | 3.23 | 3.3589
1 | Feb | 3.041 | 2.8997 | 2.922 | 3.0666 | 3.14 | 3.2252
2 | Mar | 2.275 | 2.0344 | 2.065 | 2.1146 | 2.23 | 2.287
3 | Apr | 2.446 | 2.2073 | 2.238 | 2.3223 | 2.38 | 2.4572
4 | May | 1.645 | 1.5922 | 1.569 | 1.6241 | 1.75 | 1.778
5 | Jun | 0.805 | 0.77848 | 0.748 | 0.73243 | 0.76 | 0.8526
6 | Jul | 0.599 | 0.53975 | 0.512 | 0.51445 | 0.57 | 0.61893
7 | Aug | 0.572 | 0.55338 | 0.532 | 0.47852 | 0.56 | 0.59085
8 | Sep | 1.229 | 1.1204 | 1.114 | 1.1295 | 1.19 | 1.2116
9 | Oct | 1.702 | 1.6237 | 1.619 | 1.682 | 1.77 | 1.8132
10 | Nov | 3.255 | 2.8502 | 2.931 | 3.1061 | 3.11 | 3.2066
11 | Dec | 3.171 | 2.9413 | 2.972 | 3.2044 | 3.17 | 3.2781
| max | 3.255 | 3.0202 | 3.036 | 3.2044 | 3.23 | 3.3589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 5.65 | 6.481 | 5.422 | 6.3516 | 6.19 | 6.0457
1 | Feb | 4.9211 | 5.3928 | 4.444 | 5.5373 | 5.42 | 5.1553
2 | Mar | 4.4579 | 5.1483 | 4.252 | 5.0085 | 5.04 | 4.7399
3 | Apr | 3.4735 | 4.0151 | 3.6 | 3.9307 | 4.04 | 3.8027
4 | May | 2.7741 | 3.0796 | 2.894 | 3.0864 | 3.1 | 3.0405
5 | Jun | 3.2526 | 3.2488 | 3.067 | 3.4487 | 3.43 | 3.3792
6 | Jul | 3.3187 | 3.2903 | 3.155 | 3.6284 | 3.64 | 3.4967
7 | Aug | 4.1922 | 4.1195 | 4.038 | 4.672 | 4.7 | 4.6505
8 | Sep | 5.086 | 5.4503 | 4.911 | 5.7148 | 5.58 | 5.4199
9 | Oct | 5.5767 | 6.2702 | 5.278 | 6.2221 | 6.07 | 5.9226
10 | Nov | 5.4759 | 6.149 | 5.229 | 6.194 | 6.03 | 5.824
11 | Dec | 5.537 | 6.45 | 5.294 | 6.251 | 6.12 | 5.9425
| max | 5.65 | 6.481 | 5.422 | 6.3516 | 6.19 | 6.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Case 900
Monthly Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 277.8 | 206.1043 | 275.307 | 255.8355 | 266 | 291.936
1 | Feb | 307.4 | 243.2297 | 292.916 | 294.1814 | 283 | 322.141
2 | Mar | 134.4 | 102.4399 | 119.976 | 125.5424 | 115 | 143.84
3 | Apr | 275.7 | 222.3692 | 214.166 | 268.6543 | 228 | 275.466
4 | May | 20.1 | 33.3469 | 26.771 | 33.4139 | 29 | 37.5028
5 | Jun | 0 | 0 | 0 | 0 | 0 | 0
6 | Jul | 0 | 0 | 0 | 0 | 0 | 0
7 | Aug | 0 | 0 | 0 | 0 | 0 | 0
8 | Sep | 2.1 | 0 | 0 | 0.11241 | 0 | 0.53697
9 | Oct | 80.5 | 65.0694 | 63.591 | 81.0905 | 70 | 85.0098
10 | Nov | 298.2 | 251.5988 | 283.888 | 296.9874 | 286 | 318.242
11 | Dec | 329.8 | 254.733 | 314.279 | 307.8688 | 308 | 339.357
| sum | 1726 | 1378.8913 | 1590.894 | 1663.6867 | 1585 | 1814.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 73.3141 | 67.8041 | 33.493 | 53.2805 | 42 | 44.635
1 | Feb | 24.0087 | 15.1117 | 4.724 | 12.3391 | 11 | 9.2434
2 | Mar | 86.3882 | 68.5488 | 40.898 | 65.3862 | 56 | 50.5508
3 | Apr | 29.344 | 12.3134 | 18.267 | 18.4694 | 22 | 16.0525
4 | May | 131.0941 | 117.8126 | 128.592 | 114.4874 | 125 | 98.3549
5 | Jun | 447.4956 | 372.2992 | 408.473 | 401.3344 | 404 | 365.819
6 | Jul | 440.8962 | 380.4363 | 408.145 | 398.7064 | 410 | 365.513
7 | Aug | 532.6434 | 485.6761 | 510.152 | 510.3174 | 531 | 487.566
8 | Sep | 517.8661 | 484.0294 | 466.106 | 492.837 | 492 | 458.859
9 | Oct | 296.188 | 305.5693 | 269.566 | 292.6655 | 281 | 260.853
10 | Nov | 72.6701 | 80.4854 | 56.214 | 67.9828 | 63 | 60.1796
11 | Dec | 62.0916 | 73.7394 | 38.054 | 60.9353 | 48 | 49.5012
| sum | 2714 | 2463.8258 | 2382.684 | 2488.7414 | 2485 | 2267.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 2.322 | 2.0774 | 2.178 | 1.9028 | 2.2 | 2.3786
1 | Feb | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.63 | 2.7785
2 | Mar | 1.774 | 1.6129 | 1.646 | 1.7443 | 1.76 | 1.8582
3 | Apr | 1.997 | 1.7706 | 1.725 | 2.0036 | 1.93 | 2.0359
4 | May | 1.295 | 1.1425 | 1.124 | 1.2682 | 1.23 | 1.3242
5 | Jun | 0 | 0 |  | 0 | 0 | 0
6 | Jul | 0 | 0 |  | 0 | 0 | 0
7 | Aug | 0 | 0 |  | 0 | 0 | 0
8 | Sep | 0.113 | 0 |  | 0.064157 | 0 | 0.19442
9 | Oct | 1.201 | 1.1882 | 1.158 | 1.3258 | 1.21 | 1.3311
10 | Nov | 2.427 | 2.0863 | 2.201 | 2.3161 | 2.28 | 2.4629
11 | Dec | 2.12 | 1.9268 | 1.981 | 2.1749 | 2.04 | 2.1801
| max | 2.551 | 2.4434 | 2.453 | 2.6875 | 2.63 | 2.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 1.982 | 2.2416 | 1.637 | 2.0779 | 1.81 | 1.8776
1 | Feb | 1.096 | 0.99617 | 0.588 | 0.97943 | 0.85 | 0.82938
2 | Mar | 1.508 | 1.4341 | 1.143 | 1.4931 | 1.27 | 1.4258
3 | Apr | 1.093 | 0.63116 | 1.032 | 0.95262 | 0.95 | 0.83719
4 | May | 1.555 | 1.4272 | 1.446 | 1.5339 | 1.46 | 1.4645
5 | Jun | 2.101 | 1.8967 | 1.873 | 1.9656 | 1.89 | 1.9742
6 | Jul | 2.14 | 1.943 | 1.83 | 2.0681 | 1.97 | 1.975
7 | Aug | 2.632 | 2.4852 | 2.212 | 2.5258 | 2.51 | 2.5337
8 | Sep | 2.961 | 3.1368 | 2.556 | 2.9888 | 2.81 | 2.8712
9 | Oct | 3.039 | 3.3764 | 2.549 | 3.0404 | 2.9 | 2.9401
10 | Nov | 1.982 | 2.2328 | 1.683 | 2.0018 | 1.94 | 1.9406
11 | Dec | 2.069 | 2.1054 | 1.595 | 1.9682 | 1.67 | 1.6903
| max | 3.039 | 3.3764 | 2.556 | 3.0404 | 2.9 | 2.9401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Case 600-900
Monthly Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 386.19 | 449.4807 | 397.377 | 456.0442 | 466 | 443.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Feb | 345.86 | 383.033 | 342.383 | 388.4505 | 399 | 379.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Mar | 299.108 | 333.302 | 330.518 | 346.6743 | 366 | 351.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Apr | 235.336 | 234.5851 | 233.791 | 241.4701 | 251 | 241.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | May | 92.669 | 94.449 | 101.229 | 103.4052 | 110 | 113.2292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Jun | 2.735 | 11.6999 | 11.218 | 10.0812 | 14 | 15.9512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Jul | 4.839 | 11.5431 | 10.105 | 12.0182 | 14 | 16.7263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Aug | 1.368 | 6.9186 | 8.376 | 6.5877 | 9 | 9.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Sep | 49.656 | 74.3067 | 76.741 | 73.2046 | 81 | 84.2869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Oct | 236.452 | 263.3394 | 260.557 | 266.6179 | 284 | 282.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Nov | 300.464 | 323.9542 | 301.917 | 328.2722 | 343 | 327.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Dec | 368.904 | 427.2521 | 383.54 | 427.8615 | 442 | 424.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 402.0859 | 486.2194 | 384.437 | 468.5175 | 481 | 450.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Feb | 325.1913 | 379.1855 | 310.691 | 375.159 | 387 | 358.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Mar | 363.9118 | 405.8019 | 369.838 | 418.9749 | 433 | 406.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Apr | 189.356 | 207.8222 | 211.901 | 221.9916 | 241 | 219.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | May | 211.6059 | 203.3476 | 209.99 | 225.4265 | 239 | 226.7991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Jun | 130.8044 | 125.1506 | 117.966 | 138.2706 | 146 | 150.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Jul | 127.5038 | 125.4308 | 117.004 | 137.6771 | 146 | 148.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Aug | 125.5566 | 120.8271 | 110.949 | 138.1839 | 143 | 146.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Sep | 206.9339 | 221.1635 | 205.978 | 240.871 | 251 | 251.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Oct | 332.212 | 370.5637 | 341.56 | 382.6032 | 400 | 388.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Nov | 321.6299 | 374.2554 | 320.933 | 369.6986 | 381 | 358.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Dec | 371.2084 | 429.5306 | 348.155 | 420.9241 | 428 | 406.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Heating Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 0.778 | 0.94282 | 0.858 | 1.0748 | 1.03 | 0.98026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Feb | 0.49 | 0.45628 | 0.469 | 0.37915 | 0.51 | 0.4467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Mar | 0.501 | 0.42158 | 0.419 | 0.37021 | 0.47 | 0.42882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Apr | 0.449 | 0.43669 | 0.513 | 0.31865 | 0.45 | 0.42125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | May | 0.35 | 0.44976 | 0.445 | 0.35588 | 0.52 | 0.45382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Jun | 0.805 | 0.77848 | 0.748 | 0.73243 | 0.76 | 0.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Jul | 0.599 | 0.53975 | 0.512 | 0.51445 | 0.57 | 0.61893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Aug | 0.572 | 0.55338 | 0.532 | 0.47852 | 0.56 | 0.59085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Sep | 1.116 | 1.1204 | 1.114 | 1.0654 | 1.19 | 1.0172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Oct | 0.501 | 0.43546 | 0.461 | 0.35615 | 0.56 | 0.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Nov | 0.828 | 0.76387 | 0.73 | 0.78997 | 0.83 | 0.74371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Dec | 1.051 | 1.0145 | 0.991 | 1.0296 | 1.13 | 1.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Peak Cooling Loads
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Jan | 3.668 | 4.2394 | 3.785 | 4.2737 | 4.38 | 4.1681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Feb | 3.8251 | 4.3966 | 3.856 | 4.5578 | 4.57 | 4.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Mar | 2.9499 | 3.7143 | 3.109 | 3.5155 | 3.77 | 3.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Apr | 2.3805 | 3.3839 | 2.568 | 2.9781 | 3.09 | 2.9655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | May | 1.2191 | 1.6524 | 1.448 | 1.5525 | 1.64 | 1.5759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Jun | 1.1516 | 1.3521 | 1.194 | 1.4832 | 1.54 | 1.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Jul | 1.1787 | 1.3473 | 1.325 | 1.5603 | 1.67 | 1.5217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Aug | 1.5602 | 1.6343 | 1.826 | 2.1462 | 2.19 | 2.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Sep | 2.125 | 2.3135 | 2.355 | 2.726 | 2.77 | 2.5488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Oct | 2.5377 | 2.8938 | 2.729 | 3.1817 | 3.17 | 2.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Nov | 3.4939 | 3.9162 | 3.546 | 4.1922 | 4.09 | 3.8834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Dec | 3.468 | 4.3446 | 3.699 | 4.2828 | 4.45 | 4.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOURLY HEATING & COOLING LOAD DATA
CASE 600 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 2.032 | 1.8838 | 1.9869 | 2.1523 | 2.08 | 2.1718 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 2.042 | 1.9935 | 2.0692 | 2.2223 | 2.22 | 2.271 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 2.123 | 2.0547 | 2.1291 | 2.2757 | 2.3 | 2.3414 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 2.228 | 2.1202 | 2.2065 | 2.3283 | 2.38 | 2.4106 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 2.307 | 2.1532 | 2.243 | 2.351 | 2.42 | 2.4393 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 2.358 | 2.1631 | 2.2675 | 2.3515 | 2.43 | 2.4505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 2.385 | 2.1843 | 2.2778 | 2.3551 | 2.46 | 2.4648 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 2.101 | 1.7765 | 2.1196 | 1.8832 | 2.09 | 1.7476 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 1.048 | 0.5478 | 1.2032 | 0.49397 | 0.79 | 0.29604 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0.139 | 0 | 0 | 0 | 0 | -0.15773 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.07 | -0.92066 | -0.3574 | -1.3089 | -1.28 | -1.3665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.616 | -3.0739 | -2.2142 | -3.4074 | -3.36 | -3.2336 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -3.561 | -4.364 | -3.4723 | -4.6741 | -4.69 | -4.4188 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -4.028 | -4.6667 | -4.0214 | -4.9334 | -5.08 | -4.5996 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -3.839 | -4.0529 | -4.0239 | -4.1722 | -4.39 | -3.9649 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -3.244 | -2.8873 | -3.4753 | -2.9277 | -3.24 | -2.8274 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.197 | -1.329 | -2.3221 | -1.2391 | -1.59 | -1.1647 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -0.779 | -0.036587 | -0.6489 | -0.019928 | -0.12 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 0 | 0.047689 | 0 | 0.086501 | 0.1 | 0.36036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0 | 0.87302 | 0.1486 | 0.98137 | 1 | 1.0287 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0.413 | 1.5518 | 1.0979 | 1.6393 | 1.7 | 1.6719 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 1.266 | 1.9363 | 1.6738 | 2.0595 | 2.1 | 2.1066 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 1.814 | 2.1702 | 2.0148 | 2.3234 | 2.36 | 2.3929 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 1.988 | 2.2658 | 2.1963 | 2.4352 | 2.47 | 2.5229 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 600 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0 | 0 | 0 | 0 | 0.04 | 0.094557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0 | 0 | 0 | 0 | 0.09 | 0.038588 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.332 | -0.16869 | -0.0988 | -0.35948 | -0.23 | -0.36749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -1.246 | -1.2347 | -1.022 | -1.4584 | -1.21 | -1.2888 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -2.078 | -2.2634 | -1.7729 | -2.4228 | -2.22 | -2.1777 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -2.457 | -2.7049 | -2.3147 | -2.8449 | -2.78 | -2.6489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -2.618 | -2.7504 | -2.5989 | -2.9085 | -2.93 | -2.7498 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -2.588 | -2.449 | -2.594 | -2.641 | -2.72 | -2.5224 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -2.388 | -1.9631 | -2.3269 | -2.2096 | -2.33 | -2.0736 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.096 | -1.5159 | -1.9515 | -1.7631 | -1.88 | -1.6698 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.763 | -1.1667 | -1.5665 | -1.37 | -1.49 | -1.3003 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.404 | -0.84578 | -1.1763 | -0.98285 | -1.1 | -0.91574 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -0.995 | -0.48174 | -0.7328 | -0.56694 | -0.64 | -0.50284 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -0.593 | -0.1626 | -0.2983 | -0.231 | -0.24 | -0.19628 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.32 | -0.010249 | -0.0186 | -0.04743 | -0.04 | -0.0091138 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.138 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.027 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 900 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0.792 | 0.71655 | 1.0685 | 0.97734 | 0.91 | 1.0334 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0.928 | 0.84236 | 1.1715 | 1.0829 | 1.06 | 1.1534 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 1.063 | 0.94623 | 1.2675 | 1.1826 | 1.17 | 1.2628 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 1.187 | 1.0458 | 1.3715 | 1.2862 | 1.27 | 1.3755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 1.296 | 1.1187 | 1.4399 | 1.366 | 1.36 | 1.4592 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 1.412 | 1.1879 | 1.5162 | 1.4385 | 1.43 | 1.5326 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 1.54 | 1.2589 | 1.5722 | 1.5049 | 1.51 | 1.6045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 1.45 | 1.0863 | 1.5519 | 1.3243 | 1.42 | 1.3557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0.724 | 0.53703 | 1.1996 | 0.79271 | 0.93 | 0.77638 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0.149 | 0.11777 | 0.58712 | 0.26716 | 0.38 | 0.24812 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | 0 | 0 | 0 | 0 | 0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -0.128 | -0.02487 | 0 | -0.046329 | -0.06 | -0.0097877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -0.128 | -0.0054093 | 0 | -0.027472 | -0.08 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 0 | 0 | 0 | 0 | 0 | 0.096471 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 0.183 | 0.081877 | 0.040877 | 0.17522 | 0.05 | 0.30642 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 0.342 | 0.29481 | 0.24467 | 0.39699 | 0.28 | 0.52323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 900 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.223 | -0.052736 | -0.11986 | -0.10115 | -0.17 | -0.030013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | -0.069 | -0.0012209 | -0.038655 | -0.030142 | -0.09 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | -0.012 | 0 | 0 | 0 | -0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 0 | 0 | 0 | -0.016529 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | -0.128 | -0.070157 | -0.11228 | -0.15912 | -0.11 | -0.090224 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.453 | -0.36695 | -0.36477 | -0.41739 | -0.31 | -0.31161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.771 | -0.76666 | -0.66069 | -0.76505 | -0.61 | -0.65319 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.234 | -1.1411 | -0.94273 | -1.1012 | -0.94 | -0.9806 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -1.545 | -1.3558 | -1.1934 | -1.3309 | -1.21 | -1.22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -1.667 | -1.4518 | -1.3604 | -1.4697 | -1.38 | -1.3604 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -1.652 | -1.3908 | -1.413 | -1.4822 | -1.44 | -1.3762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -1.581 | -1.2243 | -1.3583 | -1.399 | -1.38 | -1.275 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -1.472 | -1.0839 | -1.2639 | -1.291 | -1.3 | -1.1791 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.343 | -0.97268 | -1.1433 | -1.1649 | -1.2 | -1.0627 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.201 | -0.8477 | -1.0072 | -1.0134 | -1.07 | -0.91459 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -1.018 | -0.71147 | -0.84822 | -0.84554 | -0.92 | -0.75544 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -0.832 | -0.58603 | -0.70104 | -0.70239 | -0.77 | -0.62069 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.661 | -0.48581 | -0.59136 | -0.59073 | -0.65 | -0.50904 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.492 | -0.39359 | -0.48628 | -0.48864 | -0.54 | -0.40721 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.371 | -0.28879 | -0.37086 | -0.37539 | -0.42 | -0.29064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 640 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0.00043451 | 0.025 | 0.082706 | 0.08 | 0.11565 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0 | 0.39261 | 0.611 | 0.54755 | 0.6 | 0.62194 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 0.459 | 0.80293 | 0.951 | 0.91754 | 0.99 | 0.95848 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 1.053 | 1.034 | 1.19 | 1.1473 | 1.21 | 1.1918 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 1.231 | 1.1731 | 1.321 | 1.2747 | 1.35 | 1.3222 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 1.272 | 1.2448 | 1.402 | 1.3397 | 1.42 | 1.4041 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 1.306 | 1.3018 | 1.445 | 1.3839 | 1.48 | 1.466 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 3.487 | 3.0205 | 3.844 | 3.3808 | 3.06 | 2.5037 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 3.024 | 1.6521 | 2.167 | 1.7525 | 1.94 | 1.4631 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0.185 | 0.075395 | 0.159 | 0.053533 | 0.15 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.068 | -0.40515 | 0 | -0.67412 | -0.7 | -1.0953 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.581 | -2.6298 | -1.927 | -3.0125 | -2.96 | -2.69 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -3.487 | -4.1733 | -3.305 | -4.5085 | -4.51 | -4.1451 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -3.945 | -4.592 | -3.923 | -4.868 | -5 | -4.4711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -3.759 | -4.0239 | -3.966 | -4.1472 | -4.36 | -3.9067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -3.243 | -2.8759 | -3.441 | -2.918 | -3.23 | -2.8007 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.215 | -1.3246 | -2.302 | -1.2353 | -1.59 | -1.1527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -0.786 | -0.036104 | -0.637 | -0.019589 | -0.1 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 0 | 0.048108 | 0 | 0.087045 | 0.1 | 0.36164 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0 | 0.87401 | 0.155 | 0.98216 | 1 | 1.0323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0.401 | 1.5523 | 1.102 | 1.6398 | 1.7 | 1.6738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 1.239 | 1.9366 | 1.676 | 2.0598 | 2.1 | 2.1079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 1.781 | 2.1703 | 2.016 | 2.3235 | 2.36 | 2.3936 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 0.082 | 0 | 0 | 0 | 0.32 | 0.8527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 660 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.803 | 1.6843 | 1.835 | 1.8505 | 1.79 | 1.8233 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 1.782 | 1.779 | 1.901 | 1.9038 | 1.89 | 1.8954 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 1.82 | 1.8309 | 1.95 | 1.9434 | 1.94 | 1.9466 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 1.881 | 1.8839 | 2.017 | 1.9828 | 2 | 1.9958 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 1.923 | 1.9135 | 2.048 | 1.9989 | 2.04 | 2.0162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 1.952 | 1.9223 | 2.071 | 2.0006 | 2.05 | 2.028 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 1.969 | 1.9415 | 2.078 | 2.0091 | 2.08 | 2.0459 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 1.804 | 1.6726 | 1.966 | 1.7123 | 1.86 | 1.6135 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 1.191 | 0.80151 | 1.334 | 0.82326 | 1.01 | 0.71656 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0.37 | 0.082875 | 0.264 | 0.061784 | 0.13 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | 0 | -0.45456 | -0.147 | -0.49567 | -0.47 | -0.52411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -0.545 | -1.6509 | -1.232 | -1.6957 | -1.63 | -1.5139 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -1.376 | -2.1461 | -1.705 | -2.1841 | -2.18 | -1.8748 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -1.55 | -1.9151 | -1.796 | -1.8726 | -1.95 | -1.6375 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -1.192 | -1.281 | -1.52 | -1.2021 | -1.37 | -1.0626 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -0.576 | -0.38043 | -0.843 | -0.29981 | -0.49 | -0.18596 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -0.102 | 0 | 0 | 0 | -0.02 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 0 | 0.068677 | 0 | 0.10283 | 0.08 | 0.24487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0.061 | 0.85087 | 0.486 | 0.84738 | 0.87 | 0.90071 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0.76 | 1.4115 | 1.198 | 1.4079 | 1.46 | 1.4225 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 1.518 | 1.7543 | 1.641 | 1.7785 | 1.81 | 1.792 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 1.701 | 1.9598 | 1.904 | 2.0051 | 2.03 | 2.0235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 1.801 | 2.0439 | 2.043 | 2.1 | 2.13 | 2.1255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 660 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.141 | -0.059292 | 0 | -0.16326 | -0.08 | -0.17059 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.797 | -0.78553 | -0.775 | -0.88657 | -0.65 | -0.72317 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.474 | -1.5756 | -1.407 | -1.5988 | -1.38 | -1.35 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -1.707 | -1.9242 | -1.85 | -1.9127 | -1.81 | -1.6997 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -1.809 | -2.0023 | -2.099 | -2.0065 | -1.97 | -1.8273 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -1.824 | -1.8527 | -2.135 | -1.9013 | -1.92 | -1.7611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -1.741 | -1.5702 | -1.953 | -1.6894 | -1.75 | -1.5425 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -1.567 | -1.2726 | -1.664 | -1.4112 | -1.49 | -1.3035 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.335 | -1.0133 | -1.354 | -1.1343 | -1.23 | -1.0574 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.08 | -0.76378 | -1.034 | -0.84941 | -0.95 | -0.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -0.775 | -0.45877 | -0.657 | -0.52226 | -0.59 | -0.46077 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -0.461 | -0.17946 | -0.275 | -0.24015 | -0.24 | -0.21189 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.247 | -0.026977 | -0.028 | -0.081429 | -0.07 | -0.05591 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.107 | 0 | 0 | -0.0055834 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.022 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 670 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 2.67 | 2.3394 | 2.545 | 2.6246 | 2.68 | 2.7706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 2.694 | 2.4806 | 2.631 | 2.7315 | 2.95 | 2.9307 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 2.819 | 2.5674 | 2.707 | 2.8196 | 3.1 | 3.0517 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 2.973 | 2.6744 | 2.81 | 2.9079 | 3.24 | 3.1786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 3.088 | 2.7158 | 2.851 | 2.9498 | 3.31 | 3.2358 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 3.145 | 2.7285 | 2.88 | 2.9434 | 3.31 | 3.2352 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 3.154 | 2.7542 | 2.899 | 2.9242 | 3.3 | 3.2195 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 2.796 | 2.2606 | 2.693 | 2.3743 | 2.84 | 2.3857 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 1.524 | 0.84369 | 1.593 | 0.72924 | 1.21 | 0.68716 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0.298 | 0.0024258 | 0 | 0 | 0.02 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | 0 | -0.99799 | -0.306 | -1.2959 | -1.14 | -1.2316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.564 | -3.2655 | -2.277 | -3.5295 | -3.35 | -3.1719 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -3.679 | -4.6214 | -3.608 | -4.9384 | -4.86 | -4.5095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -4.214 | -4.8903 | -4.154 | -5.1408 | -5.1 | -4.5907 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -3.989 | -4.1429 | -4.118 | -4.1667 | -3.94 | -3.7353 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -3.33 | -2.8645 | -3.498 | -2.7773 | -2.63 | -2.4556 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.176 | -1.1447 | -2.216 | -0.98623 | -0.94 | -0.70988 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -0.736 | 0 | -0.314 | 0 | -0.02 | 0.1031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 0 | 0.3733 | 0 | 0.4619 | 0.72 | 0.78486 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0.146 | 1.5232 | 0.909 | 1.6223 | 1.84 | 1.8058 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 1.072 | 2.1392 | 1.818 | 2.2179 | 2.4 | 2.3956 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 2.06 | 2.4968 | 2.378 | 2.6015 | 2.75 | 2.8009 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 2.396 | 2.7218 | 2.707 | 2.8785 | 3.03 | 3.1203 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 2.613 | 2.8049 | 2.874 | 2.9941 | 3.11 | 3.2615 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 670 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 0 | 0.001611 | 0.131 | 0 | 0.12 | 0.13713 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0 | 0.20148 | 0.363 | 0.11574 | 0.33 | 0.32542 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0 | 0.20839 | 0.33 | 0.10059 | 0.29 | 0.22218 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0 | 0.0044408 | 0.012 | 0 | 0.02 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.324 | -0.19006 | -0.047 | -0.42413 | -0.26 | -0.44642 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -1.402 | -1.5089 | -1.187 | -1.7545 | -1.43 | -1.5147 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -2.485 | -2.7261 | -2.107 | -2.8853 | -2.61 | -2.5624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -2.996 | -3.2555 | -2.761 | -3.3784 | -3.26 | -3.1183 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -3.234 | -3.3127 | -3.092 | -3.4483 | -3.42 | -3.2401 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -3.202 | -2.9394 | -3.061 | -3.1098 | -3.14 | -2.9531 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -2.922 | -2.2909 | -2.681 | -2.5271 | -2.61 | -2.3467 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.521 | -1.6885 | -2.156 | -1.9379 | -2.01 | -1.8239 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -2.084 | -1.2498 | -1.647 | -1.4631 | -1.54 | -1.3771 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.63 | -0.8713 | -1.164 | -1.0152 | -1.09 | -0.93641 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -1.128 | -0.45588 | -0.649 | -0.55242 | -0.58 | -0.46799 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -0.642 | -0.099993 | -0.157 | -0.17822 | -0.14 | -0.1179 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.314 | 0 | 0 | -0.0080085 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.097 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 680 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.186 | 0.99585 | 1.044 | 1.2516 | 1.17 | 1.2499 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 1.246 | 1.1111 | 1.154 | 1.3644 | 1.32 | 1.3728 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 1.341 | 1.1938 | 1.232 | 1.4425 | 1.42 | 1.4629 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 1.44 | 1.2656 | 1.301 | 1.5049 | 1.5 | 1.5405 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 1.514 | 1.2984 | 1.332 | 1.5323 | 1.55 | 1.5779 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 1.565 | 1.3219 | 1.366 | 1.5467 | 1.57 | 1.5974 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 1.591 | 1.3375 | 1.375 | 1.5469 | 1.59 | 1.609 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 1.327 | 1.0054 | 1.238 | 1.1609 | 1.3 | 1.0329 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0.532 | 0.17368 | 0.416 | 0.15573 | 0.34 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0 | -0.053007 | 0 | -0.11857 | -0.1 | -0.73104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.759 | -1.9332 | -1.145 | -2.26 | -1.98 | -2.2417 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -2.604 | -4.069 | -2.926 | -4.3177 | -4.13 | -4.1403 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -4.128 | -5.3127 | -4.197 | -5.523 | -5.48 | -5.2985 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -4.575 | -5.5694 | -4.805 | -5.7122 | -5.85 | -5.4915 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -4.445 | -5.054 | -4.909 | -5.0803 | -5.23 | -4.9288 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -3.918 | -3.941 | -4.446 | -3.9171 | -4.14 | -3.8545 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.906 | -2.3532 | -3.389 | -2.2347 | -2.55 | -2.2038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.436 | -0.51365 | -1.841 | -0.36295 | -0.61 | -0.27043 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -0.295 | 0 | -0.479 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0 | 0.064176 | 0 | 0.26604 | 0.2 | 0.39438 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 0 | 0.54736 | 0 | 0.76843 | 0.72 | 0.79929 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 0.333 | 0.88344 | 0.516 | 1.0956 | 1.08 | 1.1242 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 0.92 | 1.0938 | 0.89 | 1.3198 | 1.29 | 1.3463 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 680 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.017 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.291 | -0.18419 | -0.168 | -0.32663 | -0.19 | -0.33152 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.988 | -1.0716 | -0.86 | -1.2062 | -0.99 | -1.094 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.632 | -1.9293 | -1.497 | -2.0156 | -1.84 | -1.892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -2.018 | -2.4066 | -2.001 | -2.5062 | -2.42 | -2.3763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -2.189 | -2.4752 | -2.264 | -2.6048 | -2.61 | -2.493 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -2.124 | -2.1675 | -2.242 | -2.348 | -2.42 | -2.2637 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -1.896 | -1.6634 | -1.981 | -1.8957 | -2 | -1.8199 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -1.645 | -1.2613 | -1.642 | -1.505 | -1.59 | -1.4619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.403 | -0.97604 | -1.311 | -1.1869 | -1.27 | -1.1511 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.131 | -0.7202 | -1.003 | -0.87653 | -0.95 | -0.8396 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -0.832 | -0.4781 | -0.694 | -0.57282 | -0.63 | -0.54058 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -0.555 | -0.27107 | -0.415 | -0.33075 | -0.37 | -0.30722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.363 | -0.12549 | -0.215 | -0.16755 | -0.18 | -0.14209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.224 | -0.025991 | -0.064 | -0.053704 | -0.05 | -0.022857 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.097 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 685 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 2.05 | 1.9212 | 2.033 | 2.1861 | 2.12 | 2.2164 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 2.059 | 2.0146 | 2.096 | 2.2406 | 2.25 | 2.2966 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 2.139 | 2.0666 | 2.145 | 2.2855 | 2.32 | 2.3561 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 2.243 | 2.1268 | 2.216 | 2.3336 | 2.39 | 2.4196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 2.321 | 2.1569 | 2.249 | 2.3538 | 2.43 | 2.4442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 2.373 | 2.1651 | 2.271 | 2.353 | 2.44 | 2.4533 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 2.401 | 2.1854 | 2.28 | 2.3559 | 2.46 | 2.4668 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 2.118 | 1.777 | 2.121 | 1.8836 | 2.09 | 1.7486 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 1.068 | 0.54801 | 1.204 | 0.46459 | 0.77 | 0.29652 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.479 | -0.95761 | -0.399 | -1.3367 | -1.11 | -1.3527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -1.956 | -2.8606 | -2.012 | -3.2585 | -3.12 | -3.1162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -3.25 | -4.335 | -3.385 | -4.6823 | -4.62 | -4.5191 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -4.289 | -5.2497 | -4.382 | -5.6082 | -5.6 | -5.4071 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -4.731 | -5.3818 | -4.783 | -5.7135 | -5.83 | -5.4259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -4.545 | -4.6926 | -4.698 | -4.881 | -5.07 | -4.6952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -3.952 | -3.486 | -4.099 | -3.5937 | -3.87 | -3.5095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.904 | -1.8707 | -2.915 | -1.876 | -2.21 | -1.8248 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.365 | -0.062132 | -1.224 | 0.036899 | -0.2 | 0.12836 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 0.009 | 1.0222 | 0.257 | 1.1009 | 1.07 | 1.0762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0.767 | 1.6012 | 1.116 | 1.6905 | 1.71 | 1.6727 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 1.239 | 1.9179 | 1.645 | 2.0307 | 2.05 | 2.0601 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 1.583 | 2.1437 | 1.993 | 2.2766 | 2.3 | 2.3472 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 1.841 | 2.2881 | 2.203 | 2.4412 | 2.48 | 2.5334 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 2.007 | 2.3327 | 2.307 | 2.4984 | 2.54 | 2.6039 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 685 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.449 | -0.049027 | 0 | -0.084479 | -0.04 | -0.052034 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | -0.286 | 0.02692 | 0.078 | -0.025064 | 0.05 | 0.025254 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | -0.155 | 0.11975 | 0.158 | 0.056452 | 0.13 | 0.145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | -0.017 | 0.24941 | 0.244 | 0.17529 | 0.26 | 0.27949 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0.11 | 0.34005 | 0.332 | 0.27165 | 0.35 | 0.37362 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0.048 | 0.23558 | 0.247 | 0.16084 | 0.26 | 0.21087 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | -0.274 | -0.1131 | -0.069 | -0.13512 | -0.09 | -0.099433 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | -0.664 | -0.4792 | -0.457 | -0.53511 | -0.45 | -0.45575 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | -1.032 | -0.89805 | -0.861 | -1.0194 | -0.91 | -0.92639 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -1.499 | -1.5518 | -1.365 | -1.7043 | -1.55 | -1.6327 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -2.125 | -2.3959 | -1.979 | -2.5672 | -2.36 | -2.4664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -2.709 | -3.1327 | -2.56 | -3.316 | -3.14 | -3.1511 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -3.08 | -3.4278 | -3.004 | -3.614 | -3.55 | -3.4891 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -3.24 | -3.4049 | -3.231 | -3.6138 | -3.63 | -3.5104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -3.208 | -3.0702 | -3.192 | -3.3078 | -3.37 | -3.232 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -3.006 | -2.5639 | -2.905 | -2.8517 | -2.95 | -2.7482 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.716 | -2.101 | -2.518 | -2.3954 | -2.49 | -2.3306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -2.389 | -1.7475 | -2.126 | -1.9943 | -2.09 | -1.9487 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -2.036 | -1.4176 | -1.731 | -1.5926 | -1.68 | -1.5442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -1.631 | -1.0309 | -1.285 | -1.1479 | -1.19 | -1.089 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -1.237 | -0.69086 | -0.849 | -0.78159 | -0.76 | -0.75479 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.974 | -0.49742 | -0.569 | -0.5735 | -0.51 | -0.54994 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.798 | -0.37088 | -0.383 | -0.43593 | -0.35 | -0.40268 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.634 | -0.25271 | -0.228 | -0.30738 | -0.23 | -0.26193 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 695 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.225 | 1.145 | 1.202 | 1.384 | 1.31 | 1.3877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 1.264 | 1.2047 | 1.253 | 1.4443 | 1.41 | 1.4641 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 1.356 | 1.2518 | 1.293 | 1.4903 | 1.48 | 1.5223 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 1.453 | 1.3012 | 1.34 | 1.5334 | 1.54 | 1.578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 1.526 | 1.3204 | 1.356 | 1.5491 | 1.57 | 1.6015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 1.577 | 1.3355 | 1.381 | 1.5567 | 1.59 | 1.612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 1.604 | 1.3459 | 1.385 | 1.5531 | 1.6 | 1.6183 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 1.34 | 1.0098 | 1.243 | 1.1644 | 1.31 | 1.0378 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0.363 | 0.059474 | 0.42 | -0.078065 | 0.25 | -0.27649 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -1.088 | -1.666 | -1.046 | -2.0066 | -1.63 | -2.0859 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -2.496 | -3.5885 | -2.585 | -3.9354 | -3.67 | -3.8622 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -3.726 | -5.0849 | -3.941 | -5.3726 | -5.21 | -5.2547 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -4.673 | -5.993 | -4.962 | -6.2586 | -6.22 | -6.1055 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -5.066 | -6.0919 | -5.418 | -6.2995 | -6.42 | -6.1336 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -4.931 | -5.5054 | -5.427 | -5.6031 | -5.73 | -5.4801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -4.405 | -4.3565 | -4.905 | -4.3995 | -4.6 | -4.3483 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -3.392 | -2.7253 | -3.811 | -2.7038 | -3 | -2.6911 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.92 | -0.87523 | -2.24 | -0.72678 | -1.02 | -0.72316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -0.65 | 0.15843 | -0.863 | 0.31916 | 0.18 | 0.26566 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0.037 | 0.60708 | -0.003 | 0.74894 | 0.67 | 0.73538 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0.474 | 0.89914 | 0.556 | 1.0411 | 1 | 1.0332 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 0.783 | 1.1068 | 0.926 | 1.2788 | 1.24 | 1.2825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 1.011 | 1.2559 | 1.153 | 1.4531 | 1.42 | 1.4716 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 1.167 | 1.3349 | 1.283 | 1.5445 | 1.52 | 1.5777 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 695 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.422 | -0.13418 | -0.139 | -0.15693 | -0.14 | -0.13755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | -0.302 | -0.081538 | -0.074 | -0.10057 | -0.07 | -0.073529 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | -0.209 | -0.026795 | -0.009 | -0.041091 | -0.02 | -0.00087619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | -0.115 | 0.034874 | 0.053 | 0.017247 | 0.04 | 0.071603 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | -0.023 | 0.098044 | 0.115 | 0.071385 | 0.11 | 0.13714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | -0.05 | 0.064405 | 0.057 | 0.032137 | 0.09 | 0.08276 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | -0.242 | -0.089405 | -0.106 | -0.1231 | -0.06 | -0.096297 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | -0.499 | -0.3116 | -0.331 | -0.38175 | -0.3 | -0.34347 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | -0.773 | -0.61456 | -0.603 | -0.73521 | -0.63 | -0.68893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -1.133 | -1.1481 | -0.989 | -1.2892 | -1.14 | -1.2695 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -1.62 | -1.8678 | -1.499 | -2.0148 | -1.84 | -1.9765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -2.108 | -2.5371 | -2.03 | -2.6747 | -2.53 | -2.6266 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -2.48 | -2.9109 | -2.469 | -3.0711 | -3 | -3.0055 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -2.649 | -2.9258 | -2.692 | -3.1133 | -3.12 | -3.0535 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -2.582 | -2.5909 | -2.645 | -2.8203 | -2.88 | -2.7773 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -2.354 | -2.0688 | -2.368 | -2.3445 | -2.44 | -2.3013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.106 | -1.6542 | -2.019 | -1.947 | -2.02 | -1.9323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.864 | -1.3655 | -1.681 | -1.6239 | -1.69 | -1.612 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.593 | -1.1029 | -1.37 | -1.3044 | -1.36 | -1.2859 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -1.295 | -0.84841 | -1.058 | -0.98545 | -1.03 | -0.96142 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -1.02 | -0.63671 | -0.778 | -0.73214 | -0.75 | -0.71544 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.83 | -0.49022 | -0.577 | -0.56394 | -0.55 | -0.55005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.691 | -0.38407 | -0.425 | -0.44324 | -0.41 | -0.42662 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.562 | -0.28879 | -0.297 | -0.3341 | -0.31 | -0.31199 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 940 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 1.097 | 0.90177 | 2.4441 | 1.2639 | 1.13 | 1.2786 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 1.669 | 1.1161 | 1.9321 | 1.5508 | 1.7 | 1.5794 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0.62 | 0.49385 | 1.2397 | 0.82256 | 0.91 | 0.84183 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | 0.047 | 0.066615 | 0.51559 | 0.29741 | 0.44 | 0.30366 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | 0 | 0 | 0 | 0 | 0.04 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0 | 0 | 0 | 0 | 0 | 0.09175 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0 | 0.086615 | 0.01799 | 0.12095 | 0.02 | 0.27159 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 0.041 | 0.33452 | 0.26925 | 0.38542 | 0.25 | 0.52154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 0.243 | 0.54165 | 0.46845 | 0.61003 | 0.52 | 0.73879 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 0.202 | 0 | 0 | 0 | 0.08 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 980 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | #N/A | 0 | 0 | 0.010067 | 0 | 0.092844 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | #N/A | 0 | 0 | 0.11176 | 0 | 0.21749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0.072 | 0 | 0 | 0.22968 | 0.1 | 0.32564 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0.211 | 0 | 0.018134 | 0.32252 | 0.22 | 0.41999 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 0.078 | 0 | 0.047822 | 0.19642 | 0.19 | 0.23403 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | #N/A | 0 | 0 | 0 | 0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | #N/A | -0.028774 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -0.068 | -0.56154 | 0 | -0.11102 | -0.09 | -0.22351 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -0.668 | -1.192 | -0.5694 | -0.74762 | -0.69 | -0.73161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -1.302 | -1.5455 | -0.92744 | -1.1811 | -1.17 | -1.1455 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -1.555 | -1.6506 | -1.173 | -1.3476 | -1.35 | -1.2934 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -1.453 | -1.5424 | -1.2114 | -1.2768 | -1.35 | -1.2148 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -0.73 | -1.1511 | -1.0054 | -0.87926 | -1.05 | -0.8108 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -0.092 | -0.46865 | -0.56114 | -0.21836 | -0.47 | -0.14797 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | #N/A | -0.10765 | -0.19504 | 0 | -0.05 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 980 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.241 | -0.18841 | -0.28999 | -0.21575 | -0.27 | -0.17298 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | -0.119 | -0.13027 | -0.22559 | -0.15588 | -0.21 | -0.10898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | -0.037 | -0.068221 | -0.15164 | -0.093652 | -0.14 | -0.038742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 0 | -0.0086705 | -0.07752 | -0.024143 | -0.06 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 0 | 0 | -0.00322 | 0 | -0.01 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 0 | 0 | -0.03011 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 0 | -0.018269 | -0.10082 | -0.062989 | -0.06 | -0.023003 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | -0.071 | -0.11586 | -0.18766 | -0.17091 | -0.16 | -0.1092 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | -0.236 | -0.24815 | -0.30235 | -0.30246 | -0.27 | -0.2488 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.487 | -0.50733 | -0.4882 | -0.52915 | -0.45 | -0.46854 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.832 | -0.86339 | -0.72195 | -0.82735 | -0.72 | -0.76822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.184 | -1.1778 | -0.9537 | -1.0995 | -1 | -1.0533 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -1.422 | -1.3736 | -1.1675 | -1.3165 | -1.23 | -1.2706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -1.553 | -1.4517 | -1.3074 | -1.4417 | -1.39 | -1.3952 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -1.593 | -1.3713 | -1.3421 | -1.438 | -1.42 | -1.39 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -1.517 | -1.1792 | -1.2783 | -1.33 | -1.34 | -1.2715 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -1.417 | -1.0349 | -1.1854 | -1.2236 | -1.24 | -1.1727 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.284 | -0.93142 | -1.0758 | -1.1098 | -1.13 | -1.0609 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.121 | -0.81522 | -0.96104 | -0.96893 | -1 | -0.91946 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -0.938 | -0.69185 | -0.82628 | -0.81412 | -0.86 | -0.76865 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -0.788 | -0.58322 | -0.70182 | -0.68625 | -0.73 | -0.6432 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -0.638 | -0.49948 | -0.61213 | -0.59068 | -0.63 | -0.54605 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.512 | -0.42484 | -0.52449 | -0.5056 | -0.54 | -0.46032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.387 | -0.33992 | -0.42934 | -0.41088 | -0.45 | -0.36221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 985 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 1.202 | 0.9489 | 1.1713 | 1.1316 | 1.07 | 1.1818 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 1.224 | 1.0473 | 1.266 | 1.2332 | 1.2 | 1.2942 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 1.323 | 1.1317 | 1.3543 | 1.3297 | 1.3 | 1.3966 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 1.408 | 1.2243 | 1.4513 | 1.4277 | 1.4 | 1.5015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 1.439 | 1.2901 | 1.5133 | 1.5004 | 1.48 | 1.5771 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 1.445 | 1.351 | 1.5837 | 1.5653 | 1.55 | 1.6428 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 1.459 | 1.4134 | 1.6344 | 1.6239 | 1.62 | 1.7074 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 1.294 | 1.226 | 1.6091 | 1.4296 | 1.52 | 1.4465 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 1.0285 | 0.63568 | 1.2523 | 0.87469 | 1.02 | 0.85185 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 0.106 | 0.19897 | 0.63558 | 0.34915 | 0.46 | 0.32364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -0.8215 | -0.34013 | -0.03353 | -0.25363 | -0.12 | -0.28825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.6695 | -0.98196 | -0.67357 | -0.93631 | -0.77 | -0.96318 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -2.3805 | -1.5878 | -1.2303 | -1.6478 | -1.48 | -1.6316 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -2.566 | -1.9023 | -1.5163 | -2.0379 | -1.94 | -1.9744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -2.464 | -1.9331 | -1.6801 | -2.082 | -2.02 | -2.0099 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -2.206 | -1.7333 | -1.6411 | -1.9005 | -1.94 | -1.8348 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -1.521 | -1.2638 | -1.3568 | -1.3981 | -1.56 | -1.3251 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -0.817 | -0.54502 | -0.83413 | -0.63216 | -0.89 | -0.55512 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -0.11 | -0.13333 | -0.3958 | -0.18634 | -0.35 | -0.12032 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 0.216 | 0.11696 | -0.11193 | 0.1006 | -0.04 | 0.17769 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 0.499 | 0.34273 | 0.13546 | 0.33635 | 0.23 | 0.41925 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 0.7242 | 0.54685 | 0.36388 | 0.5638 | 0.48 | 0.6443 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 0.96 | 0.71216 | 0.55162 | 0.75784 | 0.71 | 0.84052 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 1.158 | 0.82345 | 0.70288 | 0.89065 | 0.86 | 0.98099 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 985 JUL 14
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.821 | -0.64521 | -0.70663 | -0.71075 | -0.76 | -0.66171 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | -0.701 | -0.55887 | -0.62235 | -0.62348 | -0.66 | -0.5713 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | -0.574 | -0.46354 | -0.52812 | -0.52735 | -0.57 | -0.46544 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | -0.483 | -0.3547 | -0.43146 | -0.42151 | -0.46 | -0.35659 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | -0.4127 | -0.26008 | -0.33373 | -0.32772 | -0.35 | -0.25937 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | -0.4064 | -0.25356 | -0.34526 | -0.33274 | -0.32 | -0.26648 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | -0.5304 | -0.35224 | -0.43216 | -0.44088 | -0.4 | -0.38013 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | -0.7226 | -0.49552 | -0.56288 | -0.59821 | -0.52 | -0.51857 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | -0.9494 | -0.68807 | -0.73174 | -0.79838 | -0.68 | -0.71573 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -1.2632 | -1.0367 | -0.97482 | -1.1091 | -0.94 | -1.0407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -1.71 | -1.4712 | -1.2648 | -1.4971 | -1.29 | -1.4329 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -2.024 | -1.8619 | -1.5421 | -1.8618 | -1.65 | -1.7925 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -2.243 | -2.0803 | -1.7885 | -2.1009 | -1.93 | -2.0441 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -2.346 | -2.1666 | -1.9516 | -2.2354 | -2.11 | -2.1791 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -2.342 | -2.0876 | -2.0008 | -2.2319 | -2.15 | -2.1762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -2.25 | -1.8986 | -1.9428 | -2.1292 | -2.08 | -2.0485 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.131 | -1.7366 | -1.8455 | -2.0064 | -1.98 | -1.9356 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.988 | -1.612 | -1.7221 | -1.8639 | -1.87 | -1.7994 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.807 | -1.4718 | -1.5836 | -1.6925 | -1.72 | -1.6253 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -1.61 | -1.3161 | -1.4224 | -1.5015 | -1.55 | -1.4325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -1.433 | -1.1782 | -1.2731 | -1.3387 | -1.39 | -1.2707 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -1.281 | -1.0709 | -1.1615 | -1.2139 | -1.25 | -1.1431 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -1.15 | -0.97062 | -1.0547 | -1.0991 | -1.12 | -1.027 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -1.009 | -0.85843 | -0.93767 | -0.97318 | -1 | -0.89868 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 995 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 0.724 | 0.32105 | 0.40804 | 0.50876 | 0.42 | 0.53763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 0.814 | 0.40368 | 0.48876 | 0.59729 | 0.54 | 0.62899 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 0.942 | 0.47533 | 0.56563 | 0.67434 | 0.63 | 0.70796 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 1.054 | 0.55403 | 0.64603 | 0.74589 | 0.71 | 0.78477 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 1.142 | 0.60291 | 0.69388 | 0.78604 | 0.77 | 0.83089 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 1.221 | 0.64819 | 0.75613 | 0.81681 | 0.81 | 0.86691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 1.285 | 0.68594 | 0.79633 | 0.8414 | 0.85 | 0.90136 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 1.157 | 0.52924 | 0.76451 | 0.68673 | 0.76 | 0.69613 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 0.53 | 0.086248 | 0.41712 | 0.24592 | 0.37 | 0.19219 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -0.675 | -0.50421 | -0.16807 | -0.3633 | -0.2 | -0.42045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -1.617 | -1.1965 | -0.79694 | -1.0539 | -0.88 | -1.1165 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -2.518 | -1.8905 | -1.3983 | -1.7987 | -1.6 | -1.8616 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -3.021 | -2.4977 | -1.9247 | -2.5159 | -2.34 | -2.5375 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -3.186 | -2.7863 | -2.1968 | -2.8801 | -2.78 | -2.87 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -3.042 | -2.8206 | -2.3715 | -2.9303 | -2.83 | -2.9019 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -2.718 | -2.6157 | -2.3468 | -2.7431 | -2.73 | -2.7176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -2.122 | -2.1061 | -2.0834 | -2.2176 | -2.34 | -2.1893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.32 | -1.3534 | -1.5865 | -1.4023 | -1.63 | -1.3747 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -0.788 | -0.91496 | -1.1719 | -0.925 | -1.08 | -0.89967 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -0.385 | -0.64822 | -0.90379 | -0.60955 | -0.75 | -0.57738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -0.01 | -0.42283 | -0.6734 | -0.35944 | -0.48 | -0.32112 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 0.164 | -0.23074 | -0.46555 | -0.13628 | -0.25 | -0.10322 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 0.42 | -0.065507 | -0.2987 | 0.056384 | -0.04 | 0.091677 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 0.618 | 0.055548 | -0.16436 | 0.19471 | 0.1 | 0.2338 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY HEATING & COOLING LOAD DATA
CASE 995 JUL 14
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | -0.77 | -0.57478 | -0.6563 | -0.64079 | -0.68 | -0.61504 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | -0.642 | -0.51269 | -0.5916 | -0.57552 | -0.61 | -0.54619 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | -0.541 | -0.44442 | -0.5172 | -0.5033 | -0.54 | -0.46646 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | -0.434 | -0.36915 | -0.4428 | -0.42781 | -0.46 | -0.38577 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | -0.328 | -0.29783 | -0.3681 | -0.35439 | -0.38 | -0.31121 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | -0.33 | -0.30657 | -0.3947 | -0.37247 | -0.37 | -0.32724 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | -0.462 | -0.38991 | -0.4652 | -0.46548 | -0.44 | -0.42475 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | -0.626 | -0.48515 | -0.5517 | -0.57861 | -0.54 | -0.53025 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | -0.811 | -0.62671 | -0.6662 | -0.73081 | -0.66 | -0.68033 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | -1.077 | -0.92083 | -0.8518 | -0.98589 | -0.88 | -0.95144 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | -1.447 | -1.2898 | -1.0853 | -1.3035 | -1.17 | -1.2752 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | -1.687 | -1.6114 | -1.3168 | -1.5915 | -1.46 | -1.5789 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | -1.884 | -1.8125 | -1.5304 | -1.8176 | -1.71 | -1.8067 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | -1.984 | -1.888 | -1.6701 | -1.9425 | -1.86 | -1.9307 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | -1.971 | -1.8001 | -1.7047 | -1.9297 | -1.89 | -1.9149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | -1.872 | -1.5962 | -1.6406 | -1.8097 | -1.8 | -1.7802 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | -1.763 | -1.4401 | -1.5477 | -1.6975 | -1.69 | -1.6747 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | -1.643 | -1.3312 | -1.4379 | -1.5763 | -1.58 | -1.5534 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | -1.479 | -1.2069 | -1.3231 | -1.4243 | -1.44 | -1.3964 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | -1.294 | -1.0712 | -1.1882 | -1.2553 | -1.28 | -1.2236 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | -1.135 | -0.95683 | -1.0637 | -1.116 | -1.14 | -1.083 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | -1.041 | -0.87231 | -0.9739 | -1.0144 | -1.03 | -0.97738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | -0.967 | -0.79533 | -0.8862 | -0.92336 | -0.93 | -0.88459 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | -0.881 | -0.70925 | -0.791 | -0.82306 | -0.84 | -0.78278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
CONDITIONED ZONE TEMPERATURES
CASE 640 FEB 1
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 12.7 | 11.1142 | 10 | 10.7291 | 10.63 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 10.1 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 10 | 10 | 10 | 10 | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 15 | 15.5 | 20 | 15.8147 | 15 | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 21.3 | 20.7841 | 20 | 21.32 | 21.16 | 21.7174 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | 24.8 | 26.0342 | 26.64 | 26.4903 | 26.39 | 25.2174 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | 27 | 27 | 27 | 27 | 27 | 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | 26.8 | 25.7064 | 27 | 25.4595 | 25.82 | 24.7749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 25.4 | 21.3714 | 23.73 | 21.1465 | 21.21 | 21.2749 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 22.8 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 16.8 | 12.9579 | 11.34 | 12.9018 | 13.55 | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
CONDITIONED ZONE TEMPERATURES
CASE 940 FEB 1
[USE (-) FOR COOLING]
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
kWh | HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
262 | 1 | 18.1 | 16.6192 | 15.59 | 15.6174 | 16.04 | 14.9916 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
263 | 2 | 17.7 | 16.0221 | 15.02 | 15.0057 | 15.32 | 15.0095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
264 | 3 | 17.2 | 15.4654 | 14.48 | 14.4319 | 14.71 | 13.9919 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
265 | 4 | 16.7 | 14.9003 | 13.9 | 13.8638 | 14.11 | 13.6703 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
266 | 5 | 16.3 | 14.3857 | 13.43 | 13.3569 | 13.55 | 12.9607 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
267 | 6 | 15.8 | 13.9037 | 12.92 | 12.884 | 13.05 | 12.5881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
268 | 7 | 15.4 | 13.4247 | 12.47 | 12.4205 | 12.53 | 12.0187 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
269 | 8 | 17.6 | 15.9016 | 20 | 15.9824 | 15.29 | 15.9576 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
270 | 9 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
271 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
272 | 11 | 20.7 | 20.1042 | 20 | 20 | 20.21 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
273 | 12 | 22.2 | 21.6771 | 20.54 | 20.9908 | 20.78 | 20.9881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
274 | 13 | 23.9 | 23.7146 | 22.49 | 23.1192 | 22.86 | 23.005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
275 | 14 | 25.2 | 24.982 | 23.74 | 24.6214 | 24.53 | 24.4382 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
276 | 15 | 25.9 | 25.2873 | 24.64 | 25.2509 | 25.25 | 25.0064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
277 | 16 | 25.8 | 25.2471 | 24.91 | 25.2715 | 25.47 | 24.9739 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
278 | 17 | 24.6 | 24.4059 | 24.35 | 24.483 | 24.94 | 24.1466 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
279 | 18 | 23.2 | 22.6175 | 22.94 | 22.7901 | 23.5 | 22.4177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
280 | 19 | 22.2 | 21.3767 | 21.65 | 21.4689 | 22.04 | 21.0104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
281 | 20 | 21.4 | 20.564 | 20.76 | 20.5229 | 21.08 | 20.3503 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
282 | 21 | 20.8 | 20.0224 | 20 | 20.0026 | 20.23 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
283 | 22 | 20.2 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
284 | 23 | 19.6 | 20 | 20 | 20 | 20 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
285 | 24 | 18.8 | 18.1003 | 18.01 | 18.0038 | 18.38 | 17.6553 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MAY 4
CASE 600 OR 900
HORIZONTAL SURFACE
(USE COLUMN B ONLY)
kWh | CODENAME: | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
0 | COUNTRY:
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
kWh |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 15 | 15.0006 | 15 | 21.25 | 17.81 | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 60 | 60.0025 | 60 | 64.75 | 60.75 | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 111 | 111.0047 | 111 | 114.5833 | 110.5 | 111 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 158 | 158.0065 | 158 | 160.25 | 156.75 | 158 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 195 | 195.008 | 195 | 203.25 | 198.88 | 195 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 263 | 263.0108 | 263 | 259.8333 | 256.38 | 263 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 278 | 278.0116 | 278 | 276.5833 | 276 | 278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 277 | 277.0115 | 277 | 274.0833 | 274.88 | 277 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 259 | 259.0108 | 259 | 255.1667 | 257.25 | 259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 227 | 227.0095 | 227 | 222 | 225.25 | 227 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 181 | 181.0076 | 181 | 172 | 177.12 | 181 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 104 | 104.0043 | 104 | 101.9167 | 107.25 | 104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 53 | 53.0022 | 53 | 50.25 | 54.12 | 53 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 11 | 11.0004 | 11 | 10.5278 | 14.19 | 11 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLEAR DAY, JULY 14
CASE 600 OR 900
HORIZONTAL SURFACE
(USE COLUMN B ONLY)
kWh | CODENAME: | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
0 | COUNTRY:
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
kWh |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 1.4992 | 1.17 | 5.6503 | 2.88 | 1.8578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 90 | 82.0455 | 82.05 | 103.1926 | 90.78 | 89.6008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 275 | 264.1993 | 273.2 | 289.8646 | 272.39 | 275.5875 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 479 | 465.8199 | 477.91 | 493.4291 | 475.84 | 478.6209 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 668 | 656.5745 | 668 | 682.3352 | 666.65 | 669.4288 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 827 | 816.0523 | 827 | 837.8445 | 825.46 | 827.9708 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 941 | 931.7134 | 941 | 947.9972 | 939.78 | 941.9442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 1003 | 996.141 | 1003 | 1005.2373 | 1001.8 | 1004.1701 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 1008 | 1002.0363 | 1008 | 1004.0328 | 1005.59 | 1007.5518 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 955 | 951.5143 | 955 | 946.1468 | 952.44 | 954.4569 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 848 | 847.7872 | 848 | 835.4779 | 846.07 | 848.3258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 696 | 697.2651 | 696 | 679.2595 | 693.34 | 695.7926 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 509 | 511.7801 | 509 | 489.9716 | 506.28 | 508.9129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 306 | 309.2767 | 304.41 | 285.8351 | 302.71 | 305.8694 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 114 | 116.1785 | 110.72 | 99.0838 | 112.8 | 113.5205 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 5.5971 | 3.65 | 4.4364 | 7.48 | 5.1513 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY SKY TEMPERATURE DATA
CASE 600 CLEAR/COLD FEB 1
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | -30.2822 | -22.8397 | -30.28 | -22.9659 | -30.02 | -24.4041 | -30.2822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | -27.4567 | -26.6414 | -27.46 | -24.1358 | -27.59 | -28.908 | -27.4567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | -33.8377 | -28.0897 | -33.84 | -25.3162 | -34.17 | -30.651 | -33.8377 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | -37.567 | -33.7622 | -37.57 | -27.1947 | -37.85 | -35.7966 | -37.567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | -35.0231 | -35.2444 | -35.02 | -26.8988 | -35.32 | -36.4345 | -35.0231 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | -35.993 | -35.6508 | -35.99 | -26.6742 | -36.27 | -35.6524 | -35.993 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | -38.7016 | -37.5801 | -38.7 | -27.3883 | -39.06 | -37.476 | -38.7016 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | -35.4235 | -37.0009 | -35.42 | -26.6041 | -35.71 | -37.1982 | -35.4235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | -36.8689 | -36.328 | -36.87 | -25.3596 | -37.21 | -36.2544 | -36.8689 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | -36.1031 | -36.5645 | -36.1 | -24.4946 | -36.53 | -36.5874 | -36.1031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | -34.5636 | -35.3739 | -34.56 | -23.1465 | -35.02 | -35.3983 | -34.5636 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | -33.6763 | -34.1943 | -33.68 | -21.7912 | -34.15 | -34.1462 | -33.6763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | -31.6698 | -32.6854 | -31.67 | -20.2132 | -32.27 | -32.6565 | -31.6698 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | -33.2373 | -32.6302 | -33.24 | -20.6931 | -33.6 | -32.45 | -33.2373 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | -33.224 | -33.3209 | -33.22 | -21.7664 | -33.59 | -33.132 | -33.224 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | -33.5 | -33.4665 | -33.5 | -22.2074 | -33.87 | -33.233 | -33.5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | -34.0382 | -33.8865 | -34.04 | -22.932 | -34.35 | -33.6218 | -34.0382 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | -36.3464 | -35.3916 | -36.35 | -24.6208 | -36.61 | -35.0378 | -36.3464 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | -36.4727 | -36.4941 | -36.47 | -25.9163 | -36.72 | -36.2502 | -36.4727 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | -36.913 | -36.7865 | -36.91 | -26.5019 | -37.14 | -36.5459 | -36.913 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | -37.9742 | -37.563 | -37.97 | -27.6142 | -38.24 | -37.3195 | -37.9742 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | -38.9062 | -38.5529 | -38.91 | -28.9393 | -39.11 | -38.344 | -38.9062 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | -38.9555 | -38.9993 | -38.96 | -29.4433 | -39.18 | -38.8709 | -38.9555 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | -38.5188 | -38.7814 | -38.52 | -29.2659 | -38.79 | -38.7168 | -38.5188 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY SKY TEMPERATURE DATA
CASE 600 CLOUDY MAY 4
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 3.6876 | 0.38605 | 3.69 | -1.17 | 0.09 | 0.41396 | 3.6876 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 4.4245 | 0.40933 | 4.42 | -1.1879 | 0.67 | 0.36976 | 4.4245 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 3.8943 | 0.32324 | 3.89 | -1.261 | 0.04 | 0.3372 | 3.8943 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 3.6721 | 0.019551 | 3.67 | -1.4438 | -0.01 | -0.0004892 | 3.6721 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 3.6641 | -0.026626 | 3.66 | -1.4438 | -0.06 | -0.049894 | 3.6641 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 3.803 | -0.077933 | 3.8 | -1.4438 | -0.11 | -0.10199 | 3.803 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 4.3213 | 0.1937 | 4.32 | -1.1879 | 0.44 | 0.14095 | 4.3213 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 4.3945 | 0.43445 | 4.39 | -0.87772 | 0.44 | 0.41027 | 4.3945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 4.9064 | 0.70848 | 4.91 | -0.53267 | 0.93 | 0.66268 | 4.9064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 6.2008 | 1.807 | 6.2 | 0.6528 | 2.52 | 1.7115 | 6.2008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 6.9765 | 3.0787 | 6.98 | 1.865 | 3.53 | 3.0181 | 6.9765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 6.2647 | 3.2866 | 6.26 | 2.0953 | 3.08 | 3.3069 | 6.2647 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 4.1911 | 2.1422 | 4.19 | 0.88422 | 1.37 | 2.2335 | 4.1911 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 3.1788 | 0.78812 | 3.18 | -0.55214 | 0.32 | 0.85375 | 3.1788 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 1.9243 | -0.62158 | 1.92 | -2.0361 | -1.39 | -0.51745 | 1.9243 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 1.1489 | -0.73525 | 1.15 | -1.9974 | -0.21 | -0.76901 | 1.1489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 3.2979 | -0.44746 | 3.3 | -1.8299 | -0.63 | -0.39529 | 3.2979 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 3.2977 | -0.64839 | 3.3 | -2.1057 | -0.64 | -0.6146 | 3.2977 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 2.4978 | -0.91461 | 2.5 | -2.3646 | -1.12 | -0.85587 | 2.4978 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 1.9983 | -1.4056 | 2 | -2.9405 | -1.62 | -1.3469 | 1.9983 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 2.0062 | -1.607 | 2.01 | -3.2197 | -1.57 | -1.5768 | 2.0062 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 1.8319 | -1.9502 | 1.83 | -3.7455 | -2.24 | -1.8894 | 1.8319 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0.95143 | -2.8551 | 0.95 | -4.7857 | -3.35 | -2.7778 | 0.95143 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0.95172 | -3.3493 | 0.95 | -5.2605 | -3.34 | -3.3333 | 0.95172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY SKY TEMPERATURE DATA
CASE 600 CLEAR/HOT JULY 14
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY:
TEMP (C) | HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0.75693 | 0.90277 | 0.76 | 4.3575 | 0.7 | 1.0389 | 0.75693 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0.16261 | 0.31055 | 0.163 | 3.8578 | 0.1 | 0.40274 | 0.16261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | -1.4341 | -0.83045 | -1.43 | 2.9526 | -1.36 | -0.72718 | -1.4341 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | -2.7015 | -2.2461 | -2.7 | 1.8114 | -2.64 | -2.1863 | -2.7015 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | -4.1002 | -3.5856 | -4.1 | 0.74467 | -4.05 | -3.5387 | -4.1002 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | -1.779 | -2.9391 | -1.78 | 1.7866 | -1.82 | -3.0874 | -1.779 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 0.21141 | -0.80157 | 0.21 | 4.4173 | 0.27 | -0.93306 | 0.21141 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 1.1998 | 0.63558 | 1.2 | 6.596 | 1.19 | 0.56357 | 1.1998 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 2.2849 | 1.6749 | 2.28 | 8.3915 | 2.34 | 1.6181 | 2.2849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 5.0591 | 3.6938 | 5.06 | 10.7117 | 5.18 | 3.5737 | 5.0591 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 5.4079 | 5.1376 | 5.41 | 12.6113 | 5.23 | 5.1703 | 5.4079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 5.1147 | 5.1381 | 5.11 | 13.2726 | 5.13 | 5.2388 | 5.1147 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 5.5711 | 5.2613 | 5.57 | 13.895 | 5.64 | 5.3636 | 5.5711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 4.9914 | 5.1527 | 4.99 | 14.3919 | 4.83 | 5.3363 | 4.9914 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 6.0132 | 5.4585 | 6.01 | 14.9 | 6.27 | 5.6052 | 6.0132 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 5.4557 | 5.6185 | 5.46 | 14.7769 | 5.29 | 5.8681 | 5.4557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 6.5386 | 5.9695 | 6.54 | 14.4692 | 6.77 | 6.1476 | 6.5386 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 5.6681 | 5.9794 | 5.67 | 13.5976 | 5.56 | 6.2678 | 5.6681 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 5.1895 | 5.3256 | 5.19 | 12.3123 | 5.12 | 5.5904 | 5.1895 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 5.7177 | 5.4067 | 5.72 | 11.5045 | 5.75 | 5.6202 | 5.7177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 2.1391 | 3.6698 | 2.14 | 9.4472 | 2.22 | 4.052 | 2.1391 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 2.1388 | 2.0509 | 2.14 | 7.9167 | 2.07 | 2.235 | 2.1388 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 1.541 | 1.7227 | 1.54 | 7.1679 | 1.56 | 1.9 | 1.541 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0.44827 | 0.85954 | 0.45 | 5.9239 | 0.53 | 1.015 | 0.44827 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/COLD DAY, FEB 1
CASE 600
SOUTH WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 104.3 | 82.0324 | 62.99 | 109.5631 | 98.09 | 106.3916 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 325.7 | 297.541 | 321.42 | 323.8 | 305.31 | 323.2919 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 484.4 | 459.7525 | 491.87 | 484.0809 | 471.51 | 482.6422 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 593.5 | 578.5582 | 608.92 | 591.9351 | 588.43 | 593.3244 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 653.9 | 652.8082 | 673.56 | 648.7354 | 646.8 | 655.1426 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 665 | 673.3877 | 684.62 | 654.8384 | 656.6 | 665.9038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 623.5 | 628.6623 | 641 | 609.2696 | 617.5 | 624.0771 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 534.1 | 528.0285 | 543.97 | 513.0433 | 523.9 | 531.1272 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 396.8 | 378.3411 | 395.66 | 366.6641 | 378.6 | 392.8611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 210.3 | 191.9413 | 184.45 | 178.3747 | 190.97 | 204.1309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 0 | 14.3991 | 4.82 | 9.7889 | 10.84 | 18.3687 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/COLD DAY, FEB 1
CASE 660
SOUTH LOW-E WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 55.73 | 50.937 | 41.95 | 58.7036 | 52.46 | 56.996 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 176.5 | 180.8792 | 200.8 | 175.1923 | 165.67 | 175.7302 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 265.7 | 278.4931 | 297.08 | 263.0242 | 257.88 | 264.7322 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 327.31 | 348.905 | 362.95 | 322.5677 | 323.46 | 326.2696 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 361.31 | 391.0585 | 399.66 | 354.5078 | 356.29 | 360.9121 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 367.54 | 404.3853 | 405.96 | 357.9765 | 361.81 | 367.0186 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 344.22 | 377.3723 | 381.03 | 332.2657 | 339.8 | 343.5482 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 293.82 | 316.992 | 326.05 | 278.943 | 287.23 | 291.6286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 216.33 | 229.4327 | 242.52 | 198.6673 | 206.18 | 214.6368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 112.91 | 117.7938 | 119.32 | 95.7857 | 102.75 | 109.8074 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 0 | 9.06 | 3.3 | 5.1964 | 5.76 | 9.7258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/COLD DAY, FEB 1
CASE 670
SOUTH SINGLE-PANE WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 138.85 | 107.13 | 81.98 | 144.9621 | 130.57 | 140.083 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 409.45 | 362.8681 | 394.31 | 408.8652 | 385.67 | 406.3398 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 592.98 | 545.2226 | 584.9 | 596.1031 | 580.1 | 591.3496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 719.04 | 675.1871 | 714.8 | 720.937 | 713.01 | 718.8377 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 788.87 | 749.7897 | 786.82 | 786.606 | 781.74 | 789.0166 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 801.72 | 768.3238 | 799.14 | 793.6699 | 793.35 | 801.25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 753.75 | 720.0014 | 750.28 | 740.9315 | 747 | 753.2139 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 650.33 | 613.0512 | 642.14 | 629.5384 | 639.47 | 647.3005 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 492.04 | 452.897 | 477 | 459.3639 | 472.35 | 486.7755 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 272.44 | 241.2176 | 233.64 | 233.5125 | 248.72 | 265.4371 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 0 | 19.1922 | 6.44 | 13.5578 | 14.74 | 24.9891 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLOUDY DAY, MAY 4
CASE 600
SOUTH WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 5.6 | 5.76 | 5.49 | 6.5505 | 5.81 | 4.6924 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 21.85 | 23.0255 | 21.96 | 20.1724 | 19.89 | 19.0292 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 39.76 | 42.4983 | 40.63 | 35.7642 | 36.03 | 35.3106 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 56.42 | 60.5559 | 57.83 | 50.3329 | 51.69 | 50.5672 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 69.73 | 74.7815 | 71.37 | 64.481 | 66.46 | 63.0453 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 94.02 | 100.3258 | 96.26 | 83.2627 | 86.72 | 85.9692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 99.56 | 105.248 | 101.75 | 89.1256 | 94 | 91.4367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 99.19 | 104.1118 | 101.39 | 88.2229 | 93.56 | 91.0569 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 92.55 | 97.1633 | 94.8 | 81.5371 | 86.87 | 84.5365 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 80.82 | 85.3291 | 83.09 | 70.1431 | 75.05 | 73.2554 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 64.17 | 68.2121 | 66.25 | 53.6776 | 58.03 | 57.6238 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 37.29 | 39.5371 | 38.07 | 31.766 | 34.87 | 33.0767 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 19.35 | 20.2628 | 19.4 | 15.6051 | 17.73 | 16.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 4.09 | 4.2104 | 4.03 | 3.2381 | 4.62 | 3.4323 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLOUDY DAY, MAY 4
CASE 660
SOUTH LOW-E WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 3.06 | 3.544 | 3.54 | 3.5641 | 3.16 | 2.5704 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 11.96 | 14.1619 | 14.16 | 10.9757 | 10.83 | 10.4236 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 21.77 | 26.0993 | 26.2 | 19.4591 | 19.62 | 19.3421 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 30.88 | 37.2213 | 37.3 | 27.3858 | 28.16 | 27.6992 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 38.17 | 46.0006 | 46.03 | 35.0837 | 36.2 | 34.5344 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 51.47 | 61.4812 | 62.09 | 45.3028 | 47.23 | 47.0914 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 54.5 | 64.2908 | 65.63 | 48.4927 | 51.2 | 50.0863 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 54.3 | 63.1249 | 65.39 | 48.0015 | 50.96 | 49.8783 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 50.67 | 58.8997 | 61.14 | 44.3638 | 47.31 | 46.3066 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 44.24 | 51.7282 | 53.59 | 38.1645 | 40.88 | 40.1271 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 35.13 | 41.4256 | 42.73 | 29.2057 | 31.61 | 31.5646 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 20.41 | 24.1701 | 24.55 | 17.2837 | 18.99 | 18.1185 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 10.59 | 12.4348 | 12.51 | 8.4907 | 9.66 | 9.193 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 2.24 | 2.5852 | 2.6 | 1.7618 | 2.52 | 1.8801 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLOUDY DAY, MAY 4
CASE 670
SOUTH SINGLE-PANE WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 7.01 | 6.9223 | 6.93 | 8.271 | 7.24 | 5.8743 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 27.38 | 27.6826 | 27.74 | 25.471 | 24.8 | 23.8222 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 49.82 | 51.1502 | 51.32 | 45.1581 | 44.92 | 44.2044 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 70.69 | 72.8793 | 73.05 | 63.5536 | 64.45 | 63.3037 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 87.37 | 90.0133 | 90.15 | 81.4178 | 82.87 | 78.9248 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 117.8 | 121.0763 | 121.59 | 105.1329 | 108.12 | 107.6225 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 124.74 | 127.4075 | 128.53 | 112.5357 | 117.2 | 114.4671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 124.27 | 126.1131 | 128.06 | 111.3958 | 116.65 | 113.9917 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 115.96 | 117.7605 | 119.74 | 102.9539 | 108.31 | 105.829 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 101.26 | 103.3009 | 104.95 | 88.5672 | 93.57 | 91.7065 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 80.4 | 82.5129 | 83.68 | 67.7768 | 72.35 | 72.1377 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 46.72 | 47.709 | 48.08 | 40.1098 | 43.48 | 41.4079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 24.25 | 24.4004 | 24.5 | 19.704 | 22.11 | 21.0096 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 5.13 | 5.0665 | 5.09 | 4.0886 | 5.76 | 4.2968 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/HOT DAY, JUL 14
CASE 600
SOUTH WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0.34752 | 0.43 | 1.6849 | 0.8 | 0.66207 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 15.55 | 9.793 | 12.51 | 16.1367 | 15.28 | 15.6873 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 31.61 | 21.8537 | 28.06 | 33.0345 | 32.92 | 32.4711 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 47.98 | 35.0242 | 44.78 | 48.9027 | 49.71 | 48.7734 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 66.84 | 52.8909 | 64.53 | 70.5019 | 72.36 | 71.7945 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 112.79 | 106.0912 | 113.53 | 116.644 | 117.05 | 118.4204 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 166.86 | 171.3254 | 172.34 | 169.4457 | 169.35 | 170.3654 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 201.93 | 214.7217 | 211.22 | 201.8158 | 204.8 | 209.7239 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 204.75 | 213.836 | 214.69 | 201.2382 | 207.38 | 210.9664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 173.86 | 181.0836 | 181.43 | 168.1713 | 176.25 | 180.3064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 121.01 | 121.3543 | 124.33 | 115.2723 | 125.09 | 127.6724 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 72.45 | 63.7931 | 70.83 | 69.6148 | 77.7 | 75.3431 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 50.43 | 37.6588 | 47.22 | 48.6162 | 52.17 | 51.0656 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 34.69 | 24.2426 | 30.56 | 32.6887 | 35.49 | 34.9664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 18.13 | 11.6997 | 14.58 | 15.6631 | 17.72 | 18.0325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 1.1413 | 1.22 | 1.4014 | 2.08 | 1.895 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/HOT DAY, JUL 14
CASE 660
SOUTH LOW-E WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0.21439 | 0.28 | 0.91674 | 0.44 | 0.36266 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 8.51 | 6.0253 | 8.07 | 8.7799 | 8.33 | 8.593 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 17.3 | 13.4169 | 18.1 | 17.9739 | 17.93 | 17.7867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 26.27 | 21.4445 | 28.88 | 26.6079 | 27.07 | 26.7166 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 36.47 | 32.3826 | 43.25 | 38.6289 | 39.24 | 39.1157 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 60.56 | 66.3123 | 82.86 | 63.0283 | 62.79 | 63.6391 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 88.94 | 107.1366 | 124.7 | 90.4757 | 90.23 | 90.5877 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 107.5 | 133.6999 | 149.98 | 107.4787 | 108.79 | 111.2626 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 109.01 | 132.4799 | 152.17 | 107.1723 | 110.14 | 111.9095 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 92.64 | 112.4723 | 130.74 | 89.8075 | 93.84 | 95.7693 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 64.87 | 75.3683 | 90.97 | 62.3178 | 67.02 | 68.4197 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 39.45 | 38.9794 | 48.68 | 38.1416 | 42.07 | 41.0134 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 27.6 | 22.8693 | 30.45 | 26.4518 | 28.42 | 27.9722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 18.99 | 14.709 | 19.71 | 17.7857 | 19.33 | 19.1536 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 9.92 | 7.1153 | 9.4 | 8.5222 | 9.65 | 9.8777 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 0.69581 | 0.79 | 0.76247 | 1.13 | 1.038 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
HOURLY TRANSMITTED SOLAR RADIATION, CLEAR/HOT DAY, JUL 14
CASE 670
SOUTH SINGLE-PANE WINDOWS
(USE COLUMN B ONLY)
0 | CODENAME: | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | COUNTRY: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wh/m2 | HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
0 |  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
231 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
232 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
233 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
234 | 5 | 0 | 0.41726 | 0.54 | 2.1275 | 1 | 0.82883 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
235 | 6 | 19.48 | 11.7918 | 15.8 | 20.3752 | 19.06 | 19.6385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
236 | 7 | 39.61 | 26.3554 | 35.45 | 41.7114 | 41.04 | 40.6497 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
237 | 8 | 60.11 | 42.3184 | 56.56 | 61.7496 | 61.97 | 61.0581 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
238 | 9 | 89.08 | 67.7615 | 86.7 | 96.4962 | 94.38 | 95.0519 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
239 | 10 | 163.22 | 144.8439 | 164.26 | 170.6848 | 166.3 | 171.5706 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
240 | 11 | 238.46 | 229.0314 | 244.33 | 244.3135 | 238.75 | 245.2683 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
241 | 12 | 283.59 | 280.7528 | 293.03 | 286.2069 | 284.99 | 294.3631 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
242 | 13 | 287.12 | 281.1221 | 297.25 | 285.4691 | 288.31 | 296.2153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
243 | 14 | 247.65 | 242.0489 | 255.91 | 242.6571 | 247.87 | 257.3993 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
244 | 15 | 175.19 | 166.4995 | 179.73 | 168.6678 | 178.35 | 185.0807 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
245 | 16 | 98.49 | 83.7436 | 97.78 | 94.9682 | 103.01 | 100.6228 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
246 | 17 | 63.18 | 45.4814 | 59.64 | 61.3859 | 65.1 | 63.9276 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
247 | 18 | 43.46 | 29.321 | 38.6 | 41.2749 | 44.25 | 43.7735 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
248 | 19 | 22.72 | 14.1359 | 18.42 | 19.7772 | 22.1 | 22.5744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
249 | 20 | 0 | 1.3866 | 1.54 | 1.7694 | 2.6 | 2.3722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
250 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
251 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
252 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
253 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| = | = | = | = | = | = | = | = | = | [8 empty] | =
CONVECTIVE HEAT TRANSFER COEFFICIENT DATA
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Exterior, Annual Average
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
0 | Window | [17 empty] | Case 670
0 | HC Wall
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 200 (εext=0.1; εint=0.1; αext=0.1; high cond. wall element)
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Exterior, Annual Hourly Maximum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Exterior, Annual Hourly Minimum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Interior, Annual Average
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
0 | Window | [17 empty] | Case 670
0 | HC Wall
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 200 (εext=0.1; εint=0.1; αext=0.1; high cond. wall element)
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Interior, Annual Hourly Maximum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall
Case 600 (εext=0.9; εint=0.9; αext=0.6; αint=0.6)
Interior, Annual Hourly Minimum
|  | BSIMAC | CSE | DeST | EnergyPlus | ESP-r | TRNSYS | TestSpec-Alt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tested Prg
0 | Window
1 | Roof
2 | Floor
3 | N. Wall
4 | E. Wall
5 | W. Wall
6 | S. Wall

## BSIMAC
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | BSIMAC | BSIMAC 9
| Version: |  | 9.0.74
| Date of Results: |  | 2019-05-25
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.05 | 5.822 | 3.255 | Nov | 26 | 8 | 5.65 | Jan | 22 | 15
| 610 | 4.163 | 4.299 | 3.166 | Nov | 26 | 8 | 5.466 | Jan | 22 | 15
| 620 | 4.37 | 4.404 | 3.145 | Dec | 31 | 24 | 4.704 | Jun | 26 | 18
| 630 | 4.923 | 3.074 | 3.252 | Dec | 31 | 24 | 4.121 | Jun | 26 | 18
| 640 | 2.682 | 5.804 | 4.633 | Feb | 8 | 9 | 5.65 | Jan | 22 | 15
| 650 | 0 | 4.629 | 0 |  |  |  | 5.648 | Jan | 22 | 15
| 660 | 3.574 | 3.014 | 2.62 | Nov | 26 | 8 | 3.343 | Oct | 18 | 15
| 670 | 5.484 | 6.539 | 4.122 | Nov | 26 | 8 | 6.217 | Oct | 18 | 14
| 680 | 2.219 | 5.938 | 2.126 | Nov | 26 | 8 | 5.761 | Jan | 22 | 15
| 685 | 4.532 | 9.13 | 3.169 | Nov | 26 | 8 | 6.318 | Jan | 22 | 15
| 695 | 2.709 | 8.755 | 2.138 | Nov | 26 | 8 | 6.232 | Jan | 22 | 15
| 900 | 1.726 | 2.714 | 2.551 | Feb | 8 | 24 | 3.039 | Oct | 1 | 15
| 910 | 2.163 | 1.484 | 2.761 | Feb | 8 | 24 | 2.493 | Oct | 18 | 14
| 920 | 3.5 | 3.128 | 2.895 | Nov | 26 | 8 | 3.481 | Jun | 26 | 18
| 930 | 4.27 | 2.161 | 2.968 | Dec | 31 | 24 | 3.052 | Jun | 26 | 18
| 940 | 1.389 | 2.613 | 3.882 | Feb | 8 | 9 | 3.158 | Oct | 1 | 15
| 950 | 0 | 0.586 | 0 |  |  |  | 2.366 | Sep | 10 | 15
960
| 980 | 0.72 | 3.501 | 1.693 | Feb | 8 | 24 | 3.384 | Oct | 18 | 14
| 985 | 2.801 | 7.273 | 2.754 | Feb | 8 | 24 | 3.977 | Oct | 18 | 14
| 995 | 1.33 | 7.482 | 1.711 | Nov | 26 | 8 | 4.129 | Jan | 22 | 14
| 195 | 4.217 | 0.712 | 1.802 | Dec | 31 | 24 | 1.118 | Jun | 26 | 17
| 200 | 5.041 | 0.839 | 2.272 | Nov | 26 | 8 | 1.271 | Jun | 26 | 17
| 210 | 5.627 | 0.688 | 2.374 | Dec | 31 | 24 | 1.193 | Jun | 26 | 17
| 215 | 5.652 | 0.952 | 2.521 | Nov | 26 | 8 | 1.393 | Jun | 26 | 17
| 220 | 6.377 | 0.803 | 2.631 | Nov | 26 | 8 | 1.336 | Jun | 26 | 18
| 230 | 9.851 | 1.184 | 4.219 | Dec | 31 | 24 | 1.994 | Jun | 26 | 17
| 240 | 5.116 | 1.287 | 2.431 | Nov | 26 | 8 | 1.534 | Jun | 26 | 18
| 250 | 4.733 | 3.612 | 2.631 | Nov | 26 | 8 | 2.913 | Sep | 12 | 14
270
280
290
300
310
320
| 395 | 4.565 | 0.021 | 1.948 | Dec | 31 | 24 | 0.547 | Jun | 26 | 18
| 400 | 5.906 | 0.063 | 2.559 | Nov | 26 | 8 | 0.798 | Jun | 26 | 18
| 410 | 7.63 | 0.096 | 3.338 | Dec | 31 | 24 | 1.011 | Jun | 26 | 17
| 420 | 6.399 | 0.228 | 3.138 | Dec | 31 | 24 | 1.208 | Jun | 26 | 17
| 430 | 5.171 | 1.084 | 3.3 | Dec | 31 | 24 | 2.167 | Jun | 26 | 16
440
| 450 | 3.743 | 6.172 | 2.989 | Nov | 26 | 8 | 5.812 | Jan | 22 | 15
| 460 | 3.828 | 6.26 | 3.055 | Nov | 26 | 8 | 5.804 | Jan | 22 | 15
| 470 | 4.042 | 5.987 | 3.118 | Nov | 26 | 8 | 5.695 | Jan | 22 | 15
| 800 | 5.141 | 0.473 | 2.957 | Dec | 31 | 24 | 1.286 | Jun | 26 | 16
810
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 26.1 | -9.9 | Nov | 26 | 8 | 63.4 | Oct | 18 | 17
| 900FF | 25.5 | 0.6 | Feb | 8 | 11 | 46 | Oct | 1 | 17
| 650FF | 17.6 | -16.7 | Dec | 31 | 24 | 62.1 | Oct | 18 | 17
| 950FF | 15 | -13.2 | Dec | 31 | 24 | 37.1 | Oct | 1 | 17
| 680FF | 31.8 | -5.7 | Feb | 8 | 11 | 72.5 | Jan | 22 | 17
| 980FF | 30.7 | 7.3 | Feb | 8 | 11 | 49.7 | Oct | 1 | 17
960
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1670
| NORTH | 453
| EAST | 1061
| SOUTH | 1387
| WEST | 997
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 820
| 660/South | 447
| 670/South | 1037
| 620/West | 598
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 641
| 630/West | 438
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
600
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 663.99 | 475.4 | 3.1 | 29 | 7 | 5.65 | 22 | 15 | 277.8 | 73.3141 | 2.322 | 7 | 7 | 1.982 | 22 | 16
| Feb | 653.26 | 349.2 | 3.041 | 9 | 7 | 4.9211 | 15 | 15 | 307.4 | 24.0087 | 2.551 | 8 | 24 | 1.096 | 15 | 16
| Mar | 433.508 | 450.3 | 2.275 | 2 | 7 | 4.4579 | 24 | 14 | 134.4 | 86.3882 | 1.774 | 16 | 7 | 1.508 | 10 | 15
| Apr | 511.036 | 218.7 | 2.446 | 3 | 6 | 3.4735 | 12 | 14 | 275.7 | 29.344 | 1.997 | 2 | 7 | 1.093 | 7 | 15
| May | 112.769 | 342.7 | 1.645 | 3 | 5 | 2.7741 | 10 | 14 | 20.1 | 131.0941 | 1.295 | 4 | 6 | 1.555 | 11 | 15
| Jun | 2.735 | 578.3 | 0.805 | 9 | 5 | 3.2526 | 26 | 15 | 0 | 447.4956 | 0 |  |  | 2.101 | 26 | 15
| Jul | 4.839 | 568.4 | 0.599 | 25 | 6 | 3.3187 | 17 | 14 | 0 | 440.8962 | 0 |  |  | 2.14 | 17 | 15
| Aug | 1.368 | 658.2 | 0.572 | 10 | 7 | 4.1922 | 26 | 14 | 0 | 532.6434 | 0 |  |  | 2.632 | 26 | 15
| Sep | 51.756 | 724.8 | 1.229 | 28 | 24 | 5.086 | 30 | 14 | 2.1 | 517.8661 | 0.113 | 28 | 6 | 2.961 | 30 | 15
| Oct | 316.952 | 628.4 | 1.702 | 6 | 7 | 5.5767 | 18 | 14 | 80.5 | 296.188 | 1.201 | 6 | 7 | 3.039 | 1 | 15
| Nov | 598.664 | 394.3 | 3.255 | 26 | 8 | 5.4759 | 28 | 14 | 298.2 | 72.6701 | 2.427 | 1 | 7 | 1.982 | 6 | 15
| Dec | 698.704 | 433.3 | 3.171 | 31 | 24 | 5.537 | 1 | 14 | 329.8 | 62.0916 | 2.12 | 31 | 8 | 2.069 | 1 | 15
| Total | 4049.581 | 5822 | [6 empty] | 1726 | 2714
| Max |  |  | 3.255 |  |  | 5.65 |  |  |  |  | 2.551 |  |  | 3.039
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -30.2822 | 3.6876 | 0.75693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -27.4567 | 4.4245 | 0.16261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -33.8377 | 3.8943 | -1.4341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -37.567 | 3.6721 | -2.7015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 0 | 0 | 0 | -35.0231 | 3.6641 | -4.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 15 | 9.31 | 9.31 | 90 | 25.87 | 25.87 | -35.993 | 3.803 | -1.779 | 0 | 0 | 0 | 5.6 | 3.06 | 7.01 | 15.55 | 8.51 | 19.48
| 7 | 60 | 36.36 | 36.36 | 275 | 52.6 | 52.6 | -38.7016 | 4.3213 | 0.21141 | 0 | 0 | 0 | 21.85 | 11.96 | 27.38 | 31.61 | 17.3 | 39.61
| 8 | 111 | 66.16 | 66.07 | 479 | 79.83 | 79.83 | -35.4235 | 4.3945 | 1.1998 | 104.3 | 55.73 | 138.85 | 39.76 | 21.77 | 49.82 | 47.98 | 26.27 | 60.11
| 9 | 158 | 93.88 | 92.71 | 668 | 166.73 | 101.35 | -36.8689 | 4.9064 | 2.2849 | 325.7 | 176.5 | 409.45 | 56.42 | 30.88 | 70.69 | 66.84 | 36.47 | 89.08
| 10 | 195 | 116.03 | 113.11 | 827 | 296.45 | 117.44 | -36.1031 | 6.2008 | 5.0591 | 484.4 | 265.7 | 592.98 | 69.73 | 38.17 | 87.37 | 112.79 | 60.56 | 163.22
| 11 | 263 | 156.44 | 148.79 | 941 | 390.91 | 126.74 | -34.5636 | 6.9765 | 5.4079 | 593.5 | 327.31 | 719.04 | 94.02 | 51.47 | 117.8 | 166.86 | 88.94 | 238.46
| 12 | 278 | 165.66 | 158.81 | 1003 | 441.65 | 130.36 | -33.6763 | 6.2647 | 5.1147 | 653.9 | 361.31 | 788.87 | 99.56 | 54.5 | 124.74 | 201.93 | 107.5 | 283.59
| 13 | 277 | 165.04 | 159.18 | 1008 | 445.59 | 238.98 | -31.6698 | 4.1911 | 5.5711 | 665 | 367.54 | 801.72 | 99.19 | 54.3 | 124.27 | 204.75 | 109.01 | 287.12
| 14 | 259 | 154 | 154.61 | 955 | 401.73 | 475.13 | -33.2373 | 3.1788 | 4.9914 | 623.5 | 344.22 | 753.75 | 92.55 | 50.67 | 115.96 | 173.86 | 92.64 | 247.65
| 15 | 227 | 134.48 | 140.01 | 848 | 312.89 | 672.39 | -33.224 | 1.9243 | 6.0132 | 534.1 | 293.82 | 650.33 | 80.82 | 44.24 | 101.26 | 121.01 | 64.87 | 175.19
| 16 | 181 | 106.77 | 114.38 | 696 | 187.67 | 809.04 | -33.5 | 1.1489 | 5.4557 | 396.8 | 216.33 | 492.04 | 64.17 | 35.13 | 80.4 | 72.45 | 39.45 | 98.49
| 17 | 104 | 62.05 | 63.55 | 509 | 83.9 | 861.62 | -34.0382 | 3.2979 | 6.5386 | 210.3 | 112.91 | 272.44 | 37.29 | 20.41 | 46.72 | 50.43 | 27.6 | 63.18
| 18 | 53 | 32.2 | 32.2 | 306 | 57.72 | 806.87 | -36.3464 | 3.2977 | 5.6681 | 0 | 0 | 0 | 19.35 | 10.59 | 24.25 | 34.69 | 18.99 | 43.46
| 19 | 11 | 6.81 | 6.81 | 114 | 30.17 | 578.91 | -36.4727 | 2.4978 | 5.1895 | 0 | 0 | 0 | 4.09 | 2.24 | 5.13 | 18.13 | 9.92 | 22.72
| 20 | 0 | 0 | 0 | 0 | 0 | 0 | -36.913 | 1.9983 | 5.7177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.9742 | 2.0062 | 2.1391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.9062 | 1.8319 | 2.1388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.9555 | 0.95143 | 1.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.5188 | 0.95172 | 0.44827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.032 | 0 | 1.803 | 2.67 | 1.186 | 2.05 | 1.225 | 0.792 | 0 |  | 1.202 | 0.724 | 0 | 0 | 0 | -0.017 | -0.449 | -0.422 | -0.223 | -0.241 | -0.821 | -0.77 | 12.7 | 18.1
| 2 | 2.042 | 0 | 1.782 | 2.694 | 1.246 | 2.059 | 1.264 | 0.928 | 0 |  | 1.224 | 0.814 | 0 | 0 | 0 | 0 | -0.286 | -0.302 | -0.069 | -0.119 | -0.701 | -0.642 | 10.1 | 17.7
| 3 | 2.123 | 0.459 | 1.82 | 2.819 | 1.341 | 2.139 | 1.356 | 1.063 | 0 |  | 1.323 | 0.942 | 0 | 0 | 0 | 0 | -0.155 | -0.209 | -0.012 | -0.037 | -0.574 | -0.541 | 10 | 17.2
| 4 | 2.228 | 1.053 | 1.881 | 2.973 | 1.44 | 2.243 | 1.453 | 1.187 | 0 |  | 1.408 | 1.054 | 0 | 0 | 0 | 0 | -0.017 | -0.115 | 0 | 0 | -0.483 | -0.434 | 10 | 16.7
| 5 | 2.307 | 1.231 | 1.923 | 3.088 | 1.514 | 2.321 | 1.526 | 1.296 | 0 |  | 1.439 | 1.142 | 0 | 0 | 0 | 0 | 0.11 | -0.023 | 0 | 0 | -0.4127 | -0.328 | 10 | 16.3
| 6 | 2.358 | 1.272 | 1.952 | 3.145 | 1.565 | 2.373 | 1.577 | 1.412 | 0 | 0.072 | 1.445 | 1.221 | 0 | 0 | 0 | 0 | 0.048 | -0.05 | 0 | 0 | -0.4064 | -0.33 | 10 | 15.8
| 7 | 2.385 | 1.306 | 1.969 | 3.154 | 1.591 | 2.401 | 1.604 | 1.54 | 0 | 0.211 | 1.459 | 1.285 | 0 | 0 | 0 | 0 | -0.274 | -0.242 | 0 | 0 | -0.5304 | -0.462 | 10 | 15.4
| 8 | 2.101 | 3.487 | 1.804 | 2.796 | 1.327 | 2.118 | 1.34 | 1.45 | 1.097 | 0.078 | 1.294 | 1.157 | 0 | 0 | 0 | 0 | -0.664 | -0.499 | 0 | -0.071 | -0.7226 | -0.626 | 15 | 17.6
| 9 | 1.048 | 3.024 | 1.191 | 1.524 | 0.532 | 1.068 | 0.363 | 0.724 | 1.669 |  | 1.0285 | 0.53 | 0 | 0 | 0 | 0 | -1.032 | -0.773 | -0.128 | -0.236 | -0.9494 | -0.811 | 20 | 20
| 10 | 0.139 | 0.185 | 0.37 | 0.298 | 0 | -0.479 | -1.088 | 0.149 | 0.62 |  | 0.106 | -0.675 | -0.332 | -0.141 | -0.324 | -0.291 | -1.499 | -1.133 | -0.453 | -0.487 | -1.2632 | -1.077 | 21.3 | 20
| 11 | -0.07 | -0.068 | 0 | 0 | -0.759 | -1.956 | -2.496 | 0 | 0.047 |  | -0.8215 | -1.617 | -1.246 | -0.797 | -1.402 | -0.988 | -2.125 | -1.62 | -0.771 | -0.832 | -1.71 | -1.447 | 24.8 | 20.7
| 12 | -1.616 | -1.581 | 0 | -1.564 | -2.604 | -3.25 | -3.726 | 0 | 0 | -0.068 | -1.6695 | -2.518 | -2.078 | -1.474 | -2.485 | -1.632 | -2.709 | -2.108 | -1.234 | -1.184 | -2.024 | -1.687 | 27 | 22.2
| 13 | -3.561 | -3.487 | -0.545 | -3.679 | -4.128 | -4.289 | -4.673 | 0 | 0 | -0.668 | -2.3805 | -3.021 | -2.457 | -1.707 | -2.996 | -2.018 | -3.08 | -2.48 | -1.545 | -1.422 | -2.243 | -1.884 | 27 | 23.9
| 14 | -4.028 | -3.945 | -1.376 | -4.214 | -4.575 | -4.731 | -5.066 | 0 | 0 | -1.302 | -2.566 | -3.186 | -2.618 | -1.809 | -3.234 | -2.189 | -3.24 | -2.649 | -1.667 | -1.553 | -2.346 | -1.984 | 27 | 25.2
| 15 | -3.839 | -3.759 | -1.55 | -3.989 | -4.445 | -4.545 | -4.931 | -0.128 | 0 | -1.555 | -2.464 | -3.042 | -2.588 | -1.824 | -3.202 | -2.124 | -3.208 | -2.582 | -1.652 | -1.593 | -2.342 | -1.971 | 27 | 25.9
| 16 | -3.244 | -3.243 | -1.192 | -3.33 | -3.918 | -3.952 | -4.405 | -0.128 | 0 | -1.453 | -2.206 | -2.718 | -2.388 | -1.741 | -2.922 | -1.896 | -3.006 | -2.354 | -1.581 | -1.517 | -2.25 | -1.872 | 27 | 25.8
| 17 | -2.197 | -2.215 | -0.576 | -2.176 | -2.906 | -2.904 | -3.392 | 0 | 0 | -0.73 | -1.521 | -2.122 | -2.096 | -1.567 | -2.521 | -1.645 | -2.716 | -2.106 | -1.472 | -1.417 | -2.131 | -1.763 | 27 | 24.6
| 18 | -0.779 | -0.786 | -0.102 | -0.736 | -1.436 | -1.365 | -1.92 | 0 | 0 | -0.092 | -0.817 | -1.32 | -1.763 | -1.335 | -2.084 | -1.403 | -2.389 | -1.864 | -1.343 | -1.284 | -1.988 | -1.643 | 26.8 | 23.2
| 19 | 0 | 0 | 0 | 0 | -0.295 | 0.009 | -0.65 | 0 | 0 |  | -0.11 | -0.788 | -1.404 | -1.08 | -1.63 | -1.131 | -2.036 | -1.593 | -1.201 | -1.121 | -1.807 | -1.479 | 25.4 | 22.2
| 20 | 0 | 0 | 0.061 | 0.146 | 0 | 0.767 | 0.037 | 0 | 0 |  | 0.216 | -0.385 | -0.995 | -0.775 | -1.128 | -0.832 | -1.631 | -1.295 | -1.018 | -0.938 | -1.61 | -1.294 | 22.8 | 21.4
| 21 | 0.413 | 0.401 | 0.76 | 1.072 | 0 | 1.239 | 0.474 | 0 | 0 |  | 0.499 | -0.01 | -0.593 | -0.461 | -0.642 | -0.555 | -1.237 | -1.02 | -0.832 | -0.788 | -1.433 | -1.135 | 20 | 20.8
| 22 | 1.266 | 1.239 | 1.518 | 2.06 | 0 | 1.583 | 0.783 | 0 | 0.041 |  | 0.7242 | 0.164 | -0.32 | -0.247 | -0.314 | -0.363 | -0.974 | -0.83 | -0.661 | -0.638 | -1.281 | -1.041 | 20 | 20.2
| 23 | 1.814 | 1.781 | 1.701 | 2.396 | 0.333 | 1.841 | 1.011 | 0.183 | 0.243 |  | 0.96 | 0.42 | -0.138 | -0.107 | -0.097 | -0.224 | -0.798 | -0.691 | -0.492 | -0.512 | -1.15 | -0.967 | 20 | 19.6
| 24 | 1.988 | 0.082 | 1.801 | 2.613 | 0.92 | 2.007 | 1.167 | 0.342 | 0.202 |  | 1.158 | 0.618 | -0.027 | -0.022 | 0 | -0.097 | -0.634 | -0.562 | -0.371 | -0.387 | -1.009 | -0.881 | 16.8 | 18.8
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 13 | 15.4 | 21.7 | 23.4 | 27.4 | 26.6
| 2 | 10.3 | 14.8 | 20.1 | 22.2 | 24 | 25.8
| 3 | 7.9 | 14.2 | 19 | 21.3 | 20.8 | 24.9
| 4 | 5.7 | 13.6 | 17.8 | 20.3 | 17.8 | 24
| 5 | 3.8 | 13 | 16.6 | 19.3 | 15 | 23.2
| 6 | 2.1 | 12.4 | 16.6 | 19.3 | 12.4 | 22.4
| 7 | 0.7 | 11.8 | 18.2 | 20.5 | 10.1 | 21.8
| 8 | 0.1 | 11.2 | 20.3 | 22.1 | 8.7 | 21.4
| 9 | 1.7 | 11.8 | 22.3 | 23.4 | 9.5 | 22
| 10 | 6.1 | 13.4 | 24.9 | 24.5 | 13.1 | 23.5
| 11 | 12.5 | 15.7 | 28.3 | 25.8 | 19.1 | 25.5
| 12 | 20.2 | 18.4 | 32.3 | 27.4 | 26.7 | 27.8
| 13 | 28.5 | 21.3 | 36.2 | 28.7 | 35.2 | 30.2
| 14 | 36.1 | 23.2 | 39.7 | 29.8 | 43.4 | 32.3
| 15 | 41.9 | 24.8 | 42.5 | 30.6 | 50.2 | 33.8
| 16 | 45.4 | 25.4 | 44.4 | 31 | 55.1 | 34.6
| 17 | 46.3 | 24.6 | 45.4 | 31.4 | 57.3 | 34
| 18 | 44 | 23.5 | 41.7 | 31 | 56.3 | 32.9
| 19 | 39.5 | 22.6 | 35.5 | 30.3 | 53 | 32
| 20 | 34.4 | 21.9 | 31.7 | 29.1 | 48.8 | 31.2
| 21 | 29.3 | 20.8 | 28.6 | 28.1 | 44.3 | 30.3
| 22 | 24.6 | 20 | 26.5 | 27 | 39.8 | 29.4
| 23 | 20.2 | 19.2 | 25 | 26 | 35.4 | 28.4
| 24 | 16.3 | 18.1 | 23.5 | 24.9 | 31.2 | 27.4
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 3
| 1 | 13
| 2 | 32
| 3 | 41
| 4 | 57
| 5 | 63
| 6 | 67
| 7 | 87
| 8 | 97
| 9 | 104
| 10 | 155
| 11 | 151
| 12 | 142
| 13 | 156
| 14 | 170
| 15 | 166
| 16 | 211
| 17 | 199
| 18 | 211
| 19 | 257
| 20 | 318
| 21 | 263
| 22 | 269
| 23 | 273
| 24 | 260
| 25 | 308
| 26 | 339
| 27 | 330
| 28 | 341
| 29 | 409
| 30 | 382
| 31 | 426
| 32 | 433
| 33 | 391
| 34 | 332
| 35 | 291
| 36 | 244
| 37 | 184
| 38 | 167
| 39 | 145
| 40 | 102
| 41 | 76
| 42 | 41
| 43 | 27
| 44 | 22
| 45 | 5
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## CSE
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below. | [7 empty] | Note: Submitted CSE month formats don't match specified, if update
Keep VLOOKUP routine
MONTH |  | CODE | [6 empty] | See Rows 67, 127, 178, 500
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
[Note to Participants: Editorial changes: went with Hour 8 as example and 0n00 format (pertinent to Jan2018 discussion re Case 640)]
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracikng colors are:
Red is for edits from June 2013 through September 2017 distribution for the Round 3 sim trial draft.
Blue is for edits since Sep 2017 (since Sec5-2Aout-082917.xlsx):
editorial (not substantive) clarification re "hourly integrated"
| Software: | CSE
| Version: | 0.861.1
| Date of Results: | 2019-04-15 09:46:38.912566
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS | [7 empty] | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling | [7 empty] | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour |  | Month* | Day | Hour | kW | Month*
| 600 | 3.9928 | 5.9131 | 3.0202 | Jan | 1 | 1 | 6.481 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.481 | 1 |  | IF
| 610 | 4.0664 | 4.3818 | 3.0208 | Jan | 1 | 1 | 6.4322 | Dec | 1 | 14 |  | 1 | 1 | 1 | 6.4322 | 12
| 620 | 4.0936 | 4.0793 | 3.0379 | Jan | 1 | 1 | 4.4928 | Jun | 26 | 17 |  | 1 | 1 | 1 | 4.4928 | 6
| 630 | 4.3559 | 3.0204 | 3.0394 | Jan | 1 | 1 | 3.9983 | Jun | 26 | 18 |  | 1 | 1 | 1 | 3.9983 | 6 |  | Jan
| 640 | 2.4032 | 5.6439 | 4.2225 | Nov | 26 | 8 | 6.429 | Jan | 22 | 14 |  | 11 | 26 | 8 | 6.429 | 1 |  | Nov | VLOOKUP Table: Number to Mmm
| 650 | 0 | 4.6539 | 0 | Jan | 1 | 1 | 6.2897 | Dec | 1 | 14 |  | 1 | 1 | 1 | 6.2897 | 12
| 660 | 3.602 | 3.3397 | 2.7583 | Jan | 1 | 1 | 3.933 | Oct | 1 | 13 |  | 1 | 1 | 1 | 3.933 | 10 |  | 1 | Jan
| 670 | 5.3002 | 6.5777 | 3.6554 | Jan | 1 | 1 | 6.9253 | Oct | 1 | 13 |  | 1 | 1 | 1 | 6.9253 | 10 |  | 2 | Feb
| 680 | 1.7861 | 6.4298 | 1.7776 | Feb | 9 | 6 | 7.0513 | Jan | 22 | 14 |  | 2 | 9 | 6 | 7.0513 | 1 |  | 3 | Mar
| 685 | 4.5744 | 8.8592 | 3.0319 | Jan | 1 | 1 | 7.1594 | Jan | 22 | 14 |  | 1 | 1 | 1 | 7.1594 | 1 |  | 4 | Apr
| 695 | 2.4153 | 8.9741 | 1.7953 | Jan | 1 | 1 | 7.5407 | Jan | 22 | 14 |  | 1 | 1 | 1 | 7.5407 | 1 |  | 5 | May
| 900 | 1.3789 | 2.4638 | 2.4434 | Feb | 9 | 6 | 3.3764 | Oct | 1 | 14 |  | 2 | 9 | 6 | 3.3764 | 10 |  | 6 | Jun
| 910 | 1.6477 | 1.4149 | 2.469 | Feb | 9 | 6 | 2.7221 | Oct | 2 | 15 |  | 2 | 9 | 6 | 2.7221 | 10 |  | 7 | Jul
| 920 | 2.9561 | 2.7892 | 2.5124 | Feb | 9 | 6 | 3.0567 | Jun | 26 | 18 |  | 2 | 9 | 6 | 3.0567 | 6 |  | 8 | Aug
| 930 | 3.5236 | 2.075 | 2.537 | Feb | 9 | 6 | 2.6618 | Jun | 26 | 18 |  | 2 | 9 | 6 | 2.6618 | 6 |  | 9 | Sep
| 940 | 0.86324 | 2.3966 | 3.0519 | Jan | 1 | 9 | 3.3764 | Oct | 1 | 14 |  | 1 | 1 | 9 | 3.3764 | 10 |  | 10 | Oct
| 950 | 0 | 0.59803 | 0 | Jan | 1 | 1 | 2.3635 | Sep | 4 | 15 |  | 1 | 1 | 1 | 2.3635 | 9 |  | 11 | Nov
| 960 | 2.5221 | 0.92578 | 2.132 | Feb | 9 | 6 | 1.3771 | Jun | 26 | 17 |  | 2 | 9 | 6 | 1.3771 | 6 |  | 12 | Dec
| 980 | 0.24577 | 3.9953 | 1.2538 | Feb | 9 | 6 | 3.668 | Oct | 2 | 14 |  | 2 | 9 | 6 | 3.668 | 10
| 985 | 2.1202 | 6.2336 | 2.4522 | Feb | 9 | 6 | 4.2253 | Oct | 1 | 14 |  | 2 | 9 | 6 | 4.2253 | 10
| 995 | 0.75518 | 7.2022 | 1.3696 | Feb | 9 | 6 | 4.2238 | Jan | 22 | 15 |  | 2 | 9 | 6 | 4.2238 | 1
| 195 | 3.9901 | 0.60552 | 1.7907 | Jan | 1 | 1 | 0.99425 | Jun | 26 | 17 |  | 1 | 1 | 1 | 0.99425 | 6
| 200 | 4.8135 | 0.80024 | 2.226 | Nov | 26 | 8 | 1.2152 | Jun | 26 | 17 |  | 11 | 26 | 8 | 1.2152 | 6
| 210 | 5.9663 | 0.50307 | 2.629 | Jan | 1 | 2 | 0.94562 | Jun | 13 | 15 |  | 1 | 1 | 2 | 0.94562 | 6
| 215 | 5.3066 | 0.94579 | 2.42 | Nov | 26 | 8 | 1.3692 | Jun | 26 | 17 |  | 11 | 26 | 8 | 1.3692 | 6
| 220 | 6.6663 | 0.6106 | 2.8394 | Jan | 1 | 1 | 1.1085 | Jun | 13 | 15 |  | 1 | 1 | 1 | 1.1085 | 6
| 230 | 9.8124 | 0.99134 | 4.1329 | Jan | 1 | 1 | 1.7281 | Jun | 26 | 17 |  | 1 | 1 | 1 | 1.7281 | 6
| 240 | 5.4426 | 0.98237 | 2.6514 | Jan | 1 | 1 | 1.2947 | Jun | 13 | 15 |  | 1 | 1 | 1 | 1.2947 | 6
| 250 | 5.0438 | 3.429 | 2.8371 | Jan | 1 | 1 | 2.79 | Sep | 12 | 14 |  | 1 | 1 | 1 | 2.79 | 9
| 270 | 4.3465 | 7.2708 | 2.6114 | Jan | 1 | 2 | 7.011 | Jan | 22 | 14 |  | 1 | 1 | 2 | 7.011 | 1
| 280 | 4.5249 | 4.9963 | 2.6122 | Jan | 1 | 2 | 4.7651 | Jan | 22 | 14 |  | 1 | 1 | 2 | 4.7651 | 1
| 290 | 4.4242 | 5.6097 | 2.6115 | Jan | 1 | 2 | 6.8722 | Jan | 22 | 14 |  | 1 | 1 | 2 | 6.8722 | 1
| 300 | 4.3184 | 5.0551 | 2.6141 | Jan | 1 | 1 | 4.1631 | Jun | 26 | 17 |  | 1 | 1 | 1 | 4.1631 | 6
| 310 | 4.5803 | 3.7519 | 2.6149 | Jan | 1 | 1 | 3.7959 | Jun | 26 | 18 |  | 1 | 1 | 1 | 3.7959 | 6
| 320 | 3.6775 | 4.8585 | 2.609 | Jan | 1 | 1 | 6.4733 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.4733 | 1
| 395 | 4.855 | 0.007762 | 2.1574 | Jan | 1 | 2 | 0.3575 | Jun | 14 | 18 |  | 1 | 1 | 2 | 0.3575 | 6
| 400 | 6.5358 | 0.023304 | 2.8394 | Jan | 1 | 1 | 0.49365 | Jun | 14 | 15 |  | 1 | 1 | 1 | 0.49365 | 6
| 410 | 8.0451 | 0.048491 | 3.4407 | Jan | 1 | 1 | 0.69988 | Jun | 26 | 18 |  | 1 | 1 | 1 | 0.69988 | 6
| 420 | 6.8345 | 0.14062 | 3.2562 | Jan | 1 | 1 | 0.90853 | Jun | 26 | 18 |  | 1 | 1 | 1 | 0.90853 | 6
| 430 | 5.454 | 0.90616 | 3.2539 | Jan | 1 | 1 | 1.8398 | Jun | 26 | 15 |  | 1 | 1 | 1 | 1.8398 | 6
| 440 | 4.1559 | 3.9853 | 3.0272 | Jan | 1 | 1 | 4.6655 | Oct | 1 | 13 |  | 1 | 1 | 1 | 4.6655 | 10
| 450 | 3.9904 | 5.689 | 2.9783 | Jan | 1 | 1 | 6.1798 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.1798 | 1
| 460 | 4.0555 | 5.9398 | 2.9714 | Jan | 1 | 1 | 6.2429 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.2429 | 1
| 470 | 3.8995 | 5.6439 | 3.0007 | Jan | 1 | 1 | 6.3877 | Jan | 22 | 14 |  | 1 | 1 | 1 | 6.3877 | 1
| 800 | 4.9057 | 0.37983 | 2.7776 | Feb | 9 | 6 | 1.1019 | Aug | 5 | 15 |  | 2 | 9 | 6 | 1.1019 | 8
| 810 | 2.0375 | 1.4807 | 2.5001 | Feb | 9 | 6 | 2.4105 | Sep | 4 | 15 |  | 2 | 9 | 6 | 2.4105 | 9
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes | [7 empty] | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum | [7 empty] | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour |  | Month* | Day | Hour | °C | Month*
| 600FF | 25.5736 | -12.8904 | Feb | 9 | 7 | 68.3608 | Oct | 1 | 16 |  | 2 | 9 | 7 | 67.8478 | 10
| 900FF | 25.6921 | 2.1647 | Feb | 9 | 7 | 45.1138 | Sep | 4 | 15 |  | 2 | 9 | 7 | 44.7403 | 9
| 650FF | 18.4599 | -17.7616 | Jan | 1 | 1 | 66.8465 | Oct | 1 | 16 |  | 1 | 1 | 1 | 66.4036 | 10
| 950FF | 14.7096 | -13.2443 | Jan | 1 | 1 | 36.7765 | Sep | 11 | 15 |  | 1 | 1 | 1 | 36.6444 | 9
| 680FF | 33.1103 | -6.1966 | Feb | 9 | 7 | 78.5143 | Jan | 22 | 16 |  | 2 | 9 | 7 | 78.4503 | 1
| 980FF | 33.2952 | 12.5361 | Nov | 4 | 7 | 52.2464 | Sep | 12 | 15 |  | 11 | 4 | 7 | 51.9433 | 9
| 960 | 28.5573 | 8.0165 | Feb | 9 | 8 | 48.9033 | Oct | 2 | 16 |  | 2 | 9 | 8 | 48.5662 | 10
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1662.5278
| NORTH | 399.0475
| EAST | 1026.9874
| SOUTH | 1316.9162
| WEST | 903.0665
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 825.5194
| 660/South | 501.3136
| 670/South | 987.8182
620/West
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 665.2609
630/West
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -3.9307 | -46.2246 | Dec | 31 | 24 | 30.0812 | Jun | 13 | 15 |  | 12 | 31 | 24 | 30.0812 | 6
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 655.585 | 554.0235 | 3.0202 | 1 | 1 | 6.481 | 22 | 14 | 206.1043 | 67.8041 | 2.0774 | 1 | 5 | 2.2416 | 22 | 15
| Feb | 626.2627 | 394.2972 | 2.8997 | 9 | 6 | 5.3928 | 15 | 14 | 243.2297 | 15.1117 | 2.4434 | 9 | 6 | 0.99617 | 15 | 15
| Mar | 435.7419 | 474.3508 | 2.0344 | 17 | 6 | 5.1483 | 24 | 13 | 102.4399 | 68.5488 | 1.6129 | 17 | 6 | 1.4341 | 24 | 15
| Apr | 456.9543 | 220.1356 | 2.2073 | 11 | 6 | 4.0151 | 27 | 14 | 222.3692 | 12.3134 | 1.7706 | 3 | 4 | 0.63116 | 19 | 14
| May | 127.7958 | 321.1602 | 1.5922 | 1 | 5 | 3.0796 | 21 | 14 | 33.3469 | 117.8126 | 1.1425 | 1 | 5 | 1.4272 | 21 | 14
| Jun | 11.6999 | 497.4498 | 0.77848 | 9 | 5 | 3.2488 | 13 | 13 | 0 | 372.2992 | 0 | 1 | 1 | 1.8967 | 14 | 14
| Jul | 11.5431 | 505.8671 | 0.53975 | 26 | 5 | 3.2903 | 17 | 14 | 0 | 380.4363 | 0 | 1 | 1 | 1.943 | 17 | 14
| Aug | 6.9186 | 606.5032 | 0.55338 | 17 | 6 | 4.1195 | 8 | 14 | 0 | 485.6761 | 0 | 1 | 1 | 2.4852 | 5 | 14
| Sep | 74.3067 | 705.1929 | 1.1204 | 29 | 1 | 5.4503 | 2 | 14 | 0 | 484.0294 | 0 | 1 | 1 | 3.1368 | 4 | 14
| Oct | 328.4088 | 676.133 | 1.6237 | 15 | 6 | 6.2702 | 1 | 13 | 65.0694 | 305.5693 | 1.1882 | 7 | 7 | 3.3764 | 1 | 14
| Nov | 575.553 | 454.7409 | 2.8502 | 26 | 8 | 6.149 | 28 | 13 | 251.5988 | 80.4854 | 2.0863 | 26 | 8 | 2.2328 | 20 | 15
| Dec | 681.9851 | 503.27 | 2.9413 | 31 | 24 | 6.45 | 1 | 14 | 254.733 | 73.7394 | 1.9268 | 31 | 8 | 2.1054 | 1 | 15
| Total | 3992.755 | 5913.1242 | [6 empty] | 1378.8913 | 2463.8258
| Max |  |  | 3.0202 |  |  | 6.481 |  |  |  |  | 2.4434 |  |  | 3.3764
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -22.8397 | 0.38605 | 0.90277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -26.6414 | 0.40933 | 0.31055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -28.0897 | 0.32324 | -0.83045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -33.7622 | 0.019551 | -2.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 1.4992 | 0.54029 | 0.54029 | -35.2444 | -0.026626 | -3.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34752 | 0.21439 | 0.41726
| 6 | 15.0006 | 9.0004 | 9.0004 | 82.0455 | 15.3297 | 15.3297 | -35.6508 | -0.077933 | -2.9391 | 0 | 0 | 0 | 5.76 | 3.544 | 6.9223 | 9.793 | 6.0253 | 11.7918
| 7 | 60.0025 | 36.0015 | 36.0015 | 264.1993 | 34.4328 | 34.4328 | -37.5801 | 0.1937 | -0.80157 | 0 | 0 | 0 | 23.0255 | 14.1619 | 27.6826 | 21.8537 | 13.4169 | 26.3554
| 8 | 111.0047 | 66.6028 | 66.6028 | 465.8199 | 55.5566 | 55.5479 | -37.0009 | 0.43445 | 0.63558 | 82.0324 | 50.937 | 107.13 | 42.4983 | 26.0993 | 51.1502 | 35.0242 | 21.4445 | 42.3184
| 9 | 158.0065 | 94.8038 | 94.8038 | 656.5745 | 139.4762 | 75.5077 | -36.328 | 0.70848 | 1.6749 | 297.541 | 180.8792 | 362.8681 | 60.5559 | 37.2213 | 72.8793 | 52.8909 | 32.3826 | 67.7615
| 10 | 195.008 | 117.0048 | 117.0048 | 816.0523 | 272.6453 | 91.9039 | -36.5645 | 1.807 | 3.6938 | 459.7525 | 278.4931 | 545.2226 | 74.7815 | 46.0006 | 90.0133 | 106.0912 | 66.3123 | 144.8439
| 11 | 263.0108 | 157.8065 | 157.8065 | 931.7134 | 372.0415 | 103.7499 | -35.3739 | 3.0787 | 5.1376 | 578.5582 | 348.905 | 675.1871 | 100.3258 | 61.4812 | 121.0763 | 171.3254 | 107.1366 | 229.0314
| 12 | 278.0116 | 166.8069 | 166.8069 | 996.141 | 427.7583 | 110.2849 | -34.1943 | 3.2866 | 5.1381 | 652.8082 | 391.0585 | 749.7897 | 105.248 | 64.2908 | 127.4075 | 214.7217 | 133.6999 | 280.7528
| 13 | 277.0115 | 166.2068 | 166.2068 | 1002.0363 | 433.4522 | 207.6793 | -32.6854 | 2.1422 | 5.2613 | 673.3877 | 404.3853 | 768.3238 | 104.1118 | 63.1249 | 126.1131 | 213.836 | 132.4799 | 281.1221
| 14 | 259.0108 | 155.4066 | 155.4066 | 951.5143 | 389.6588 | 443.3988 | -32.6302 | 0.78812 | 5.1527 | 628.6623 | 377.3723 | 720.0014 | 97.1633 | 58.8997 | 117.7605 | 181.0836 | 112.4723 | 242.0489
| 15 | 227.0095 | 136.2054 | 136.2054 | 847.7872 | 300.3721 | 644.8859 | -33.3209 | -0.62158 | 5.4585 | 528.0285 | 316.992 | 613.0512 | 85.3291 | 51.7282 | 103.3009 | 121.3543 | 75.3683 | 166.4995
| 16 | 181.0076 | 108.6046 | 108.6046 | 697.2651 | 174.1119 | 787.9666 | -33.4665 | -0.73525 | 5.6185 | 378.3411 | 229.4327 | 452.897 | 68.2121 | 41.4256 | 82.5129 | 63.7931 | 38.9794 | 83.7436
| 17 | 104.0043 | 62.4026 | 62.4026 | 511.7801 | 64.3006 | 850.1509 | -33.8865 | -0.44746 | 5.9695 | 191.9413 | 117.7938 | 241.2176 | 39.5371 | 24.1701 | 47.709 | 37.6588 | 22.8693 | 45.4814
| 18 | 53.0022 | 31.8013 | 31.8013 | 309.2767 | 39.0057 | 805.1397 | -35.3916 | -0.64839 | 5.9794 | 14.3991 | 9.06 | 19.1922 | 20.2628 | 12.4348 | 24.4004 | 24.2426 | 14.709 | 29.321
| 19 | 11.0004 | 6.6003 | 6.6003 | 116.1785 | 18.8437 | 590.3427 | -36.4941 | -0.91461 | 5.3256 | 0 | 0 | 0 | 4.2104 | 2.5852 | 5.0665 | 11.6997 | 7.1153 | 14.1359
| 20 | 0 | 0 | 0 | 5.5971 | 1.841 | 78.5987 | -36.7865 | -1.4056 | 5.4067 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1413 | 0.69581 | 1.3866
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.563 | -1.607 | 3.6698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.5529 | -1.9502 | 2.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.9993 | -2.8551 | 1.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.7814 | -3.3493 | 0.85954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 1.8838 | 0.00043451 | 1.6843 | 2.3394 | 0.99585 | 1.9212 | 1.145 | 0.71655 | 0 | 0 | 0.9489 | 0.32105 | 0 | 0 | 0 | 0 | -0.049027 | -0.13418 | -0.052736 | -0.18841 | -0.64521 | -0.57478 | 11.1142 | 16.6192
| 2 | 1.9935 | 0.39261 | 1.779 | 2.4806 | 1.1111 | 2.0146 | 1.2047 | 0.84236 | 0 | 0 | 1.0473 | 0.40368 | 0 | 0 | 0 | 0 | 0.02692 | -0.081538 | -0.0012209 | -0.13027 | -0.55887 | -0.51269 | 10 | 16.0221
| 3 | 2.0547 | 0.80293 | 1.8309 | 2.5674 | 1.1938 | 2.0666 | 1.2518 | 0.94623 | 0 | 0 | 1.1317 | 0.47533 | 0 | 0 | 0 | 0 | 0.11975 | -0.026795 | 0 | -0.068221 | -0.46354 | -0.44442 | 10 | 15.4654
| 4 | 2.1202 | 1.034 | 1.8839 | 2.6744 | 1.2656 | 2.1268 | 1.3012 | 1.0458 | 0 | 0 | 1.2243 | 0.55403 | 0 | 0 | 0.001611 | 0 | 0.24941 | 0.034874 | 0 | -0.0086705 | -0.3547 | -0.36915 | 10 | 14.9003
| 5 | 2.1532 | 1.1731 | 1.9135 | 2.7158 | 1.2984 | 2.1569 | 1.3204 | 1.1187 | 0 | 0 | 1.2901 | 0.60291 | 0 | 0 | 0.20148 | 0 | 0.34005 | 0.098044 | 0 | 0 | -0.26008 | -0.29783 | 10 | 14.3857
| 6 | 2.1631 | 1.2448 | 1.9223 | 2.7285 | 1.3219 | 2.1651 | 1.3355 | 1.1879 | 0 | 0 | 1.351 | 0.64819 | 0 | 0 | 0.20839 | 0 | 0.23558 | 0.064405 | 0 | 0 | -0.25356 | -0.30657 | 10 | 13.9037
| 7 | 2.1843 | 1.3018 | 1.9415 | 2.7542 | 1.3375 | 2.1854 | 1.3459 | 1.2589 | 0 | 0 | 1.4134 | 0.68594 | 0 | 0 | 0.0044408 | 0 | -0.1131 | -0.089405 | 0 | -0.018269 | -0.35224 | -0.38991 | 10 | 13.4247
| 8 | 1.7765 | 3.0205 | 1.6726 | 2.2606 | 1.0054 | 1.777 | 1.0098 | 1.0863 | 0.90177 | 0 | 1.226 | 0.52924 | 0 | 0 | 0 | 0 | -0.4792 | -0.3116 | 0 | -0.11586 | -0.49552 | -0.48515 | 15.5 | 15.9016
| 9 | 0.5478 | 1.6521 | 0.80151 | 0.84369 | 0.17368 | 0.54801 | 0.059474 | 0.53703 | 1.1161 | 0 | 0.63568 | 0.086248 | 0 | 0 | 0 | 0 | -0.89805 | -0.61456 | -0.070157 | -0.24815 | -0.68807 | -0.62671 | 20 | 20
| 10 | 0 | 0.075395 | 0.082875 | 0.0024258 | -0.053007 | -0.95761 | -1.666 | 0.11777 | 0.49385 | 0 | 0.19897 | -0.50421 | -0.16869 | -0.059292 | -0.19006 | -0.18419 | -1.5518 | -1.1481 | -0.36695 | -0.50733 | -1.0367 | -0.92083 | 20.7841 | 20
| 11 | -0.92066 | -0.40515 | 0 | -0.99799 | -1.9332 | -2.8606 | -3.5885 | 0 | 0.066615 | -0.028774 | -0.34013 | -1.1965 | -1.2347 | -0.78553 | -1.5089 | -1.0716 | -2.3959 | -1.8678 | -0.76666 | -0.86339 | -1.4712 | -1.2898 | 26.0342 | 20.1042
| 12 | -3.0739 | -2.6298 | -0.45456 | -3.2655 | -4.069 | -4.335 | -5.0849 | 0 | 0 | -0.56154 | -0.98196 | -1.8905 | -2.2634 | -1.5756 | -2.7261 | -1.9293 | -3.1327 | -2.5371 | -1.1411 | -1.1778 | -1.8619 | -1.6114 | 27 | 21.6771
| 13 | -4.364 | -4.1733 | -1.6509 | -4.6214 | -5.3127 | -5.2497 | -5.993 | 0 | 0 | -1.192 | -1.5878 | -2.4977 | -2.7049 | -1.9242 | -3.2555 | -2.4066 | -3.4278 | -2.9109 | -1.3558 | -1.3736 | -2.0803 | -1.8125 | 27 | 23.7146
| 14 | -4.6667 | -4.592 | -2.1461 | -4.8903 | -5.5694 | -5.3818 | -6.0919 | 0 | 0 | -1.5455 | -1.9023 | -2.7863 | -2.7504 | -2.0023 | -3.3127 | -2.4752 | -3.4049 | -2.9258 | -1.4518 | -1.4517 | -2.1666 | -1.888 | 27 | 24.982
| 15 | -4.0529 | -4.0239 | -1.9151 | -4.1429 | -5.054 | -4.6926 | -5.5054 | -0.02487 | 0 | -1.6506 | -1.9331 | -2.8206 | -2.449 | -1.8527 | -2.9394 | -2.1675 | -3.0702 | -2.5909 | -1.3908 | -1.3713 | -2.0876 | -1.8001 | 27 | 25.2873
| 16 | -2.8873 | -2.8759 | -1.281 | -2.8645 | -3.941 | -3.486 | -4.3565 | -0.0054093 | 0 | -1.5424 | -1.7333 | -2.6157 | -1.9631 | -1.5702 | -2.2909 | -1.6634 | -2.5639 | -2.0688 | -1.2243 | -1.1792 | -1.8986 | -1.5962 | 27 | 25.2471
| 17 | -1.329 | -1.3246 | -0.38043 | -1.1447 | -2.3532 | -1.8707 | -2.7253 | 0 | 0 | -1.1511 | -1.2638 | -2.1061 | -1.5159 | -1.2726 | -1.6885 | -1.2613 | -2.101 | -1.6542 | -1.0839 | -1.0349 | -1.7366 | -1.4401 | 27 | 24.4059
| 18 | -0.036587 | -0.036104 | 0 | 0 | -0.51365 | -0.062132 | -0.87523 | 0 | 0 | -0.46865 | -0.54502 | -1.3534 | -1.1667 | -1.0133 | -1.2498 | -0.97604 | -1.7475 | -1.3655 | -0.97268 | -0.93142 | -1.612 | -1.3312 | 25.7064 | 22.6175
| 19 | 0.047689 | 0.048108 | 0.068677 | 0.3733 | 0 | 1.0222 | 0.15843 | 0 | 0 | -0.10765 | -0.13333 | -0.91496 | -0.84578 | -0.76378 | -0.8713 | -0.7202 | -1.4176 | -1.1029 | -0.8477 | -0.81522 | -1.4718 | -1.2069 | 21.3714 | 21.3767
| 20 | 0.87302 | 0.87401 | 0.85087 | 1.5232 | 0 | 1.6012 | 0.60708 | 0 | 0 | 0 | 0.11696 | -0.64822 | -0.48174 | -0.45877 | -0.45588 | -0.4781 | -1.0309 | -0.84841 | -0.71147 | -0.69185 | -1.3161 | -1.0712 | 20 | 20.564
| 21 | 1.5518 | 1.5523 | 1.4115 | 2.1392 | 0.064176 | 1.9179 | 0.89914 | 0 | 0.086615 | 0 | 0.34273 | -0.42283 | -0.1626 | -0.17946 | -0.099993 | -0.27107 | -0.69086 | -0.63671 | -0.58603 | -0.58322 | -1.1782 | -0.95683 | 20 | 20.0224
| 22 | 1.9363 | 1.9366 | 1.7543 | 2.4968 | 0.54736 | 2.1437 | 1.1068 | 0 | 0.33452 | 0 | 0.54685 | -0.23074 | -0.010249 | -0.026977 | 0 | -0.12549 | -0.49742 | -0.49022 | -0.48581 | -0.49948 | -1.0709 | -0.87231 | 20 | 20
| 23 | 2.1702 | 2.1703 | 1.9598 | 2.7218 | 0.88344 | 2.2881 | 1.2559 | 0.081877 | 0.54165 | 0 | 0.71216 | -0.065507 | 0 | 0 | 0 | -0.025991 | -0.37088 | -0.38407 | -0.39359 | -0.42484 | -0.97062 | -0.79533 | 20 | 20
| 24 | 2.2658 | 0 | 2.0439 | 2.8049 | 1.0938 | 2.3327 | 1.3349 | 0.29481 | 0 | 0 | 0.82345 | 0.055548 | 0 | 0 | 0 | 0 | -0.25271 | -0.28879 | -0.28879 | -0.33992 | -0.85843 | -0.70925 | 12.9579 | 18.1003
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 7.3199 | 14.7379 | 19.8311 | 21.2148 | 19.3025 | 27.6665
| 2 | 5.475 | 14.2075 | 19.0165 | 20.7077 | 17.2859 | 27.1526
| 3 | 3.8429 | 13.7002 | 18.1137 | 20.0478 | 15.4125 | 26.66
| 4 | 2.3514 | 13.1833 | 16.994 | 19.188 | 13.6262 | 26.1515
| 5 | 1.0503 | 12.7111 | 15.8658 | 18.2994 | 11.9969 | 25.6862
| 6 | -0.033328 | 12.2668 | 16.1929 | 18.5567 | 10.5252 | 25.2544
| 7 | -1.0231 | 11.8353 | 18.4147 | 20.0938 | 9.1662 | 24.8308
| 8 | -0.98405 | 11.941 | 20.1417 | 22.4421 | 8.8545 | 24.9686
| 9 | 2.4994 | 13.2165 | 22.2539 | 23.5009 | 11.6688 | 26.3146
| 10 | 9.5334 | 15.2859 | 25.3076 | 24.6745 | 17.8327 | 28.2183
| 11 | 17.965 | 17.5497 | 29.4735 | 26.1394 | 25.8327 | 30.208
| 12 | 26.9295 | 19.8553 | 34.0869 | 27.5275 | 34.849 | 32.2226
| 13 | 35.5894 | 22.0025 | 38.0756 | 28.5007 | 43.9435 | 34.0812
| 14 | 42.8259 | 23.2661 | 41.1874 | 29.1549 | 51.6986 | 35.3862
| 15 | 47.0783 | 23.5646 | 43.0949 | 29.3989 | 57.0436 | 35.9936
| 16 | 48.2109 | 23.5055 | 43.7728 | 29.2893 | 59.5967 | 36.0431
| 17 | 45.9023 | 22.7021 | 43.4747 | 29.1458 | 58.7261 | 35.2665
| 18 | 39.9832 | 20.9392 | 42.6822 | 29.0474 | 54.2792 | 33.6073
| 19 | 33.3 | 19.7278 | 34.1248 | 28.666 | 49.0597 | 32.4976
| 20 | 27.5274 | 18.9536 | 30.7295 | 27.3534 | 44.294 | 31.7818
| 21 | 22.5321 | 18.2399 | 27.846 | 26.0894 | 39.9085 | 31.126
| 22 | 18.1055 | 17.5304 | 25.8648 | 25.2973 | 35.8862 | 30.5149
| 23 | 14.1487 | 16.8299 | 24.4442 | 24.6727 | 32.1123 | 29.9001
| 24 | 10.8188 | 16.228 | 22.9121 | 23.7451 | 28.6933 | 29.355
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 0
| 2 | 4
| 3 | 7
| 4 | 23
| 5 | 25
| 6 | 36
| 7 | 44
| 8 | 65
| 9 | 74
| 10 | 98
| 11 | 117
| 12 | 148
| 13 | 211
| 14 | 206
| 15 | 208
| 16 | 255
| 17 | 288
| 18 | 253
| 19 | 329
| 20 | 365
| 21 | 323
| 22 | 327
| 23 | 316
| 24 | 283
| 25 | 286
| 26 | 299
| 27 | 287
| 28 | 319
| 29 | 340
| 30 | 362
| 31 | 417
| 32 | 429
| 33 | 417
| 34 | 390
| 35 | 335
| 36 | 272
| 37 | 210
| 38 | 150
| 39 | 77
| 40 | 60
| 41 | 40
| 42 | 30
| 43 | 21
| 44 | 11
| 45 | 3
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## DeST
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | DeST | DeST
| Version: |  | 2.0-20190401
| Date of Results: |  | May 20. 2019
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.047 | 5.432 | 3.035 | Jan | 1 | 0 | 5.422 | Jan | 22 | 14
| 610 | 4.144 | 4.173 | 3.039 | Jan | 1 | 0 | 5.331 | Jan | 22 | 14
| 620 | 4.297 | 3.909 | 3.068 | Jan | 1 | 0 | 3.955 | Jun | 26 | 17
| 630 | 4.677 | 2.787 | 3.072 | Jan | 1 | 0 | 3.526 | Jun | 26 | 17
| 640 | 2.619 | 5.237 | 4.658 | Nov | 26 | 7 | 5.365 | Jan | 22 | 14
| 650 | 0 | 4.186 | 0 |  |  |  | 5.045 | Oct | 18 | 14
| 660 | 3.821 | 3.26 | 2.798 | Jan | 1 | 0 | 3.355 | Oct | 11 | 14
| 670 | 5.573 | 5.954 | 3.812 | Jan | 1 | 0 | 5.839 | Oct | 10 | 13
| 680 | 1.732 | 5.932 | 1.811 | Jan | 1 | 1 | 5.861 | Jan | 22 | 14
| 685 | 4.646 | 8.238 | 3.054 | Jan | 1 | 0 | 6.071 | Jan | 22 | 14
| 695 | 2.385 | 8.386 | 1.855 | Jan | 1 | 1 | 6.355 | Jan | 22 | 14
| 900 | 1.591 | 2.383 | 2.453 | Feb | 9 | 5 | 2.556 | Sep | 11 | 14
| 910 | 1.86 | 1.49 | 2.474 | Feb | 9 | 5 | 2.103 | Oct | 12 | 14
| 920 | 3.259 | 2.706 | 2.513 | Feb | 9 | 5 | 2.71 | Jun | 26 | 17
| 930 | 3.933 | 1.908 | 2.549 | Feb | 9 | 5 | 2.335 | Jun | 26 | 17
| 940 | 1.149 | 2.343 | 3.659 | Feb | 9 | 7 | 2.556 | Sep | 11 | 14
| 950 | 0 | 0.618 | 0 |  |  |  | 2.054 | Sep | 11 | 14
| 960 | 2.771 | 0.909 | 2.085 | Jan | 1 | 0 | 1.367 | Jun | 26 | 16
| 980 | 0.266 | 3.758 | 1.382 | Feb | 9 | 5 | 2.93 | Oct | 18 | 14
| 985 | 2.279 | 5.88 | 2.458 | Feb | 9 | 5 | 3.208 | Oct | 11 | 14
| 995 | 0.77 | 6.771 | 1.462 | Feb | 9 | 5 | 3.315 | Jan | 22 | 14
| 195 | 4.157 | 0.628 | 1.799 | Jan | 1 | 0 | 0.973 | Jun | 26 | 16
| 200 | 5.226 | 0.835 | 2.308 | Jan | 1 | 0 | 1.239 | Jun | 26 | 16
| 210 | 6.531 | 0.496 | 2.605 | Jan | 1 | 0 | 0.937 | Jun | 26 | 16
| 215 | 5.697 | 0.922 | 2.52 | Jan | 1 | 0 | 1.386 | Jun | 26 | 16
| 220 | 7.178 | 0.55 | 2.863 | Jan | 1 | 0 | 1.04 | Jun | 26 | 16
| 230 | 10.417 | 0.929 | 4.223 | Jan | 1 | 0 | 1.734 | Jun | 26 | 16
| 240 | 5.944 | 0.876 | 2.685 | Jan | 1 | 0 | 1.218 | Jun | 26 | 16
| 250 | 5.373 | 3.471 | 2.855 | Jan | 1 | 0 | 2.751 | Sep | 3 | 14
| 270 | 4.273 | 6.698 | 2.56 | Jan | 1 | 1 | 5.832 | Jan | 22 | 14
| 280 | 4.619 | 4.215 | 2.568 | Jan | 1 | 1 | 3.768 | Dec | 1 | 13
| 290 | 4.381 | 5.31 | 2.561 | Jan | 1 | 1 | 5.739 | Jan | 22 | 14
| 300 | 4.46 | 4.805 | 2.589 | Jan | 1 | 0 | 3.695 | Jun | 26 | 17
| 310 | 4.846 | 3.402 | 2.592 | Jan | 1 | 0 | 3.252 | Jun | 26 | 17
| 320 | 3.599 | 4.42 | 2.546 | Jan | 1 | 1 | 5.304 | Jan | 22 | 14
| 395 | 5.145 | 0.006 | 2.085 | Jan | 1 | 1 | 0.308 | Jun | 14 | 16
| 400 | 7.047 | 0.017 | 2.863 | Jan | 1 | 0 | 0.457 | Jun | 26 | 17
| 410 | 8.661 | 0.041 | 3.543 | Jan | 1 | 0 | 0.709 | Jun | 26 | 16
| 420 | 7.433 | 0.119 | 3.365 | Jan | 1 | 0 | 0.917 | Jun | 26 | 16
| 430 | 5.954 | 0.944 | 3.36 | Jan | 1 | 0 | 1.84 | Jun | 26 | 15
| 440 | 4.33 | 3.458 | 3.06 | Jan | 1 | 0 | 3.766 | Oct | 11 | 13
| 450 | 3.375 | 6.161 | 2.753 | Jan | 1 | 0 | 6.063 | Jan | 22 | 13
| 460 | 3.873 | 5.929 | 2.98 | Jan | 1 | 0 | 5.902 | Jan | 22 | 13
| 470 | 3.54 | 5.649 | 2.807 | Jan | 1 | 0 | 5.57 | Jan | 22 | 14
| 800 | 5.403 | 0.362 | 2.864 | Feb | 9 | 5 | 1.157 | Aug | 5 | 14
| 810 | 2.454 | 1.357 | 2.512 | Feb | 9 | 5 | 1.94 | Sep | 11 | 14
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 25.26 | -13.52 | Feb | 9 | 6 | 65 | Oct | 11 | 15
| 900FF | 25.25 | 1.31 | Feb | 9 | 7 | 44.46 | Sep | 11 | 15
| 650FF | 18.04 | -17.37 | Dec | 30 | 23 | 62.59 | Oct | 11 | 15
| 950FF | 14.35 | -13.36 | Dec | 30 | 23 | 36.37 | Sep | 11 | 15
| 680FF | 33.3 | -6.89 | Feb | 9 | 7 | 74.97 | Oct | 12 | 15
| 980FF | 33.3 | 12.4 | Nov | 5 | 6 | 52.81 | Oct | 21 | 14
| 960 | 29.45 | 6.74 | Feb | 9 | 6 | 53.18 | Oct | 20 | 14
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1667.158
| NORTH | 477.31
| EAST | 1016.676
| SOUTH | 1290.593
| WEST | 905.722
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 805.046
| 660/South | 506.461
| 670/South | 994.318
| 620/West | 569.394
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 663.345
| 630/West | 399.173
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.9 | -46.85 | Dec | 31 | 23 | 24.62 | Aug | 4 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 672.684 | 417.93 | 3.036 | 1 | 0 | 5.422 | 22 | 14 | 275.307 | 33.493 | 2.178 | 1 | 4 | 1.637 | 22 | 15
| Feb | 635.299 | 315.415 | 2.922 | 9 | 5 | 4.444 | 15 | 14 | 292.916 | 4.724 | 2.453 | 9 | 5 | 0.588 | 15 | 15
| Mar | 450.494 | 410.736 | 2.065 | 17 | 5 | 4.252 | 9 | 14 | 119.976 | 40.898 | 1.646 | 17 | 5 | 1.143 | 10 | 14
| Apr | 447.957 | 230.168 | 2.238 | 11 | 5 | 3.6 | 7 | 14 | 214.166 | 18.267 | 1.725 | 3 | 3 | 1.032 | 8 | 14
| May | 128 | 338.582 | 1.569 | 1 | 4 | 2.894 | 10 | 14 | 26.771 | 128.592 | 1.124 | 1 | 5 | 1.446 | 11 | 14
| Jun | 11.218 | 526.439 | 0.748 | 9 | 4 | 3.067 | 14 | 14 | 0 | 408.473 |  |  |  | 1.873 | 14 | 14
| Jul | 10.105 | 525.149 | 0.512 | 26 | 4 | 3.155 | 29 | 13 | 0 | 408.145 |  |  |  | 1.83 | 17 | 14
| Aug | 8.376 | 621.101 | 0.532 | 17 | 5 | 4.038 | 29 | 13 | 0 | 510.152 |  |  |  | 2.212 | 29 | 14
| Sep | 76.741 | 672.084 | 1.114 | 29 | 2 | 4.911 | 30 | 13 | 0 | 466.106 |  |  |  | 2.556 | 11 | 14
| Oct | 324.148 | 611.126 | 1.619 | 9 | 5 | 5.278 | 10 | 13 | 63.591 | 269.566 | 1.158 | 7 | 6 | 2.549 | 12 | 14
| Nov | 585.805 | 377.147 | 2.931 | 26 | 7 | 5.229 | 29 | 13 | 283.888 | 56.214 | 2.201 | 26 | 7 | 1.683 | 20 | 14
| Dec | 697.819 | 386.209 | 2.972 | 31 | 23 | 5.294 | 1 | 13 | 314.279 | 38.054 | 1.981 | 9 | 6 | 1.595 | 2 | 14
| Total | 4048.646 | 5432.086 | [6 empty] | 1590.894 | 2382.684
| Max |  |  | 3.036 |  |  | 5.422 |  |  |  |  | 2.453 |  |  | 2.556
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -30.28 | 3.69 | 0.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -27.46 | 4.42 | 0.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -33.84 | 3.89 | -1.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -37.57 | 3.67 | -2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 1.17 | 0.7 | 0.7 | -35.02 | 3.66 | -4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 0.28 | 0.54
| 6 | 15 | 9 | 9 | 82.05 | 20.5 | 20.5 | -35.99 | 3.8 | -1.78 | 0 | 0 | 0 | 5.49 | 3.54 | 6.93 | 12.51 | 8.07 | 15.8
| 7 | 60 | 36 | 36 | 273.2 | 46 | 46 | -38.7 | 4.32 | 0.21 | 0 | 0 | 0 | 21.96 | 14.16 | 27.74 | 28.06 | 18.1 | 35.45
| 8 | 111 | 66.6 | 66.6 | 477.91 | 73.4 | 73.4 | -35.42 | 4.39 | 1.2 | 62.99 | 41.95 | 81.98 | 40.63 | 26.2 | 51.32 | 44.78 | 28.88 | 56.56
| 9 | 158 | 94.8 | 94.8 | 668 | 164.1 | 98.8 | -36.87 | 4.91 | 2.28 | 321.42 | 200.8 | 394.31 | 57.83 | 37.3 | 73.05 | 64.53 | 43.25 | 86.7
| 10 | 195 | 117 | 117 | 827 | 294.38 | 119.2 | -36.1 | 6.2 | 5.06 | 491.87 | 297.08 | 584.9 | 71.37 | 46.03 | 90.15 | 113.53 | 82.86 | 164.26
| 11 | 263 | 157.8 | 157.8 | 941 | 390.75 | 133.6 | -34.56 | 6.98 | 5.41 | 608.92 | 362.95 | 714.8 | 96.26 | 62.09 | 121.59 | 172.34 | 124.7 | 244.33
| 12 | 278 | 166.8 | 166.8 | 1003 | 443.74 | 141.3 | -33.68 | 6.26 | 5.11 | 673.56 | 399.66 | 786.82 | 101.75 | 65.63 | 128.53 | 211.22 | 149.98 | 293.03
| 13 | 277 | 166.2 | 166.2 | 1008 | 448.17 | 238.46 | -31.67 | 4.19 | 5.57 | 684.62 | 405.96 | 799.14 | 101.39 | 65.39 | 128.06 | 214.69 | 152.17 | 297.25
| 14 | 259 | 155.4 | 155.4 | 955 | 403.38 | 460.58 | -33.24 | 3.18 | 4.99 | 641 | 381.03 | 750.28 | 94.8 | 61.14 | 119.74 | 181.43 | 130.74 | 255.91
| 15 | 227 | 136.2 | 136.2 | 848 | 314 | 644.63 | -33.22 | 1.92 | 6.01 | 543.97 | 326.05 | 642.14 | 83.09 | 53.59 | 104.95 | 124.33 | 90.97 | 179.73
| 16 | 181 | 108.6 | 108.6 | 696 | 189.16 | 771.27 | -33.5 | 1.15 | 5.46 | 395.66 | 242.52 | 477 | 66.25 | 42.73 | 83.68 | 70.83 | 48.68 | 97.78
| 17 | 104 | 62.4 | 62.4 | 509 | 77.4 | 818.34 | -34.04 | 3.3 | 6.54 | 184.45 | 119.32 | 233.64 | 38.07 | 24.55 | 48.08 | 47.22 | 30.45 | 59.64
| 18 | 53 | 31.8 | 31.8 | 304.41 | 50.1 | 758.2 | -36.35 | 3.3 | 5.67 | 4.82 | 3.3 | 6.44 | 19.4 | 12.51 | 24.5 | 30.56 | 19.71 | 38.6
| 19 | 11 | 6.6 | 6.6 | 110.72 | 23.9 | 525.64 | -36.47 | 2.5 | 5.19 | 0 | 0 | 0 | 4.03 | 2.6 | 5.09 | 14.58 | 9.4 | 18.42
| 20 | 0 | 0 | 0 | 3.65 | 2 | 19.69 | -36.91 | 2 | 5.72 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 0.79 | 1.54
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.97 | 2.01 | 2.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.91 | 1.83 | 2.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.96 | 0.95 | 1.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.52 | 0.95 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 1.9869 | 0.025 | 1.835 | 2.545 | 1.044 | 2.033 | 1.202 | 1.0685 | 0 | 0 | 1.1713 | 0.40804 | 0 | 0 | 0 | 0 | 0 | -0.139 | -0.11986 | -0.28999 | -0.70663 | -0.6563 | 10 | 15.59
| 2 | 2.0692 | 0.611 | 1.901 | 2.631 | 1.154 | 2.096 | 1.253 | 1.1715 | 0 | 0 | 1.266 | 0.48876 | 0 | 0 | 0 | 0 | 0.078 | -0.074 | -0.038655 | -0.22559 | -0.62235 | -0.5916 | 10 | 15.02
| 3 | 2.1291 | 0.951 | 1.95 | 2.707 | 1.232 | 2.145 | 1.293 | 1.2675 | 0 | 0 | 1.3543 | 0.56563 | 0 | 0 | 0 | 0 | 0.158 | -0.009 | 0 | -0.15164 | -0.52812 | -0.5172 | 10 | 14.48
| 4 | 2.2065 | 1.19 | 2.017 | 2.81 | 1.301 | 2.216 | 1.34 | 1.3715 | 0 | 0 | 1.4513 | 0.64603 | 0 | 0 | 0.131 | 0 | 0.244 | 0.053 | 0 | -0.07752 | -0.43146 | -0.4428 | 10 | 13.9
| 5 | 2.243 | 1.321 | 2.048 | 2.851 | 1.332 | 2.249 | 1.356 | 1.4399 | 0 | 0 | 1.5133 | 0.69388 | 0 | 0 | 0.363 | 0 | 0.332 | 0.115 | 0 | -0.00322 | -0.33373 | -0.3681 | 10 | 13.43
| 6 | 2.2675 | 1.402 | 2.071 | 2.88 | 1.366 | 2.271 | 1.381 | 1.5162 | 0 | 0 | 1.5837 | 0.75613 | 0 | 0 | 0.33 | 0 | 0.247 | 0.057 | 0 | -0.03011 | -0.34526 | -0.3947 | 10 | 12.92
| 7 | 2.2778 | 1.445 | 2.078 | 2.899 | 1.375 | 2.28 | 1.385 | 1.5722 | 0 | 0.018134 | 1.6344 | 0.79633 | 0 | 0 | 0.012 | 0 | -0.069 | -0.106 | 0 | -0.10082 | -0.43216 | -0.4652 | 10 | 12.47
| 8 | 2.1196 | 3.844 | 1.966 | 2.693 | 1.238 | 2.121 | 1.243 | 1.5519 | 2.4441 | 0.047822 | 1.6091 | 0.76451 | 0 | 0 | 0 | 0 | -0.457 | -0.331 | 0 | -0.18766 | -0.56288 | -0.5517 | 20 | 20
| 9 | 1.2032 | 2.167 | 1.334 | 1.593 | 0.416 | 1.204 | 0.42 | 1.1996 | 1.9321 | 0 | 1.2523 | 0.41712 | 0 | 0 | 0 | 0 | -0.861 | -0.603 | -0.11228 | -0.30235 | -0.73174 | -0.6662 | 20 | 20
| 10 | 0 | 0.159 | 0.264 | 0 | 0 | -0.399 | -1.046 | 0.58712 | 1.2397 | 0 | 0.63558 | -0.16807 | -0.0988 | 0 | -0.047 | -0.168 | -1.365 | -0.989 | -0.36477 | -0.4882 | -0.97482 | -0.8518 | 20 | 20
| 11 | -0.3574 | 0 | 0 | -0.306 | -1.145 | -2.012 | -2.585 | 0 | 0.51559 | 0 | -0.03353 | -0.79694 | -1.022 | -0.775 | -1.187 | -0.86 | -1.979 | -1.499 | -0.66069 | -0.72195 | -1.2648 | -1.0853 | 26.64 | 20
| 12 | -2.2142 | -1.927 | -0.147 | -2.277 | -2.926 | -3.385 | -3.941 | 0 | 0 | 0 | -0.67357 | -1.3983 | -1.7729 | -1.407 | -2.107 | -1.497 | -2.56 | -2.03 | -0.94273 | -0.9537 | -1.5421 | -1.3168 | 27 | 20.54
| 13 | -3.4723 | -3.305 | -1.232 | -3.608 | -4.197 | -4.382 | -4.962 | 0 | 0 | -0.5694 | -1.2303 | -1.9247 | -2.3147 | -1.85 | -2.761 | -2.001 | -3.004 | -2.469 | -1.1934 | -1.1675 | -1.7885 | -1.5304 | 27 | 22.49
| 14 | -4.0214 | -3.923 | -1.705 | -4.154 | -4.805 | -4.783 | -5.418 | 0 | 0 | -0.92744 | -1.5163 | -2.1968 | -2.5989 | -2.099 | -3.092 | -2.264 | -3.231 | -2.692 | -1.3604 | -1.3074 | -1.9516 | -1.6701 | 27 | 23.74
| 15 | -4.0239 | -3.966 | -1.796 | -4.118 | -4.909 | -4.698 | -5.427 | 0 | 0 | -1.173 | -1.6801 | -2.3715 | -2.594 | -2.135 | -3.061 | -2.242 | -3.192 | -2.645 | -1.413 | -1.3421 | -2.0008 | -1.7047 | 27 | 24.64
| 16 | -3.4753 | -3.441 | -1.52 | -3.498 | -4.446 | -4.099 | -4.905 | 0 | 0 | -1.2114 | -1.6411 | -2.3468 | -2.3269 | -1.953 | -2.681 | -1.981 | -2.905 | -2.368 | -1.3583 | -1.2783 | -1.9428 | -1.6406 | 27 | 24.91
| 17 | -2.3221 | -2.302 | -0.843 | -2.216 | -3.389 | -2.915 | -3.811 | 0 | 0 | -1.0054 | -1.3568 | -2.0834 | -1.9515 | -1.664 | -2.156 | -1.642 | -2.518 | -2.019 | -1.2639 | -1.1854 | -1.8455 | -1.5477 | 27 | 24.35
| 18 | -0.6489 | -0.637 | 0 | -0.314 | -1.841 | -1.224 | -2.24 | 0 | 0 | -0.56114 | -0.83413 | -1.5865 | -1.5665 | -1.354 | -1.647 | -1.311 | -2.126 | -1.681 | -1.1433 | -1.0758 | -1.7221 | -1.4379 | 27 | 22.94
| 19 | 0 | 0 | 0 | 0 | -0.479 | 0.257 | -0.863 | 0 | 0 | -0.19504 | -0.3958 | -1.1719 | -1.1763 | -1.034 | -1.164 | -1.003 | -1.731 | -1.37 | -1.0072 | -0.96104 | -1.5836 | -1.3231 | 23.73 | 21.65
| 20 | 0.1486 | 0.155 | 0.486 | 0.909 | 0 | 1.116 | -0.003 | 0 | 0 | 0 | -0.11193 | -0.90379 | -0.7328 | -0.657 | -0.649 | -0.694 | -1.285 | -1.058 | -0.84822 | -0.82628 | -1.4224 | -1.1882 | 20 | 20.76
| 21 | 1.0979 | 1.102 | 1.198 | 1.818 | 0 | 1.645 | 0.556 | 0 | 0.01799 | 0 | 0.13546 | -0.6734 | -0.2983 | -0.275 | -0.157 | -0.415 | -0.849 | -0.778 | -0.70104 | -0.70182 | -1.2731 | -1.0637 | 20 | 20
| 22 | 1.6738 | 1.676 | 1.641 | 2.378 | 0 | 1.993 | 0.926 | 0 | 0.26925 | 0 | 0.36388 | -0.46555 | -0.0186 | -0.028 | 0 | -0.215 | -0.569 | -0.577 | -0.59136 | -0.61213 | -1.1615 | -0.9739 | 20 | 20
| 23 | 2.0148 | 2.016 | 1.904 | 2.707 | 0.516 | 2.203 | 1.153 | 0.040877 | 0.46845 | 0 | 0.55162 | -0.2987 | 0 | 0 | 0 | -0.064 | -0.383 | -0.425 | -0.48628 | -0.52449 | -1.0547 | -0.8862 | 20 | 20
| 24 | 2.1963 | 0 | 2.043 | 2.874 | 0.89 | 2.307 | 1.283 | 0.24467 | 0 | 0 | 0.70288 | -0.16436 | 0 | 0 | 0 | 0 | -0.228 | -0.297 | -0.37086 | -0.42934 | -0.93767 | -0.791 | 11.34 | 18.01
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 4.4672 | 11.7017 | 19.6725 | 20.9717 | 16.0238 | 24.2654
| 2 | 2.8568 | 11.245 | 18.88 | 20.4879 | 14.3021 | 23.841
| 3 | 1.4091 | 10.7932 | 17.7669 | 19.6293 | 12.6782 | 23.4157
| 4 | -0.016476 | 10.3008 | 16.6508 | 18.7479 | 11.0975 | 22.967
| 5 | -1.2245 | 9.9029 | 15.4711 | 17.7906 | 9.689 | 22.6075
| 6 | -2.2862 | 9.4738 | 17.1247 | 19.3484 | 8.334 | 22.1993
| 7 | -3.193 | 9.0975 | 19.397 | 21.0886 | 7.1316 | 21.8506
| 8 | -3.3337 | 8.9582 | 20.5125 | 23.1543 | 6.5882 | 21.7274
| 9 | -0.19628 | 9.8876 | 22.8099 | 23.8657 | 8.9979 | 22.6222
| 10 | 6.8013 | 11.7551 | 25.8855 | 24.7959 | 15.0347 | 24.3831
| 11 | 15.6352 | 13.9547 | 29.838 | 25.9168 | 23.1553 | 26.4423
| 12 | 25.0661 | 16.2133 | 34.1747 | 27.0556 | 32.2721 | 28.5594
| 13 | 34.0622 | 18.3357 | 38.3724 | 28.1472 | 41.4162 | 30.5625
| 14 | 41.1697 | 19.6982 | 41.8987 | 29.0149 | 49.1534 | 31.8566
| 15 | 46.07 | 20.6912 | 44.2829 | 29.5372 | 55.1901 | 32.861
| 16 | 48.1263 | 21.0435 | 45.2962 | 29.7074 | 58.6456 | 33.2429
| 17 | 46.582 | 20.5729 | 45.2885 | 29.7175 | 58.7506 | 32.828
| 18 | 41.232 | 19.2453 | 44.6098 | 29.6094 | 55.2721 | 31.5769
| 19 | 34.5581 | 18.0354 | 33.257 | 28.4499 | 50.4057 | 30.4417
| 20 | 28.7453 | 17.2201 | 30.0661 | 26.9749 | 45.8603 | 29.6795
| 21 | 23.5942 | 16.476 | 27.4122 | 25.7654 | 41.5737 | 28.995
| 22 | 18.976 | 15.7483 | 25.8257 | 25.2338 | 37.5376 | 28.3418
| 23 | 14.9392 | 15.107 | 24.2308 | 24.4091 | 33.8308 | 27.7806
| 24 | 11.505 | 14.5494 | 22.4527 | 23.2527 | 30.4633 | 27.2948
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 3
| 2 | 8
| 3 | 19
| 4 | 32
| 5 | 31
| 6 | 42
| 7 | 60
| 8 | 110
| 9 | 95
| 10 | 112
| 11 | 155
| 12 | 190
| 13 | 230
| 14 | 229
| 15 | 244
| 16 | 291
| 17 | 297
| 18 | 334
| 19 | 337
| 20 | 313
| 21 | 324
| 22 | 267
| 23 | 253
| 24 | 252
| 25 | 241
| 26 | 254
| 27 | 241
| 28 | 264
| 29 | 297
| 30 | 298
| 31 | 331
| 32 | 377
| 33 | 384
| 34 | 411
| 35 | 363
| 36 | 315
| 37 | 255
| 38 | 208
| 39 | 132
| 40 | 75
| 41 | 45
| 42 | 24
| 43 | 12
| 44 | 5
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## EnergyPlus
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
[Note to Participants: Editorial changes: went with Hour 8 as example and 0n00 format (pertinent to Jan2018 discussion re Case 640)]
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracikng colors are:
Red is for edits from June 2013 through September 2017 distribution for the Round 3 sim trial draft.
Blue is for edits since Sep 2017 (since Sec5-2Aout-082917.xlsx):
editorial (not substantive) clarification re "hourly integrated".
| Software: | EnergyPlus | EnergyPlus
| Version: |  | Version 9.0.1
| Date of Results: |  | 2018-10-19
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.3244 | 6.027 | 3.2044 | Dec | 31 | 24 | 6.3516 | Jan | 22 | 14
| 610 | 4.3748 | 4.3328 | 3.1918 | Dec | 31 | 24 | 6.1345 | Dec | 1 | 14
| 620 | 4.4851 | 4.0595 | 3.2291 | Dec | 31 | 24 | 4.7974 | Jun | 26 | 17
| 630 | 4.7835 | 2.836 | 3.2066 | Dec | 31 | 24 | 4.2122 | Jun | 26 | 17
| 640 | 2.6618 | 5.7631 | 4.5585 | Nov | 26 | 8 | 6.2974 | Jan | 22 | 14
| 650 | 0 | 4.8168 | 0 | Jan | 1 | 1 | 6.1381 | Oct | 18 | 14
| 660 | 3.7067 | 3.2315 | 2.8311 | Dec | 31 | 24 | 3.7703 | Oct | 18 | 14
| 670 | 5.6161 | 6.6227 | 3.8535 | Nov | 26 | 7 | 6.8062 | Jan | 22 | 14
| 680 | 2.1797 | 6.4439 | 2.0524 | Nov | 26 | 7 | 6.7702 | Jan | 22 | 14
| 685 | 4.8771 | 9.1188 | 3.2232 | Dec | 31 | 24 | 7.1068 | Jan | 22 | 14
| 695 | 2.8019 | 9.1716 | 2.0718 | Dec | 31 | 24 | 7.3343 | Jan | 22 | 14
| 900 | 1.6637 | 2.4887 | 2.6875 | Feb | 9 | 6 | 3.0404 | Oct | 1 | 14
| 910 | 1.9557 | 1.3835 | 2.6989 | Feb | 9 | 6 | 2.2221 | Oct | 18 | 15
| 920 | 3.3365 | 2.7308 | 2.7702 | Feb | 9 | 6 | 3.2603 | Jun | 26 | 18
| 930 | 3.9938 | 1.9191 | 2.7849 | Feb | 9 | 6 | 2.7815 | Jun | 26 | 18
| 940 | 1.0674 | 2.4244 | 3.1428 | Dec | 31 | 9 | 3.04 | Oct | 1 | 14
| 950 | 0 | 0.70692 | 0 | Jan | 1 | 1 | 2.3875 | Sep | 11 | 15
| 960 | 2.689 | 0.90712 | 2.2594 | Feb | 9 | 6 | 1.4799 | Jun | 26 | 17
| 980 | 0.41094 | 3.7118 | 1.5378 | Feb | 9 | 6 | 3.4501 | Oct | 18 | 15
| 985 | 2.3693 | 6.3592 | 2.6954 | Feb | 9 | 6 | 3.9148 | Oct | 18 | 15
| 995 | 1.0065 | 7.2029 | 1.6221 | Feb | 9 | 6 | 4.1774 | Jan | 22 | 15
| 195 | 4.0696 | 0.61152 | 1.7944 | Dec | 31 | 24 | 1.041 | Jun | 26 | 17
| 200 | 5.1054 | 0.81408 | 2.3413 | Nov | 26 | 8 | 1.3075 | Jun | 26 | 17
| 210 | 6.0466 | 0.5599 | 2.5646 | Dec | 31 | 24 | 1.0844 | Jun | 26 | 17
| 215 | 5.4054 | 0.87747 | 2.4778 | Nov | 26 | 8 | 1.4004 | Jun | 26 | 17
| 220 | 6.4551 | 0.6099 | 2.692 | Dec | 31 | 24 | 1.1845 | Jun | 26 | 18
| 230 | 9.9299 | 0.99121 | 4.3161 | Dec | 31 | 24 | 1.8409 | Jun | 26 | 17
| 240 | 5.2794 | 0.97875 | 2.5071 | Dec | 31 | 24 | 1.3659 | Jun | 26 | 18
| 250 | 4.8991 | 3.1816 | 2.6874 | Dec | 31 | 24 | 2.8666 | Sep | 12 | 14
| 270 | 4.3854 | 7.5215 | 2.5966 | Dec | 31 | 24 | 6.8388 | Jan | 22 | 14
| 280 | 4.5701 | 5.1829 | 2.602 | Dec | 31 | 24 | 4.7272 | Jan | 22 | 14
| 290 | 4.4244 | 5.7425 | 2.5834 | Dec | 31 | 24 | 6.5946 | Jan | 22 | 14
| 300 | 4.4245 | 5.152 | 2.6031 | Dec | 31 | 24 | 4.4755 | Jun | 26 | 17
| 310 | 4.6912 | 3.6695 | 2.5801 | Dec | 31 | 24 | 3.9695 | Jun | 26 | 18
| 320 | 3.7712 | 4.986 | 2.5735 | Dec | 31 | 24 | 6.2091 | Jan | 22 | 14
| 395 | 4.6412 | 0.01038 | 1.9517 | Dec | 31 | 24 | 0.37747 | Jun | 26 | 19
| 400 | 6.3478 | 0.030566 | 2.692 | Dec | 31 | 24 | 0.60691 | Jun | 26 | 18
| 410 | 8.0803 | 0.057269 | 3.504 | Dec | 31 | 24 | 0.82785 | Jun | 26 | 18
| 420 | 6.9058 | 0.15257 | 3.3191 | Dec | 31 | 24 | 1.0325 | Jun | 26 | 18
| 430 | 5.6201 | 0.85562 | 3.3163 | Dec | 31 | 24 | 1.9294 | Jun | 26 | 16
| 440 | 4.5001 | 4.085 | 3.2187 | Dec | 31 | 24 | 4.686 | Oct | 18 | 14
| 450 | 3.9625 | 6.5073 | 3.0998 | Dec | 31 | 24 | 6.4663 | Jan | 22 | 14
| 460 | 4.1938 | 6.4746 | 3.0911 | Dec | 31 | 24 | 6.3742 | Jan | 22 | 14
| 470 | 4.0939 | 6.0294 | 3.2067 | Dec | 31 | 24 | 6.4436 | Jan | 22 | 14
| 800 | 5.1156 | 0.37353 | 2.9237 | Feb | 9 | 6 | 1.0458 | Jun | 26 | 16
| 810 | 2.3418 | 1.5078 | 2.749 | Feb | 9 | 6 | 2.2702 | Sep | 11 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 24.9173 | -12.5613 | Feb | 9 | 7 | 63.8408 | Oct | 18 | 16
| 900FF | 25.1213 | 1.2424 | Feb | 9 | 7 | 44.2922 | Sep | 12 | 15
| 650FF | 18.4195 | -17.0758 | Dec | 31 | 24 | 62.469 | Oct | 18 | 16
| 950FF | 14.789 | -12.8122 | Feb | 9 | 7 | 36.6805 | Sep | 11 | 16
| 680FF | 30.9584 | -7.0523 | Feb | 9 | 7 | 70.1447 | Jan | 22 | 16
| 980FF | 31.1618 | 9.917 | Nov | 4 | 7 | 49.6221 | Sep | 12 | 16
| 960 | 27.7427 | 5.0931 | Feb | 9 | 7 | 49.8773 | Oct | 12 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1664.3425
| NORTH | 438.241
| EAST | 1062.1572
| SOUTH | 1370.4819
| WEST | 967.278
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 804.0205
| 660/South | 435.995
| 670/South | 1024.2026
| 620/West | 581.0395
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 646.1319
| 630/West | 419.3545
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour | [15 empty] | min date | max date
| 600 | -2.0216 | -37.9798 | Dec | 31 | 24 | 24.7268 | Aug | 4 | 16 | [15 empty] | 12/31 24:00:00 | 08/04 16:00:00
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900 | [12 empty] | Case 600 |  |  |  | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling | [10 empty] | Peak Heat |  | Peak Cooling |  | Peak Heat | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour | [8 empty] | date |  |  | date | date |  | date
| Jan | 711.8797 | 521.798 | 2.9776 | 1 | 3 | 6.3516 | 22 | 14 | 255.8355 | 53.2805 | 1.9028 | 29 | 7 | 2.0779 | 22 | 15 | [8 empty] | 01/01 03:00:00 |  |  | 01/22 14:00:00 | 01/29 07:00:00 |  | 01/22 15:00:00
| Feb | 682.632 | 387.4981 | 3.0666 | 9 | 6 | 5.5373 | 2 | 14 | 294.1814 | 12.3391 | 2.6875 | 9 | 6 | 0.97943 | 15 | 15 | [8 empty] | 02/09 06:00:00 |  |  | 02/02 14:00:00 | 02/09 06:00:00 |  | 02/15 15:00:00
| Mar | 472.2167 | 484.3611 | 2.1146 | 17 | 6 | 5.0085 | 9 | 14 | 125.5424 | 65.3862 | 1.7443 | 17 | 6 | 1.4931 | 11 | 14 | [8 empty] | 03/17 06:00:00 |  |  | 03/09 14:00:00 | 03/17 06:00:00 |  | 03/11 14:00:00
| Apr | 510.1244 | 240.4611 | 2.3223 | 11 | 5 | 3.9307 | 12 | 14 | 268.6543 | 18.4694 | 2.0036 | 3 | 4 | 0.95262 | 7 | 15 | [8 empty] | 04/11 05:00:00 |  |  | 04/12 14:00:00 | 04/03 04:00:00 |  | 04/07 15:00:00
| May | 136.8192 | 339.9139 | 1.6241 | 1 | 5 | 3.0864 | 10 | 13 | 33.4139 | 114.4874 | 1.2682 | 1 | 5 | 1.5339 | 11 | 14 | [8 empty] | 05/01 05:00:00 |  |  | 05/10 13:00:00 | 05/01 05:00:00 |  | 05/11 14:00:00
| Jun | 10.0812 | 539.605 | 0.73243 | 9 | 5 | 3.4487 | 13 | 13 | 0 | 401.3344 | 0 | 1 | 1 | 1.9656 | 14 | 14 | [8 empty] | 06/09 05:00:00 |  |  | 06/13 13:00:00 | 06/01 01:00:00 |  | 06/14 14:00:00
| Jul | 12.0182 | 536.3834 | 0.51445 | 26 | 5 | 3.6284 | 17 | 14 | 0 | 398.7064 | 0 | 1 | 1 | 2.0681 | 17 | 15 | [8 empty] | 07/26 05:00:00 |  |  | 07/17 14:00:00 | 07/01 01:00:00 |  | 07/17 15:00:00
| Aug | 6.5877 | 648.5013 | 0.47852 | 17 | 6 | 4.672 | 26 | 14 | 0 | 510.3174 | 0 | 1 | 1 | 2.5258 | 29 | 15 | [8 empty] | 08/17 06:00:00 |  |  | 08/26 14:00:00 | 08/01 01:00:00 |  | 08/29 15:00:00
| Sep | 73.317 | 733.708 | 1.1295 | 28 | 24 | 5.7148 | 30 | 13 | 0.11241 | 492.837 | 0.064157 | 29 | 7 | 2.9888 | 11 | 15 | [8 empty] | 09/28 24:00:00 |  |  | 09/30 13:00:00 | 09/29 07:00:00 |  | 09/11 15:00:00
| Oct | 347.7084 | 675.2687 | 1.682 | 15 | 5 | 6.2221 | 18 | 14 | 81.0905 | 292.6655 | 1.3258 | 7 | 7 | 3.0404 | 1 | 14 | [8 empty] | 10/15 05:00:00 |  |  | 10/18 14:00:00 | 10/07 07:00:00 |  | 10/01 14:00:00
| Nov | 625.2596 | 437.6814 | 3.1061 | 26 | 7 | 6.194 | 28 | 13 | 296.9874 | 67.9828 | 2.3161 | 26 | 7 | 2.0018 | 20 | 15 | [8 empty] | 11/26 07:00:00 |  |  | 11/28 13:00:00 | 11/26 07:00:00 |  | 11/20 15:00:00
| Dec | 735.7303 | 481.8594 | 3.2044 | 31 | 24 | 6.251 | 1 | 14 | 307.8688 | 60.9353 | 2.1749 | 31 | 7 | 1.9682 | 2 | 15 | [8 empty] | 12/31 24:00:00 |  |  | 12/01 14:00:00 | 12/31 07:00:00 |  | 12/02 15:00:00
| Total | 4324.3743 | 6027.0394 | [6 empty] | 1663.6867 | 2488.7414
| Max |  |  | 3.2044 |  |  | 6.3516 |  |  |  |  | 2.6875 |  |  | 3.0404
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -22.9659 | -1.17 | 4.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -24.1358 | -1.1879 | 3.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -25.3162 | -1.261 | 2.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -27.1947 | -1.4438 | 1.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 5.6503 | 2.825 | 2.825 | -26.8988 | -1.4438 | 0.74467 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6849 | 0.91674 | 2.1275
| 6 | 21.25 | 10.9831 | 10.9831 | 103.1926 | 27.0562 | 27.0562 | -26.6742 | -1.4438 | 1.7866 | 0 | 0 | 0 | 6.5505 | 3.5641 | 8.271 | 16.1367 | 8.7799 | 20.3752
| 7 | 64.75 | 33.8229 | 33.8229 | 289.8646 | 55.3885 | 55.3885 | -27.3883 | -1.1879 | 4.4173 | 0 | 0 | 0 | 20.1724 | 10.9757 | 25.471 | 33.0345 | 17.9739 | 41.7114
| 8 | 114.5833 | 59.9654 | 59.7762 | 493.4291 | 82.404 | 81.9746 | -26.6041 | -0.87772 | 6.596 | 109.5631 | 58.7036 | 144.9621 | 35.7642 | 19.4591 | 45.1581 | 48.9027 | 26.6079 | 61.7496
| 9 | 160.25 | 84.3926 | 83.0745 | 682.3352 | 179.1211 | 104.1185 | -25.3596 | -0.53267 | 8.3915 | 323.8 | 175.1923 | 408.8652 | 50.3329 | 27.3858 | 63.5536 | 70.5019 | 38.6289 | 96.4962
| 10 | 203.25 | 108.1146 | 104.629 | 837.8445 | 305.7869 | 119.4839 | -24.4946 | 0.6528 | 10.7117 | 484.0809 | 263.0242 | 596.1031 | 64.481 | 35.0837 | 81.4178 | 116.644 | 63.0283 | 170.6848
| 11 | 259.8333 | 139.6057 | 132.0397 | 947.9972 | 396.7139 | 128.2458 | -23.1465 | 1.865 | 12.6113 | 591.9351 | 322.5677 | 720.937 | 83.2627 | 45.3028 | 105.1329 | 169.4457 | 90.4757 | 244.3135
| 12 | 276.5833 | 149.4359 | 140.236 | 1005.2373 | 443.5116 | 131.5461 | -21.7912 | 2.0953 | 13.2726 | 648.7354 | 354.5078 | 786.606 | 89.1256 | 48.4927 | 112.5357 | 201.8158 | 107.4787 | 286.2069
| 13 | 274.0833 | 147.9223 | 142.6342 | 1004.0328 | 442.6572 | 258.9316 | -20.2132 | 0.88422 | 13.895 | 654.8384 | 357.9765 | 793.6699 | 88.2229 | 48.0015 | 111.3958 | 201.2382 | 107.1723 | 285.4691
| 14 | 255.1667 | 136.7123 | 137.7338 | 946.1468 | 394.8902 | 491.6517 | -20.6931 | -0.55214 | 14.3919 | 609.2696 | 332.2657 | 740.9315 | 81.5371 | 44.3638 | 102.9539 | 168.1713 | 89.8075 | 242.6571
| 15 | 222 | 117.6082 | 123.3077 | 835.4779 | 303.1678 | 683.8576 | -21.7664 | -2.0361 | 14.9 | 513.0433 | 278.943 | 629.5384 | 70.1431 | 38.1645 | 88.5672 | 115.2723 | 62.3178 | 168.6678
| 16 | 172 | 90.0007 | 96.8707 | 679.2595 | 175.5288 | 811.9781 | -22.2074 | -1.9974 | 14.7769 | 366.6641 | 198.6673 | 459.3639 | 53.6776 | 29.2057 | 67.7768 | 69.6148 | 38.1416 | 94.9682
| 17 | 101.9167 | 53.2617 | 54.9349 | 489.9716 | 81.5142 | 853.4406 | -22.932 | -1.8299 | 14.4692 | 178.3747 | 95.7857 | 233.5125 | 31.766 | 17.2837 | 40.1098 | 48.6162 | 26.4518 | 61.3859
| 18 | 50.25 | 26.165 | 26.165 | 285.8351 | 54.8088 | 778.077 | -24.6208 | -2.1057 | 13.5976 | 9.7889 | 5.1964 | 13.5578 | 15.6051 | 8.4907 | 19.704 | 32.6887 | 17.7857 | 41.2749
| 19 | 10.5278 | 5.4293 | 5.4293 | 99.0838 | 26.2621 | 527.4004 | -25.9163 | -2.3646 | 12.3123 | 0 | 0 | 0 | 3.2381 | 1.7618 | 4.0886 | 15.6631 | 8.5222 | 19.7772
| 20 | 0 | 0 | 0 | 4.4364 | 2.3496 | 70.2141 | -26.5019 | -2.9405 | 11.5045 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4014 | 0.76247 | 1.7694
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -27.6142 | -3.2197 | 9.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -28.9393 | -3.7455 | 7.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -29.4433 | -4.7857 | 7.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -29.2659 | -5.2605 | 5.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.1523 | 0.082706 | 1.8505 | 2.6246 | 1.2516 | 2.1861 | 1.384 | 0.97734 | 0 | 0 | 1.1316 | 0.50876 | 0 | 0 | 0 | 0 | -0.084479 | -0.15693 | -0.10115 | -0.21575 | -0.71075 | -0.64079 | 10.7291 | 15.6174
| 2 | 2.2223 | 0.54755 | 1.9038 | 2.7315 | 1.3644 | 2.2406 | 1.4443 | 1.0829 | 0 | 0 | 1.2332 | 0.59729 | 0 | 0 | 0 | 0 | -0.025064 | -0.10057 | -0.030142 | -0.15588 | -0.62348 | -0.57552 | 10 | 15.0057
| 3 | 2.2757 | 0.91754 | 1.9434 | 2.8196 | 1.4425 | 2.2855 | 1.4903 | 1.1826 | 0 | 0 | 1.3297 | 0.67434 | 0 | 0 | 0 | 0 | 0.056452 | -0.041091 | 0 | -0.093652 | -0.52735 | -0.5033 | 10 | 14.4319
| 4 | 2.3283 | 1.1473 | 1.9828 | 2.9079 | 1.5049 | 2.3336 | 1.5334 | 1.2862 | 0 | 0.010067 | 1.4277 | 0.74589 | 0 | 0 | 0 | 0 | 0.17529 | 0.017247 | 0 | -0.024143 | -0.42151 | -0.42781 | 10 | 13.8638
| 5 | 2.351 | 1.2747 | 1.9989 | 2.9498 | 1.5323 | 2.3538 | 1.5491 | 1.366 | 0 | 0.11176 | 1.5004 | 0.78604 | 0 | 0 | 0.11574 | 0 | 0.27165 | 0.071385 | 0 | 0 | -0.32772 | -0.35439 | 10 | 13.3569
| 6 | 2.3515 | 1.3397 | 2.0006 | 2.9434 | 1.5467 | 2.353 | 1.5567 | 1.4385 | 0 | 0.22968 | 1.5653 | 0.81681 | 0 | 0 | 0.10059 | 0 | 0.16084 | 0.032137 | 0 | 0 | -0.33274 | -0.37247 | 10 | 12.884
| 7 | 2.3551 | 1.3839 | 2.0091 | 2.9242 | 1.5469 | 2.3559 | 1.5531 | 1.5049 | 0 | 0.32252 | 1.6239 | 0.8414 | 0 | 0 | 0 | 0 | -0.13512 | -0.1231 | 0 | -0.062989 | -0.44088 | -0.46548 | 10 | 12.4205
| 8 | 1.8832 | 3.3808 | 1.7123 | 2.3743 | 1.1609 | 1.8836 | 1.1644 | 1.3243 | 1.2639 | 0.19642 | 1.4296 | 0.68673 | 0 | 0 | 0 | 0 | -0.53511 | -0.38175 | -0.016529 | -0.17091 | -0.59821 | -0.57861 | 15.8147 | 15.9824
| 9 | 0.49397 | 1.7525 | 0.82326 | 0.72924 | 0.15573 | 0.46459 | -0.078065 | 0.79271 | 1.5508 | 0 | 0.87469 | 0.24592 | 0 | 0 | 0 | 0 | -1.0194 | -0.73521 | -0.15912 | -0.30246 | -0.79838 | -0.73081 | 20 | 20
| 10 | 0 | 0.053533 | 0.061784 | 0 | -0.11857 | -1.3367 | -2.0066 | 0.26716 | 0.82256 | 0 | 0.34915 | -0.3633 | -0.35948 | -0.16326 | -0.42413 | -0.32663 | -1.7043 | -1.2892 | -0.41739 | -0.52915 | -1.1091 | -0.98589 | 21.32 | 20
| 11 | -1.3089 | -0.67412 | 0 | -1.2959 | -2.26 | -3.2585 | -3.9354 | 0 | 0.29741 | 0 | -0.25363 | -1.0539 | -1.4584 | -0.88657 | -1.7545 | -1.2062 | -2.5672 | -2.0148 | -0.76505 | -0.82735 | -1.4971 | -1.3035 | 26.4903 | 20
| 12 | -3.4074 | -3.0125 | -0.49567 | -3.5295 | -4.3177 | -4.6823 | -5.3726 | 0 | 0 | -0.11102 | -0.93631 | -1.7987 | -2.4228 | -1.5988 | -2.8853 | -2.0156 | -3.316 | -2.6747 | -1.1012 | -1.0995 | -1.8618 | -1.5915 | 27 | 20.9908
| 13 | -4.6741 | -4.5085 | -1.6957 | -4.9384 | -5.523 | -5.6082 | -6.2586 | 0 | 0 | -0.74762 | -1.6478 | -2.5159 | -2.8449 | -1.9127 | -3.3784 | -2.5062 | -3.614 | -3.0711 | -1.3309 | -1.3165 | -2.1009 | -1.8176 | 27 | 23.1192
| 14 | -4.9334 | -4.868 | -2.1841 | -5.1408 | -5.7122 | -5.7135 | -6.2995 | 0 | 0 | -1.1811 | -2.0379 | -2.8801 | -2.9085 | -2.0065 | -3.4483 | -2.6048 | -3.6138 | -3.1133 | -1.4697 | -1.4417 | -2.2354 | -1.9425 | 27 | 24.6214
| 15 | -4.1722 | -4.1472 | -1.8726 | -4.1667 | -5.0803 | -4.881 | -5.6031 | -0.046329 | 0 | -1.3476 | -2.082 | -2.9303 | -2.641 | -1.9013 | -3.1098 | -2.348 | -3.3078 | -2.8203 | -1.4822 | -1.438 | -2.2319 | -1.9297 | 27 | 25.2509
| 16 | -2.9277 | -2.918 | -1.2021 | -2.7773 | -3.9171 | -3.5937 | -4.3995 | -0.027472 | 0 | -1.2768 | -1.9005 | -2.7431 | -2.2096 | -1.6894 | -2.5271 | -1.8957 | -2.8517 | -2.3445 | -1.399 | -1.33 | -2.1292 | -1.8097 | 27 | 25.2715
| 17 | -1.2391 | -1.2353 | -0.29981 | -0.98623 | -2.2347 | -1.876 | -2.7038 | 0 | 0 | -0.87926 | -1.3981 | -2.2176 | -1.7631 | -1.4112 | -1.9379 | -1.505 | -2.3954 | -1.947 | -1.291 | -1.2236 | -2.0064 | -1.6975 | 27 | 24.483
| 18 | -0.019928 | -0.019589 | 0 | 0 | -0.36295 | 0.036899 | -0.72678 | 0 | 0 | -0.21836 | -0.63216 | -1.4023 | -1.37 | -1.1343 | -1.4631 | -1.1869 | -1.9943 | -1.6239 | -1.1649 | -1.1098 | -1.8639 | -1.5763 | 25.4595 | 22.7901
| 19 | 0.086501 | 0.087045 | 0.10283 | 0.4619 | 0 | 1.1009 | 0.31916 | 0 | 0 | 0 | -0.18634 | -0.925 | -0.98285 | -0.84941 | -1.0152 | -0.87653 | -1.5926 | -1.3044 | -1.0134 | -0.96893 | -1.6925 | -1.4243 | 21.1465 | 21.4689
| 20 | 0.98137 | 0.98216 | 0.84738 | 1.6223 | 0 | 1.6905 | 0.74894 | 0 | 0 | 0 | 0.1006 | -0.60955 | -0.56694 | -0.52226 | -0.55242 | -0.57282 | -1.1479 | -0.98545 | -0.84554 | -0.81412 | -1.5015 | -1.2553 | 20 | 20.5229
| 21 | 1.6393 | 1.6398 | 1.4079 | 2.2179 | 0.26604 | 2.0307 | 1.0411 | 0 | 0.12095 | 0 | 0.33635 | -0.35944 | -0.231 | -0.24015 | -0.17822 | -0.33075 | -0.78159 | -0.73214 | -0.70239 | -0.68625 | -1.3387 | -1.116 | 20 | 20.0026
| 22 | 2.0595 | 2.0598 | 1.7785 | 2.6015 | 0.76843 | 2.2766 | 1.2788 | 0 | 0.38542 | 0 | 0.5638 | -0.13628 | -0.04743 | -0.081429 | -0.0080085 | -0.16755 | -0.5735 | -0.56394 | -0.59073 | -0.59068 | -1.2139 | -1.0144 | 20 | 20
| 23 | 2.3234 | 2.3235 | 2.0051 | 2.8785 | 1.0956 | 2.4412 | 1.4531 | 0.17522 | 0.61003 | 0 | 0.75784 | 0.056384 | 0 | -0.0055834 | 0 | -0.053704 | -0.43593 | -0.44324 | -0.48864 | -0.5056 | -1.0991 | -0.92336 | 20 | 20
| 24 | 2.4352 | 0 | 2.1 | 2.9941 | 1.3198 | 2.4984 | 1.5445 | 0.39699 | 0 | 0 | 0.89065 | 0.19471 | 0 | 0 | 0 | 0 | -0.30738 | -0.3341 | -0.37539 | -0.41088 | -0.97318 | -0.82306 | 12.9018 | 18.0038
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 5.443 | 12.938 | 19.8711 | 21.2303 | 15.3461 | 22.7451
| 2 | 3.8072 | 12.4251 | 19.0627 | 20.7155 | 13.4846 | 22.2438
| 3 | 2.3742 | 11.9298 | 18.14 | 20.0299 | 11.7774 | 21.7632
| 4 | 1.0857 | 11.432 | 17.0158 | 19.1593 | 10.1946 | 21.2816
| 5 | -0.0051534 | 10.9913 | 15.8836 | 18.2535 | 8.775 | 20.8555
| 6 | -0.89643 | 10.5804 | 16.3875 | 18.6317 | 7.5063 | 20.459
| 7 | -1.7104 | 10.1741 | 18.7611 | 20.2686 | 6.3475 | 20.0788
| 8 | -1.4759 | 10.3241 | 20.8898 | 22.8727 | 6.2878 | 20.2516
| 9 | 2.7076 | 11.7504 | 23.2971 | 24.4046 | 10.0373 | 21.6585
| 10 | 9.9288 | 13.8083 | 26.426 | 25.569 | 16.5873 | 23.5492
| 11 | 18.7293 | 15.9577 | 30.6202 | 26.9141 | 24.697 | 25.5857
| 12 | 28.01 | 18.2069 | 35.2192 | 28.1778 | 33.6544 | 27.7875
| 13 | 36.5705 | 20.4419 | 39.1876 | 29.1272 | 42.5122 | 29.9726
| 14 | 43.3942 | 22.0116 | 42.1006 | 29.8598 | 49.7746 | 31.4705
| 15 | 46.9798 | 22.7239 | 44.2085 | 30.2902 | 54.3914 | 32.0838
| 16 | 47.5927 | 22.8195 | 44.886 | 30.4309 | 56.3144 | 32.1996
| 17 | 44.8818 | 22.102 | 44.6042 | 30.4338 | 54.9811 | 31.4583
| 18 | 38.7015 | 20.4887 | 43.7421 | 30.3524 | 50.2114 | 29.8322
| 19 | 32.1639 | 19.2192 | 34.4834 | 29.0273 | 44.9265 | 28.6662
| 20 | 26.2951 | 18.324 | 30.8554 | 27.6463 | 39.9705 | 27.8593
| 21 | 21.5268 | 17.5351 | 27.9576 | 26.3384 | 35.6029 | 27.1608
| 22 | 17.0314 | 16.7569 | 25.9916 | 25.5339 | 31.6493 | 26.4922
| 23 | 13.2781 | 15.9944 | 24.5462 | 24.8642 | 28.034 | 25.8183
| 24 | 10.2079 | 15.3612 | 22.9825 | 23.8852 | 24.8425 | 25.2512
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 4
| 2 | 4
| 3 | 20
| 4 | 21
| 5 | 39
| 6 | 51
| 7 | 63
| 8 | 71
| 9 | 83
| 10 | 128
| 11 | 164
| 12 | 218
| 13 | 185
| 14 | 197
| 15 | 253
| 16 | 269
| 17 | 241
| 18 | 312
| 19 | 321
| 20 | 337
| 21 | 305
| 22 | 324
| 23 | 302
| 24 | 276
| 25 | 296
| 26 | 283
| 27 | 313
| 28 | 302
| 29 | 326
| 30 | 356
| 31 | 386
| 32 | 366
| 33 | 399
| 34 | 374
| 35 | 315
| 36 | 253
| 37 | 209
| 38 | 152
| 39 | 118
| 40 | 64
| 41 | 34
| 42 | 17
| 43 | 7
| 44 | 2
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760
Intermediate calculation cells
DATE
02/11
02/11
02/07
02/11
02/11
02/11
02/11
DATE
07/20
04/23
04/29
10/06
10/06
10/06
10/06
DATE
11/26
12/31
01/22
10/18
01/22
10/18
01/15
DATE
06/27
06/17
07/11
06/02
05/10
09/17
08/01

## ESP-r
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | ESP-r
| Version: | 13.3
| Date of Results: |  | 26th April 2019
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.362 | 6.1618 | 3.228 | Jan | 1 | 1 | 6.193 | Jan | 22 | 14
| 610 | 4.527 | 4.2325 | 3.233 | Jan | 1 | 1 | 5.934 | Jan | 22 | 14
| 620 | 4.5143 | 4.2457 | 3.253 | Jan | 1 | 1 | 4.622 | Jun | 26 | 17
| 630 | 5.0506 | 2.5953 | 3.259 | Jan | 1 | 1 | 3.971 | Jun | 26 | 17
| 640 | 2.6544 | 5.8926 | 4.101 | Nov | 26 | 8 | 6.127 | Jan | 22 | 14
| 650 | 0 | 4.9451 | 0 | Jan | 1 | 1 | 5.961 | Oct | 18 | 14
| 660 | 3.787 | 3.2186 | 2.846 | Jan | 1 | 1 | 3.53 | Oct | 1 | 14
| 670 | 5.975 | 6.5203 | 3.992 | Nov | 26 | 7 | 6.482 | Oct | 18 | 14
| 680 | 2.1321 | 6.5294 | 2.022 | Feb | 9 | 7 | 6.676 | Jan | 22 | 14
| 685 | 4.9035 | 9.1214 | 3.247 | Jan | 1 | 1 | 6.934 | Jan | 22 | 14
| 695 | 2.7321 | 9.149 | 2.025 | Nov | 26 | 7 | 7.239 | Jan | 22 | 14
| 900 | 1.5847 | 2.4877 | 2.633 | Feb | 9 | 7 | 2.896 | Oct | 12 | 15
| 910 | 2.0672 | 1.2829 | 2.684 | Feb | 9 | 7 | 2.212 | Oct | 2 | 15
| 920 | 3.2997 | 2.8144 | 2.706 | Feb | 9 | 7 | 3.099 | Jun | 26 | 18
| 930 | 4.2776 | 1.6538 | 2.765 | Feb | 9 | 6 | 2.494 | Jun | 26 | 18
| 940 | 1.0147 | 2.4276 | 3.122 | Feb | 9 | 9 | 2.891 | Oct | 12 | 15
| 950 | 0 | 0.656 | 0 | Jan | 1 | 1 | 2.202 | Sep | 10 | 15
| 960 | 2.6239 | 0.9496 | 2.201 | Feb | 9 | 6 | 1.403 | Jun | 26 | 17
| 980 | 0.3511 | 3.7745 | 1.473 | Feb | 9 | 7 | 3.341 | Oct | 12 | 15
| 985 | 2.2833 | 6.2493 | 2.642 | Feb | 9 | 7 | 3.736 | Oct | 12 | 15
| 995 | 0.9048 | 7.1488 | 1.56 | Feb | 9 | 7 | 3.954 | Jan | 22 | 15
| 195 | 3.9509 | 0.611 | 1.802 | Jan | 1 | 1 | 0.944 | Jun | 26 | 17
| 200 | 4.9204 | 0.8004 | 2.275 | Dec | 31 | 24 | 1.198 | Jun | 26 | 17
| 210 | 6.3171 | 0.5185 | 2.671 | Jan | 1 | 1 | 0.877 | Jun | 14 | 14
| 215 | 5.1811 | 0.8948 | 2.39 | Nov | 26 | 8 | 1.366 | Jun | 26 | 17
| 220 | 6.7257 | 0.5762 | 2.788 | Jan | 1 | 1 | 1.012 | Jun | 14 | 15
| 230 | 9.9385 | 0.955 | 4.16 | Jan | 1 | 1 | 1.701 | Jun | 26 | 17
| 240 | 5.5393 | 0.9218 | 2.605 | Jan | 1 | 1 | 1.192 | Jun | 14 | 15
| 250 | 4.935 | 3.4668 | 2.78 | Jan | 1 | 1 | 3.034 | Sept | 12 | 14
| 270 | 4.5764 | 7.3086 | 2.748 | Jan | 1 | 1 | 6.613 | Jan | 22 | 14
| 280 | 4.7381 | 5.2058 | 2.752 | Jan | 1 | 1 | 4.676 | Jan | 22 | 14
| 290 | 4.7447 | 5.3206 | 2.75 | Jan | 1 | 1 | 6.411 | Jan | 22 | 14
| 300 | 4.6679 | 5.0381 | 2.766 | Jan | 1 | 1 | 4.221 | Jun | 26 | 17
| 310 | 5.2396 | 3.1279 | 2.771 | Jan | 1 | 1 | 3.618 | Jun | 26 | 18
| 320 | 3.9699 | 4.9131 | 2.733 | Jan | 1 | 2 | 5.993 | Jan | 22 | 14
| 395 | 4.8657 | 0.0055 | 2.09 | Jan | 1 | 2 | 0.294 | Aug | 5 | 18
| 400 | 6.61 | 0.0244 | 2.788 | Jan | 1 | 1 | 0.456 | Aug | 5 | 17
| 410 | 8.2122 | 0.0523 | 3.473 | Jan | 1 | 1 | 0.624 | Jun | 26 | 18
| 420 | 7.027 | 0.1419 | 3.29 | Jan | 1 | 1 | 0.836 | Jun | 26 | 17
| 430 | 5.5449 | 0.9527 | 3.285 | Jan | 1 | 1 | 1.874 | Jul | 17 | 14
| 440 | 4.5039 | 4.4141 | 3.237 | Jan | 1 | 1 | 4.679 | Oct | 18 | 14
| 450 | 3.8503 | 6.6132 | 3.042 | Jan | 1 | 1 | 6.501 | Jan | 22 | 14
| 460 | 4.2625 | 6.7291 | 3.101 | Jan | 1 | 1 | 6.304 | Jan | 22 | 14
| 470 | 3.9597 | 6.0054 | 3.169 | Jan | 1 | 1 | 6.407 | Jan | 22 | 14
| 800 | 4.9798 | 0.3914 | 2.84 | Feb | 9 | 7 | 1.052 | Aug | 5 | 15
| 810 | 2.185 | 1.6056 | 2.695 | Feb | 9 | 7 | 2.179 | Sep | 4 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 25.26 | -13.5 | Feb | 9 | 7 | 64.6 | Oct | 1 | 16
| 900FF | 25.34 | 1.6 | Feb | 9 | 7 | 44.3 | Sep | 12 | 16
| 650FF | 18.93 | -17.5 | Jan | 1 | 1 | 63.3 | Oct | 1 | 16
| 950FF | 14.78 | -12.5 | Feb | 9 | 6 | 36.4 | Aug | 5 | 16
| 680FF | 31.71 | -7.2 | Feb | 9 | 7 | 72.2 | Oct | 12 | 16
| 980FF | 31.84 | 10.5 | Nov | 4 | 8 | 50.2 | Sep | 12 | 15
| 960 | 27.74 | 5 | Feb | 9 | 7 | 49.5 | Oct | 12 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1665.18
| NORTH | 432.12
| EAST | 1054.24
| SOUTH | 1363.1
| WEST | 961.18
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 813.88
| 660/South | 442.7
| 670/South | 1028.35
| 620/West | 591.88
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 631.33
| 630/West | 389.67
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.17 | -46.9 | Dec | 31 | 23 | 26.7 | Aug | 4 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 732 | 523 | 3.23 | 1 | 1 | 6.19 | 22 | 14 | 266 | 42 | 2.2 | 1 | 5 | 1.81 | 22 | 16
| Feb | 682 | 398 | 3.14 | 9 | 6 | 5.42 | 2 | 14 | 283 | 11 | 2.63 | 9 | 7 | 0.85 | 15 | 16
| Mar | 481 | 489 | 2.23 | 17 | 6 | 5.04 | 9 | 14 | 115 | 56 | 1.76 | 17 | 7 | 1.27 | 10 | 15
| Apr | 479 | 263 | 2.38 | 11 | 6 | 4.04 | 12 | 14 | 228 | 22 | 1.93 | 3 | 4 | 0.95 | 8 | 15
| May | 139 | 364 | 1.75 | 1 | 5 | 3.1 | 10 | 14 | 29 | 125 | 1.23 | 1 | 5 | 1.46 | 11 | 15
| Jun | 14 | 550 | 0.76 | 10 | 5 | 3.43 | 13 | 14 | 0 | 404 | 0 | 1 | 1 | 1.89 | 14 | 15
| Jul | 14 | 556 | 0.57 | 26 | 5 | 3.64 | 17 | 14 | 0 | 410 | 0 | 1 | 1 | 1.97 | 17 | 15
| Aug | 9 | 674 | 0.56 | 17 | 6 | 4.7 | 29 | 14 | 0 | 531 | 0 | 1 | 1 | 2.51 | 29 | 15
| Sep | 81 | 743 | 1.19 | 29 | 1 | 5.58 | 30 | 14 | 0 | 492 | 0 | 1 | 1 | 2.81 | 11 | 15
| Oct | 354 | 681 | 1.77 | 9 | 6 | 6.07 | 18 | 14 | 70 | 281 | 1.21 | 7 | 7 | 2.9 | 12 | 15
| Nov | 629 | 444 | 3.11 | 26 | 7 | 6.03 | 28 | 14 | 286 | 63 | 2.28 | 26 | 8 | 1.94 | 20 | 15
| Dec | 750 | 476 | 3.17 | 31 | 24 | 6.12 | 1 | 14 | 308 | 48 | 2.04 | 9 | 7 | 1.67 | 2 | 15
| Total | 4364 | 6161 | [6 empty] | 1585 | 2485
| Max |  |  | 3.23 |  |  | 6.19 |  |  |  |  | 2.63 |  |  | 2.9
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -30.02 | 0.09 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -27.59 | 0.67 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -34.17 | 0.04 | -1.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -37.85 | -0.01 | -2.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 2.88 | 1.27 | 1.27 | -35.32 | -0.06 | -4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.44 | 1
| 6 | 17.81 | 9.22 | 9.22 | 90.78 | 24.28 | 24.28 | -36.27 | -0.11 | -1.82 | 0 | 0 | 0 | 5.81 | 3.16 | 7.24 | 15.28 | 8.33 | 19.06
| 7 | 60.75 | 31.59 | 31.59 | 272.39 | 52.29 | 52.29 | -39.06 | 0.44 | 0.27 | 0 | 0 | 0 | 19.89 | 10.83 | 24.8 | 32.92 | 17.93 | 41.04
| 8 | 110.5 | 57.22 | 56.9 | 475.84 | 79.31 | 78.93 | -35.71 | 0.44 | 1.19 | 98.09 | 52.46 | 130.57 | 36.03 | 19.62 | 44.92 | 49.71 | 27.07 | 61.97
| 9 | 156.75 | 82.11 | 80.12 | 666.65 | 166.72 | 101.39 | -37.21 | 0.93 | 2.34 | 305.31 | 165.67 | 385.67 | 51.69 | 28.16 | 64.45 | 72.36 | 39.24 | 94.38
| 10 | 198.88 | 105.56 | 100.9 | 825.46 | 295.8 | 117.25 | -36.53 | 2.52 | 5.18 | 471.51 | 257.88 | 580.1 | 66.46 | 36.2 | 82.87 | 117.05 | 62.79 | 166.3
| 11 | 256.38 | 137.73 | 128.06 | 939.78 | 390.25 | 126.5 | -35.02 | 3.53 | 5.23 | 588.43 | 323.46 | 713.01 | 86.72 | 47.23 | 108.12 | 169.35 | 90.23 | 238.75
| 12 | 276 | 149.3 | 137.41 | 1001.8 | 441.16 | 130.19 | -34.15 | 3.08 | 5.13 | 646.8 | 356.29 | 781.74 | 94 | 51.2 | 117.2 | 204.8 | 108.79 | 284.99
| 13 | 274.88 | 148.6 | 141.06 | 1005.59 | 444.52 | 238.72 | -32.27 | 1.37 | 5.64 | 656.6 | 361.81 | 793.35 | 93.56 | 50.96 | 116.65 | 207.38 | 110.14 | 288.31
| 14 | 257.25 | 137.97 | 138.78 | 952.44 | 400.86 | 471.42 | -33.6 | 0.32 | 4.83 | 617.5 | 339.8 | 747 | 86.87 | 47.31 | 108.31 | 176.25 | 93.84 | 247.87
| 15 | 225.25 | 119.2 | 126.87 | 846.07 | 312.83 | 668.03 | -33.59 | -1.39 | 6.27 | 523.9 | 287.23 | 639.47 | 75.05 | 40.88 | 93.57 | 125.09 | 67.02 | 178.35
| 16 | 177.12 | 92.17 | 103.03 | 693.34 | 187.96 | 802.57 | -33.87 | -0.21 | 5.29 | 378.6 | 206.18 | 472.35 | 58.03 | 31.61 | 72.35 | 77.7 | 42.07 | 103.01
| 17 | 107.25 | 55.39 | 61.13 | 506.28 | 85.41 | 852.47 | -34.35 | -0.63 | 6.77 | 190.97 | 102.75 | 248.72 | 34.87 | 18.99 | 43.48 | 52.17 | 28.42 | 65.1
| 18 | 54.12 | 28.16 | 28.89 | 302.71 | 56.38 | 789.03 | -36.61 | -0.64 | 5.56 | 10.84 | 5.76 | 14.74 | 17.73 | 9.66 | 22.11 | 35.49 | 19.33 | 44.25
| 19 | 14.19 | 7.34 | 7.34 | 112.8 | 28.15 | 555.16 | -36.72 | -1.12 | 5.12 | 0 | 0 | 0 | 4.62 | 2.52 | 5.76 | 17.72 | 9.65 | 22.1
| 20 | 0 | 0 | 0 | 7.48 | 3.31 | 94.52 | -37.14 | -1.62 | 5.75 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 1.13 | 2.6
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -38.24 | -1.57 | 2.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -39.11 | -2.24 | 2.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -39.18 | -3.35 | 1.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.79 | -3.34 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.08 | 0.08 | 1.79 | 2.68 | 1.17 | 2.12 | 1.31 | 0.91 | 0 | 0 | 1.07 | 0.42 | 0 | 0 | 0 | 0 | -0.04 | -0.14 | -0.17 | -0.27 | -0.76 | -0.68 | 10.63 | 16.04
| 2 | 2.22 | 0.6 | 1.89 | 2.95 | 1.32 | 2.25 | 1.41 | 1.06 | 0 | 0 | 1.2 | 0.54 | 0 | 0 | 0 | 0 | 0.05 | -0.07 | -0.09 | -0.21 | -0.66 | -0.61 | 10 | 15.32
| 3 | 2.3 | 0.99 | 1.94 | 3.1 | 1.42 | 2.32 | 1.48 | 1.17 | 0 | 0 | 1.3 | 0.63 | 0 | 0 | 0 | 0 | 0.13 | -0.02 | -0.01 | -0.14 | -0.57 | -0.54 | 10 | 14.71
| 4 | 2.38 | 1.21 | 2 | 3.24 | 1.5 | 2.39 | 1.54 | 1.27 | 0 | 0 | 1.4 | 0.71 | 0 | 0 | 0.12 | 0 | 0.26 | 0.04 | 0 | -0.06 | -0.46 | -0.46 | 10 | 14.11
| 5 | 2.42 | 1.35 | 2.04 | 3.31 | 1.55 | 2.43 | 1.57 | 1.36 | 0 | 0 | 1.48 | 0.77 | 0.04 | 0 | 0.33 | 0 | 0.35 | 0.11 | 0 | -0.01 | -0.35 | -0.38 | 10 | 13.55
| 6 | 2.43 | 1.42 | 2.05 | 3.31 | 1.57 | 2.44 | 1.59 | 1.43 | 0 | 0.1 | 1.55 | 0.81 | 0.09 | 0 | 0.29 | 0 | 0.26 | 0.09 | 0 | 0 | -0.32 | -0.37 | 10 | 13.05
| 7 | 2.46 | 1.48 | 2.08 | 3.3 | 1.59 | 2.46 | 1.6 | 1.51 | 0 | 0.22 | 1.62 | 0.85 | 0 | 0 | 0.02 | 0 | -0.09 | -0.06 | 0 | -0.06 | -0.4 | -0.44 | 10 | 12.53
| 8 | 2.09 | 3.06 | 1.86 | 2.84 | 1.3 | 2.09 | 1.31 | 1.42 | 1.13 | 0.19 | 1.52 | 0.76 | 0 | 0 | 0 | 0 | -0.45 | -0.3 | 0 | -0.16 | -0.52 | -0.54 | 15 | 15.29
| 9 | 0.79 | 1.94 | 1.01 | 1.21 | 0.34 | 0.77 | 0.25 | 0.93 | 1.7 | 0.01 | 1.02 | 0.37 | 0 | 0 | 0 | 0 | -0.91 | -0.63 | -0.11 | -0.27 | -0.68 | -0.66 | 20 | 20
| 10 | 0 | 0.15 | 0.13 | 0.02 | -0.1 | -1.11 | -1.63 | 0.38 | 0.91 | 0 | 0.46 | -0.2 | -0.23 | -0.08 | -0.26 | -0.19 | -1.55 | -1.14 | -0.31 | -0.45 | -0.94 | -0.88 | 21.16 | 20
| 11 | -1.28 | -0.7 | 0 | -1.14 | -1.98 | -3.12 | -3.67 | 0.01 | 0.44 | 0 | -0.12 | -0.88 | -1.21 | -0.65 | -1.43 | -0.99 | -2.36 | -1.84 | -0.61 | -0.72 | -1.29 | -1.17 | 26.39 | 20.21
| 12 | -3.36 | -2.96 | -0.47 | -3.35 | -4.13 | -4.62 | -5.21 | 0 | 0.04 | -0.09 | -0.77 | -1.6 | -2.22 | -1.38 | -2.61 | -1.84 | -3.14 | -2.53 | -0.94 | -1 | -1.65 | -1.46 | 27 | 20.78
| 13 | -4.69 | -4.51 | -1.63 | -4.86 | -5.48 | -5.6 | -6.22 | 0 | 0 | -0.69 | -1.48 | -2.34 | -2.78 | -1.81 | -3.26 | -2.42 | -3.55 | -3 | -1.21 | -1.23 | -1.93 | -1.71 | 27 | 22.86
| 14 | -5.08 | -5 | -2.18 | -5.1 | -5.85 | -5.83 | -6.42 | 0 | 0 | -1.17 | -1.94 | -2.78 | -2.93 | -1.97 | -3.42 | -2.61 | -3.63 | -3.12 | -1.38 | -1.39 | -2.11 | -1.86 | 27 | 24.53
| 15 | -4.39 | -4.36 | -1.95 | -3.94 | -5.23 | -5.07 | -5.73 | -0.06 | 0 | -1.35 | -2.02 | -2.83 | -2.72 | -1.92 | -3.14 | -2.42 | -3.37 | -2.88 | -1.44 | -1.42 | -2.15 | -1.89 | 27 | 25.25
| 16 | -3.24 | -3.23 | -1.37 | -2.63 | -4.14 | -3.87 | -4.6 | -0.08 | 0 | -1.35 | -1.94 | -2.73 | -2.33 | -1.75 | -2.61 | -2 | -2.95 | -2.44 | -1.38 | -1.34 | -2.08 | -1.8 | 27 | 25.47
| 17 | -1.59 | -1.59 | -0.49 | -0.94 | -2.55 | -2.21 | -3 | 0 | 0 | -1.05 | -1.56 | -2.34 | -1.88 | -1.49 | -2.01 | -1.59 | -2.49 | -2.02 | -1.3 | -1.24 | -1.98 | -1.69 | 27 | 24.94
| 18 | -0.12 | -0.1 | -0.02 | -0.02 | -0.61 | -0.2 | -1.02 | 0 | 0 | -0.47 | -0.89 | -1.63 | -1.49 | -1.23 | -1.54 | -1.27 | -2.09 | -1.69 | -1.2 | -1.13 | -1.87 | -1.58 | 25.82 | 23.5
| 19 | 0.1 | 0.1 | 0.08 | 0.72 | 0 | 1.07 | 0.18 | 0 | 0 | -0.05 | -0.35 | -1.08 | -1.1 | -0.95 | -1.09 | -0.95 | -1.68 | -1.36 | -1.07 | -1 | -1.72 | -1.44 | 21.21 | 22.04
| 20 | 1 | 1 | 0.87 | 1.84 | 0 | 1.71 | 0.67 | 0 | 0 | 0 | -0.04 | -0.75 | -0.64 | -0.59 | -0.58 | -0.63 | -1.19 | -1.03 | -0.92 | -0.86 | -1.55 | -1.28 | 20 | 21.08
| 21 | 1.7 | 1.7 | 1.46 | 2.4 | 0.2 | 2.05 | 1 | 0 | 0.02 | 0 | 0.23 | -0.48 | -0.24 | -0.24 | -0.14 | -0.37 | -0.76 | -0.75 | -0.77 | -0.73 | -1.39 | -1.14 | 20 | 20.23
| 22 | 2.1 | 2.1 | 1.81 | 2.75 | 0.72 | 2.3 | 1.24 | 0 | 0.25 | 0 | 0.48 | -0.25 | -0.04 | -0.07 | 0 | -0.18 | -0.51 | -0.55 | -0.65 | -0.63 | -1.25 | -1.03 | 20 | 20
| 23 | 2.36 | 2.36 | 2.03 | 3.03 | 1.08 | 2.48 | 1.42 | 0.05 | 0.52 | 0 | 0.71 | -0.04 | 0 | 0 | 0 | -0.05 | -0.35 | -0.41 | -0.54 | -0.54 | -1.12 | -0.93 | 20 | 20
| 24 | 2.47 | 0.32 | 2.13 | 3.11 | 1.29 | 2.54 | 1.52 | 0.28 | 0.08 | 0 | 0.86 | 0.1 | 0 | 0 | 0 | 0 | -0.23 | -0.31 | -0.42 | -0.45 | -1 | -0.84 | 13.55 | 18.38
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 6 | 13.28 | 19.86 | 21.37 | 16.32 | 23.79
| 2 | 4.1 | 12.7 | 19.01 | 20.84 | 14.25 | 23.19
| 3 | 2.48 | 12.17 | 18.1 | 20.18 | 12.37 | 22.68
| 4 | 0.99 | 11.64 | 16.97 | 19.31 | 10.6 | 22.16
| 5 | -0.3 | 11.15 | 15.83 | 18.4 | 9.01 | 21.69
| 6 | -1.35 | 10.72 | 16.09 | 18.55 | 7.61 | 21.27
| 7 | -2.34 | 10.25 | 18.49 | 20.13 | 6.29 | 20.84
| 8 | -2.4 | 10.14 | 20.94 | 22.07 | 5.9 | 20.76
| 9 | 1.57 | 11.22 | 23.29 | 24.04 | 9.12 | 21.86
| 10 | 9.22 | 13.19 | 26.23 | 25.3 | 15.82 | 23.76
| 11 | 18.48 | 15.41 | 30.05 | 26.65 | 24.43 | 25.83
| 12 | 28.14 | 17.71 | 34.64 | 27.92 | 33.78 | 28.05
| 13 | 37.38 | 20.03 | 38.99 | 28.96 | 43.16 | 30.34
| 14 | 44.87 | 21.78 | 42.49 | 29.78 | 51.16 | 32.04
| 15 | 48.81 | 22.59 | 44.77 | 30.31 | 56.13 | 32.66
| 16 | 49.81 | 22.89 | 45.78 | 30.52 | 58.45 | 32.9
| 17 | 47.28 | 22.44 | 45.65 | 30.55 | 57.42 | 32.38
| 18 | 40.93 | 21.07 | 44.91 | 30.53 | 52.78 | 30.99
| 19 | 33.48 | 19.67 | 38.29 | 29.51 | 47.02 | 29.68
| 20 | 27.37 | 18.77 | 31.6 | 27.82 | 42.06 | 28.9
| 21 | 22.09 | 17.93 | 28.34 | 26.48 | 37.49 | 28.17
| 22 | 17.43 | 17.11 | 26.14 | 25.61 | 33.3 | 27.47
| 23 | 13.28 | 16.31 | 24.6 | 24.95 | 29.35 | 26.76
| 24 | 9.82 | 15.65 | 22.99 | 23.99 | 25.88 | 26.21
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 3
| 2 | 6
| 3 | 19
| 4 | 29
| 5 | 29
| 6 | 43
| 7 | 66
| 8 | 74
| 9 | 96
| 10 | 110
| 11 | 141
| 12 | 200
| 13 | 203
| 14 | 196
| 15 | 238
| 16 | 271
| 17 | 271
| 18 | 310
| 19 | 340
| 20 | 323
| 21 | 319
| 22 | 319
| 23 | 285
| 24 | 272
| 25 | 270
| 26 | 270
| 27 | 272
| 28 | 318
| 29 | 296
| 30 | 327
| 31 | 363
| 32 | 374
| 33 | 403
| 34 | 390
| 35 | 336
| 36 | 292
| 37 | 237
| 38 | 178
| 39 | 117
| 40 | 71
| 41 | 45
| 42 | 21
| 43 | 14
| 44 | 3
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## TRNSYS
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Participants: This file is reorganized since 140-2014. Regarding content changes to 140-2014, edit tracking colors are:
Red is for edits from June 2013 through April 2018 distribution for the Round 3 sim trial draft.
| Software: | TRNSYS
| Version: | TRNSYS 18.00.0001
| Date of Results: | 2019-04-25
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.5036 | 5.7795 | 3.3589 | Jan | 1 | 1 | 6.0457 | Jan | 22 | 14
| 610 | 4.5921 | 4.1168 | 3.3595 | Jan | 1 | 1 | 5.8678 | Dec | 1 | 14
| 620 | 4.719 | 3.8407 | 3.3846 | Jan | 1 | 1 | 4.5883 | Jun | 26 | 17
| 630 | 5.1386 | 2.5729 | 3.3876 | Jan | 1 | 1 | 3.9494 | Jun | 26 | 17
| 640 | 2.6528 | 5.4772 | 4.0385 | Nov | 26 | 8 | 5.9671 | Jan | 22 | 14
| 650 | 0 | 4.6323 | 0 | Dec | 31 | 0 | 5.7975 | Oct | 18 | 14
| 660 | 3.7897 | 2.9663 | 2.9552 | Jan | 1 | 1 | 3.4574 | Oct | 18 | 14
| 670 | 6.1399 | 6.1978 | 4.221 | Nov | 26 | 8 | 6.4013 | Oct | 18 | 14
| 680 | 2.2863 | 6.3098 | 2.1147 | Nov | 26 | 8 | 6.5566 | Jan | 22 | 14
| 685 | 5.0422 | 8.8513 | 3.3744 | Jan | 1 | 1 | 6.8674 | Jan | 22 | 14
| 695 | 2.8917 | 9.0391 | 2.1177 | Nov | 26 | 8 | 7.1752 | Jan | 22 | 14
| 900 | 1.814 | 2.2671 | 2.7785 | Feb | 9 | 7 | 2.9401 | Oct | 1 | 14
| 910 | 2.1318 | 1.1909 | 2.7992 | Feb | 9 | 6 | 2.081 | Oct | 12 | 15
| 920 | 3.6067 | 2.5489 | 2.8643 | Feb | 9 | 6 | 3.1541 | Jun | 26 | 18
| 930 | 4.3841 | 1.6718 | 2.9004 | Feb | 9 | 6 | 2.6131 | Jun | 26 | 18
| 940 | 1.1691 | 2.2035 | 3.4048 | Jan | 1 | 9 | 2.9376 | Oct | 1 | 14
| 950 | 0 | 0.64162 | 0 | Dec | 31 | 0 | 2.2364 | Sep | 11 | 15
| 960 | 2.8595 | 0.78896 | 2.3004 | Feb | 9 | 6 | 1.3385 | Jun | 26 | 17
| 980 | 0.45047 | 3.5185 | 1.5921 | Feb | 9 | 7 | 3.3126 | Oct | 12 | 14
| 985 | 2.5364 | 6.1135 | 2.7854 | Feb | 9 | 6 | 3.8847 | Oct | 1 | 14
| 995 | 1.077 | 7.0638 | 1.662 | Feb | 9 | 6 | 4.1149 | Jan | 22 | 15
| 195 | 4.0939 | 0.59153 | 1.7959 | Jan | 1 | 1 | 0.99351 | Jun | 26 | 17
| 200 | 5.1429 | 0.78844 | 2.3527 | Nov | 26 | 8 | 1.2589 | Jun | 26 | 17
| 210 | 6.4295 | 0.45918 | 2.7498 | Jan | 1 | 1 | 0.88416 | Jun | 26 | 18
| 215 | 5.4434 | 0.85047 | 2.4894 | Nov | 26 | 8 | 1.3521 | Jun | 26 | 17
| 220 | 6.8678 | 0.49766 | 2.8786 | Jan | 1 | 1 | 0.96801 | Jun | 26 | 18
| 230 | 10.2343 | 0.89664 | 4.3153 | Jan | 1 | 1 | 1.6936 | Jun | 26 | 17
| 240 | 5.6572 | 0.83378 | 2.6931 | Jan | 1 | 1 | 1.1496 | Jun | 26 | 18
| 250 | 5.1047 | 2.9038 | 2.8744 | Jan | 1 | 1 | 2.688 | Sep | 12 | 14
| 270 | 4.6312 | 7.2885 | 2.8432 | Jan | 1 | 2 | 6.6375 | Jan | 22 | 14
| 280 | 4.8699 | 4.8081 | 2.8487 | Jan | 1 | 1 | 4.3999 | Jan | 22 | 14
| 290 | 4.7248 | 5.4612 | 2.8434 | Jan | 1 | 2 | 6.4019 | Jan | 22 | 14
| 300 | 4.7256 | 4.913 | 2.8536 | Jan | 1 | 1 | 4.2782 | Jun | 26 | 17
| 310 | 5.1626 | 3.3242 | 2.8563 | Jan | 1 | 1 | 3.7015 | Jun | 26 | 18
| 320 | 4.0311 | 4.7877 | 2.8335 | Jan | 1 | 2 | 5.9494 | Jan | 22 | 14
| 395 | 4.9081 | 0.0035162 | 2.1613 | Jan | 1 | 2 | 0.2652 | Jun | 14 | 18
| 400 | 6.7692 | 0.012683 | 2.8786 | Jan | 1 | 1 | 0.37199 | Jun | 14 | 17
| 410 | 8.4449 | 0.03512 | 3.5969 | Jan | 1 | 1 | 0.60368 | Jun | 26 | 18
| 420 | 7.2364 | 0.10944 | 3.4115 | Jan | 1 | 1 | 0.81407 | Jun | 26 | 18
| 430 | 5.8505 | 0.73902 | 3.4088 | Jan | 1 | 1 | 1.7041 | Jun | 26 | 15
| 440 | 4.7207 | 3.7412 | 3.3743 | Jan | 1 | 1 | 4.3076 | Oct | 18 | 14
| 450 | 3.8709 | 6.5307 | 3.0373 | Jan | 1 | 1 | 6.3134 | Jan | 22 | 14
| 460 | 4.2898 | 6.2434 | 3.1597 | Jan | 1 | 1 | 6.0689 | Jan | 22 | 14
| 470 | 4.0746 | 6.0559 | 3.2315 | Jan | 1 | 1 | 6.32 | Jan | 22 | 14
| 800 | 5.3695 | 0.28208 | 2.9669 | Feb | 9 | 6 | 0.93559 | Aug | 5 | 15
| 810 | 2.6098 | 1.2945 | 2.8447 | Feb | 9 | 6 | 2.1129 | Sep | 11 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 24.2578 | -13.8442 | Feb | 9 | 7 | 62.3692 | Oct | 1 | 15
| 900FF | 24.4623 | 0.63931 | Feb | 9 | 7 | 43.2522 | Sep | 12 | 15
| 650FF | 18.402 | -17.5067 | Dec | 31 | 24 | 61.1332 | Oct | 1 | 15
| 950FF | 14.6786 | -12.7995 | Feb | 9 | 6 | 36.1267 | Sep | 11 | 16
| 680FF | 30.1869 | -8.0736 | Feb | 9 | 7 | 69.7742 | Jan | 22 | 16
| 980FF | 30.492 | 9.4717 | Nov | 4 | 7 | 48.5406 | Sep | 12 | 15
| 960 | 26.7976 | 4.2376 | Feb | 9 | 7 | 48.0966 | Oct | 12 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1668.98
| NORTH | 440.165
| EAST | 1067.94
| SOUTH | 1384.23
| WEST | 974.473
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 822.589
| 660/South | 448.493
| 670/South | 1039.23
| 620/West | 623.797
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 661.81
| 630/West | 445.549
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.0587 | -46.1617 | Dec | 31 | 24 | 26.0293 | Jun | 13 | 18
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 734.943 | 495.012 | 3.3589 | 1 | 1 | 6.0457 | 22 | 14 | 291.936 | 44.635 | 2.3786 | 1 | 5 | 1.8776 | 22 | 15
| Feb | 702.079 | 367.404 | 3.2252 | 9 | 6 | 5.1553 | 2 | 14 | 322.141 | 9.2434 | 2.7785 | 9 | 7 | 0.82938 | 15 | 15
| Mar | 495.001 | 457.384 | 2.287 | 17 | 6 | 4.7399 | 9 | 14 | 143.84 | 50.5508 | 1.8582 | 17 | 6 | 1.4258 | 11 | 14
| Apr | 517.287 | 235.357 | 2.4572 | 11 | 6 | 3.8027 | 12 | 14 | 275.466 | 16.0525 | 2.0359 | 3 | 4 | 0.83719 | 8 | 15
| May | 150.732 | 325.154 | 1.778 | 1 | 5 | 3.0405 | 21 | 14 | 37.5028 | 98.3549 | 1.3242 | 1 | 5 | 1.4645 | 11 | 14
| Jun | 15.9512 | 516.057 | 0.8526 | 9 | 5 | 3.3792 | 13 | 13 | 0 | 365.819 | 0 | 31 | 0 | 1.9742 | 14 | 14
| Jul | 16.7263 | 514.389 | 0.61893 | 26 | 5 | 3.4967 | 17 | 14 | 0 | 365.513 | 0 | 31 | 0 | 1.975 | 17 | 15
| Aug | 9.6039 | 634.136 | 0.59085 | 17 | 6 | 4.6505 | 27 | 13 | 0 | 487.566 | 0 | 31 | 0 | 2.5337 | 29 | 15
| Sep | 84.8239 | 710.474 | 1.2116 | 28 | 24 | 5.4199 | 30 | 14 | 0.53697 | 458.859 | 0.19442 | 29 | 7 | 2.8712 | 11 | 15
| Oct | 367.051 | 649.483 | 1.8132 | 15 | 6 | 5.9226 | 18 | 14 | 85.0098 | 260.853 | 1.3311 | 7 | 7 | 2.9401 | 1 | 14
| Nov | 645.809 | 418.571 | 3.2066 | 26 | 8 | 5.824 | 28 | 14 | 318.242 | 60.1796 | 2.4629 | 26 | 8 | 1.9406 | 22 | 14
| Dec | 763.546 | 456.103 | 3.2781 | 31 | 24 | 5.9425 | 1 | 14 | 339.357 | 49.5012 | 2.1801 | 9 | 7 | 1.6903 | 2 | 15
| Total | 4503.5533 | 5779.524 | [6 empty] | 1814.0316 | 2267.1274
| Max |  |  | 3.3589 |  |  | 6.0457 |  |  |  |  | 2.7785 |  |  | 2.9401
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -24.4041 | 0.41396 | 1.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -28.908 | 0.36976 | 0.40274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -30.651 | 0.3372 | -0.72718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -35.7966 | -0.0004892 | -2.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 1.8578 | 1.0886 | 1.0886 | -36.4345 | -0.049894 | -3.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66207 | 0.36266 | 0.82883
| 6 | 15 | 7.7154 | 7.7154 | 89.6008 | 25.7932 | 25.7932 | -35.6524 | -0.10199 | -3.0874 | 0 | 0 | 0 | 4.6924 | 2.5704 | 5.8743 | 15.6873 | 8.593 | 19.6385
| 7 | 60 | 31.2881 | 31.2881 | 275.5875 | 53.3893 | 53.3893 | -37.476 | 0.14095 | -0.93306 | 0 | 0 | 0 | 19.0292 | 10.4236 | 23.8222 | 32.4711 | 17.7867 | 40.6497
| 8 | 111 | 58.0581 | 57.9409 | 478.6209 | 80.1937 | 80.1937 | -37.1982 | 0.41027 | 0.56357 | 106.3916 | 56.996 | 140.083 | 35.3106 | 19.3421 | 44.2044 | 48.7734 | 26.7166 | 61.0581
| 9 | 158 | 83.1431 | 81.9063 | 669.4288 | 178.5571 | 102.9649 | -36.2544 | 0.66268 | 1.6181 | 323.2919 | 175.7302 | 406.3398 | 50.5672 | 27.6992 | 63.3037 | 71.7945 | 39.1157 | 95.0519
| 10 | 195 | 103.6598 | 100.6192 | 827.9708 | 304.6694 | 118.7803 | -36.5874 | 1.7115 | 3.5737 | 482.6422 | 264.7322 | 591.3496 | 63.0453 | 34.5344 | 78.9248 | 118.4204 | 63.6391 | 171.5706
| 11 | 263 | 141.3514 | 133.4601 | 941.9442 | 398.8477 | 127.9971 | -35.3983 | 3.0181 | 5.1703 | 593.3244 | 326.2696 | 718.8377 | 85.9692 | 47.0914 | 107.6225 | 170.3654 | 90.5877 | 245.2683
| 12 | 278 | 150.3411 | 140.7836 | 1004.1701 | 449.7855 | 131.6306 | -34.1462 | 3.3069 | 5.2388 | 655.1426 | 360.9121 | 789.0166 | 91.4367 | 50.0863 | 114.4671 | 209.7239 | 111.2626 | 294.3631
| 13 | 277 | 149.7167 | 143.6691 | 1007.5518 | 452.8075 | 238.8366 | -32.6565 | 2.2335 | 5.3636 | 665.9038 | 367.0186 | 801.25 | 91.0569 | 49.8783 | 113.9917 | 210.9664 | 111.9095 | 296.2153
| 14 | 259 | 138.9957 | 139.5313 | 954.4569 | 408.8874 | 475.03 | -32.45 | 0.85375 | 5.3363 | 624.0771 | 343.5482 | 753.2139 | 84.5365 | 46.3066 | 105.829 | 180.3064 | 95.7693 | 257.3993
| 15 | 227 | 120.4472 | 126.0353 | 848.3258 | 320.8144 | 673.0005 | -33.132 | -0.51745 | 5.6052 | 531.1272 | 291.6286 | 647.3005 | 73.2554 | 40.1271 | 91.7065 | 127.6724 | 68.4197 | 185.0807
| 16 | 181 | 94.7457 | 102.5145 | 695.7926 | 197.5898 | 809.0801 | -33.233 | -0.76901 | 5.8681 | 392.8611 | 214.6368 | 486.7755 | 57.6238 | 31.5646 | 72.1377 | 75.3431 | 41.0134 | 100.6228
| 17 | 104 | 54.3851 | 56.0031 | 508.9129 | 83.9625 | 861.5066 | -33.6218 | -0.39529 | 6.1476 | 204.1309 | 109.8074 | 265.4371 | 33.0767 | 18.1185 | 41.4079 | 51.0656 | 27.9722 | 63.9276
| 18 | 53 | 27.594 | 27.594 | 305.8694 | 57.4921 | 806.2411 | -35.0378 | -0.6146 | 6.2678 | 18.3687 | 9.7258 | 24.9891 | 16.7825 | 9.193 | 21.0096 | 34.9664 | 19.1536 | 43.7735
| 19 | 11 | 5.6434 | 5.6434 | 113.5205 | 29.6492 | 588.0142 | -36.2502 | -0.85587 | 5.5904 | 0 | 0 | 0 | 3.4323 | 1.8801 | 4.2968 | 18.0325 | 9.8777 | 22.5744
| 20 | 0 | 0 | 0 | 5.1513 | 3.1157 | 83.7153 | -36.5459 | -1.3469 | 5.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 1.895 | 1.038 | 2.3722
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -37.3195 | -1.5768 | 4.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -38.344 | -1.8894 | 2.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -38.8709 | -2.7778 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -38.7168 | -3.3333 | 1.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
| 1 | 2.1718 | 0.11565 | 1.8233 | 2.7706 | 1.2499 | 2.2164 | 1.3877 | 1.0334 | 0 | 0 | 1.1818 | 0.53763 | 0 | 0 | 0 | 0 | -0.052034 | -0.13755 | -0.030013 | -0.17298 | -0.66171 | -0.61504 | 10 | 14.9916
| 2 | 2.271 | 0.62194 | 1.8954 | 2.9307 | 1.3728 | 2.2966 | 1.4641 | 1.1534 | 0 | 0 | 1.2942 | 0.62899 | 0 | 0 | 0 | 0 | 0.025254 | -0.073529 | 0 | -0.10898 | -0.5713 | -0.54619 | 10 | 15.0095
| 3 | 2.3414 | 0.95848 | 1.9466 | 3.0517 | 1.4629 | 2.3561 | 1.5223 | 1.2628 | 0 | 0 | 1.3966 | 0.70796 | 0 | 0 | 0 | 0 | 0.145 | -0.00087619 | 0 | -0.038742 | -0.46544 | -0.46646 | 10 | 13.9919
| 4 | 2.4106 | 1.1918 | 1.9958 | 3.1786 | 1.5405 | 2.4196 | 1.578 | 1.3755 | 0 | 0.092844 | 1.5015 | 0.78477 | 0 | 0 | 0.13713 | 0 | 0.27949 | 0.071603 | 0 | 0 | -0.35659 | -0.38577 | 10 | 13.6703
| 5 | 2.4393 | 1.3222 | 2.0162 | 3.2358 | 1.5779 | 2.4442 | 1.6015 | 1.4592 | 0 | 0.21749 | 1.5771 | 0.83089 | 0.094557 | 0 | 0.32542 | 0 | 0.37362 | 0.13714 | 0 | 0 | -0.25937 | -0.31121 | 10 | 12.9607
| 6 | 2.4505 | 1.4041 | 2.028 | 3.2352 | 1.5974 | 2.4533 | 1.612 | 1.5326 | 0 | 0.32564 | 1.6428 | 0.86691 | 0.038588 | 0 | 0.22218 | 0 | 0.21087 | 0.08276 | 0 | 0 | -0.26648 | -0.32724 | 10 | 12.5881
| 7 | 2.4648 | 1.466 | 2.0459 | 3.2195 | 1.609 | 2.4668 | 1.6183 | 1.6045 | 0 | 0.41999 | 1.7074 | 0.90136 | 0 | 0 | 0 | 0 | -0.099433 | -0.096297 | 0 | -0.023003 | -0.38013 | -0.42475 | 10 | 12.0187
| 8 | 1.7476 | 2.5037 | 1.6135 | 2.3857 | 1.0329 | 1.7486 | 1.0378 | 1.3557 | 1.2786 | 0.23403 | 1.4465 | 0.69613 | 0 | 0 | 0 | 0 | -0.45575 | -0.34347 | 0 | -0.1092 | -0.51857 | -0.53025 | 15 | 15.9576
| 9 | 0.29604 | 1.4631 | 0.71656 | 0.68716 | 0 | 0.29652 | -0.27649 | 0.77638 | 1.5794 | 0 | 0.85185 | 0.19219 | 0 | 0 | 0 | 0 | -0.92639 | -0.68893 | -0.090224 | -0.2488 | -0.71573 | -0.68033 | 20 | 20
| 10 | -0.15773 | 0 | 0 | 0 | -0.73104 | -1.3527 | -2.0859 | 0.24812 | 0.84183 | 0 | 0.32364 | -0.42045 | -0.36749 | -0.17059 | -0.44642 | -0.33152 | -1.6327 | -1.2695 | -0.31161 | -0.46854 | -1.0407 | -0.95144 | 21.7174 | 20
| 11 | -1.3665 | -1.0953 | 0 | -1.2316 | -2.2417 | -3.1162 | -3.8622 | 0 | 0.30366 | 0 | -0.28825 | -1.1165 | -1.2888 | -0.72317 | -1.5147 | -1.094 | -2.4664 | -1.9765 | -0.65319 | -0.76822 | -1.4329 | -1.2752 | 25.2174 | 20
| 12 | -3.2336 | -2.69 | -0.52411 | -3.1719 | -4.1403 | -4.5191 | -5.2547 | 0 | 0 | -0.22351 | -0.96318 | -1.8616 | -2.1777 | -1.35 | -2.5624 | -1.892 | -3.1511 | -2.6266 | -0.9806 | -1.0533 | -1.7925 | -1.5789 | 27 | 20.9881
| 13 | -4.4188 | -4.1451 | -1.5139 | -4.5095 | -5.2985 | -5.4071 | -6.1055 | 0 | 0 | -0.73161 | -1.6316 | -2.5375 | -2.6489 | -1.6997 | -3.1183 | -2.3763 | -3.4891 | -3.0055 | -1.22 | -1.2706 | -2.0441 | -1.8067 | 27 | 23.005
| 14 | -4.5996 | -4.4711 | -1.8748 | -4.5907 | -5.4915 | -5.4259 | -6.1336 | 0 | 0 | -1.1455 | -1.9744 | -2.87 | -2.7498 | -1.8273 | -3.2401 | -2.493 | -3.5104 | -3.0535 | -1.3604 | -1.3952 | -2.1791 | -1.9307 | 27 | 24.4382
| 15 | -3.9649 | -3.9067 | -1.6375 | -3.7353 | -4.9288 | -4.6952 | -5.4801 | -0.0097877 | 0 | -1.2934 | -2.0099 | -2.9019 | -2.5224 | -1.7611 | -2.9531 | -2.2637 | -3.232 | -2.7773 | -1.3762 | -1.39 | -2.1762 | -1.9149 | 27 | 25.0064
| 16 | -2.8274 | -2.8007 | -1.0626 | -2.4556 | -3.8545 | -3.5095 | -4.3483 | 0 | 0 | -1.2148 | -1.8348 | -2.7176 | -2.0736 | -1.5425 | -2.3467 | -1.8199 | -2.7482 | -2.3013 | -1.275 | -1.2715 | -2.0485 | -1.7802 | 27 | 24.9739
| 17 | -1.1647 | -1.1527 | -0.18596 | -0.70988 | -2.2038 | -1.8248 | -2.6911 | 0 | 0 | -0.8108 | -1.3251 | -2.1893 | -1.6698 | -1.3035 | -1.8239 | -1.4619 | -2.3306 | -1.9323 | -1.1791 | -1.1727 | -1.9356 | -1.6747 | 27 | 24.1466
| 18 | 0 | 0 | 0 | 0.1031 | -0.27043 | 0.12836 | -0.72316 | 0 | 0 | -0.14797 | -0.55512 | -1.3747 | -1.3003 | -1.0574 | -1.3771 | -1.1511 | -1.9487 | -1.612 | -1.0627 | -1.0609 | -1.7994 | -1.5534 | 24.7749 | 22.4177
| 19 | 0.36036 | 0.36164 | 0.24487 | 0.78486 | 0 | 1.0762 | 0.26566 | 0 | 0 | 0 | -0.12032 | -0.89967 | -0.91574 | -0.7825 | -0.93641 | -0.8396 | -1.5442 | -1.2859 | -0.91459 | -0.91946 | -1.6253 | -1.3964 | 21.2749 | 21.0104
| 20 | 1.0287 | 1.0323 | 0.90071 | 1.8058 | 0 | 1.6727 | 0.73538 | 0 | 0.09175 | 0 | 0.17769 | -0.57738 | -0.50284 | -0.46077 | -0.46799 | -0.54058 | -1.089 | -0.96142 | -0.75544 | -0.76865 | -1.4325 | -1.2236 | 20 | 20.3503
| 21 | 1.6719 | 1.6738 | 1.4225 | 2.3956 | 0.39438 | 2.0601 | 1.0332 | 0 | 0.27159 | 0 | 0.41925 | -0.32112 | -0.19628 | -0.21189 | -0.1179 | -0.30722 | -0.75479 | -0.71544 | -0.62069 | -0.6432 | -1.2707 | -1.083 | 20 | 20
| 22 | 2.1066 | 2.1079 | 1.792 | 2.8009 | 0.79929 | 2.3472 | 1.2825 | 0.096471 | 0.52154 | 0 | 0.6443 | -0.10322 | -0.0091138 | -0.05591 | 0 | -0.14209 | -0.54994 | -0.55005 | -0.50904 | -0.54605 | -1.1431 | -0.97738 | 20 | 20
| 23 | 2.3929 | 2.3936 | 2.0235 | 3.1203 | 1.1242 | 2.5334 | 1.4716 | 0.30642 | 0.73879 | 0 | 0.84052 | 0.091677 | 0 | 0 | 0 | -0.022857 | -0.40268 | -0.42662 | -0.40721 | -0.46032 | -1.027 | -0.88459 | 20 | 20
| 24 | 2.5229 | 0.8527 | 2.1255 | 3.2615 | 1.3463 | 2.6039 | 1.5777 | 0.52323 | 0 | 0 | 0.98099 | 0.2338 | 0 | 0 | 0 | 0 | -0.26193 | -0.31199 | -0.29064 | -0.36221 | -0.89868 | -0.78278 | 15 | 17.6553
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 4.8678 | 12.3543 | 20.0209 | 21.1154 | 14.4417 | 22.2363
| 2 | 3.1842 | 11.8184 | 18.7675 | 20.5424 | 12.548 | 21.7134
| 3 | 1.7232 | 11.3192 | 18.213 | 19.9172 | 10.8267 | 21.2323
| 4 | 0.38989 | 10.8039 | 16.7605 | 19.0113 | 9.1997 | 20.7325
| 5 | -0.73229 | 10.3478 | 15.8849 | 18.1384 | 7.7578 | 20.2913
| 6 | -1.6653 | 9.9295 | 16.0945 | 18.3188 | 6.48 | 19.892
| 7 | -2.5318 | 9.4998 | 18.6396 | 19.9757 | 5.2952 | 19.4952
| 8 | -1.339 | 9.799 | 20.6119 | 22.5701 | 6.1093 | 19.8079
| 9 | 4.1068 | 11.4018 | 23.2169 | 24.209 | 11.026 | 21.363
| 10 | 11.9724 | 13.4628 | 26.4995 | 25.0426 | 18.4242 | 23.32
| 11 | 20.6983 | 15.5991 | 30.7733 | 26.5298 | 26.9441 | 25.378
| 12 | 29.8333 | 17.9031 | 35.1804 | 27.7048 | 36.1278 | 27.6309
| 13 | 38.2109 | 20.0527 | 39.0337 | 28.7071 | 44.8321 | 29.7398
| 14 | 44.2314 | 21.5258 | 41.924 | 29.4146 | 51.5938 | 31.1593
| 15 | 47.0105 | 22.2103 | 43.5674 | 29.8578 | 55.5469 | 31.7177
| 16 | 46.9306 | 22.2681 | 43.8561 | 29.9484 | 56.7937 | 31.761
| 17 | 43.4741 | 21.5145 | 43.3487 | 29.9561 | 54.6584 | 30.9917
| 18 | 36.5383 | 19.867 | 42.3948 | 29.8951 | 49.111 | 29.3415
| 19 | 29.6668 | 18.5155 | 33.6127 | 28.9728 | 43.4177 | 28.1322
| 20 | 24.2082 | 17.6825 | 29.6146 | 27.553 | 38.6121 | 27.3891
| 21 | 19.2617 | 16.825 | 27.9251 | 26.2179 | 34.0685 | 26.6361
| 22 | 15.0331 | 16.0591 | 25.3141 | 25.3225 | 30.1063 | 26.0008
| 23 | 11.2196 | 15.2703 | 24.6473 | 24.6889 | 26.2987 | 25.3028
| 24 | 8.1223 | 14.6249 | 22.567 | 23.7105 | 22.9692 | 24.7283
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 3
| 1 | 2
| 2 | 16
| 3 | 25
| 4 | 24
| 5 | 43
| 6 | 60
| 7 | 74
| 8 | 75
| 9 | 102
| 10 | 142
| 11 | 184
| 12 | 212
| 13 | 192
| 14 | 204
| 15 | 289
| 16 | 255
| 17 | 278
| 18 | 351
| 19 | 323
| 20 | 317
| 21 | 326
| 22 | 306
| 23 | 291
| 24 | 280
| 25 | 292
| 26 | 288
| 27 | 330
| 28 | 310
| 29 | 356
| 30 | 383
| 31 | 385
| 32 | 411
| 33 | 379
| 34 | 338
| 35 | 265
| 36 | 232
| 37 | 161
| 38 | 113
| 39 | 71
| 40 | 39
| 41 | 21
| 42 | 9
| 43 | 3
| 44 | 0
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760

## TestSpecAlt
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx |  | July 2019
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
[Note to Users: This file is reorganized since 140-2017. Red text indicates content changes to 140-2017.]
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
[Note to Users: Sky temperatures here are alternative specified values shown in a few charts and tables.]
| Software: | TestSpec-Alt
Version:
| Date of Results: | Sep 2018
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
600
610
620
630
640
650
660
670
680
685
695
900
910
920
930
940
950
960
980
985
995
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
450
460
470
800
810
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
600FF
900FF
650FF
950FF
680FF
980FF
960
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
HORZ.
NORTH
EAST
SOUTH
WEST
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
600/South
660/South
670/South
620/West
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
610/South
630/West
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -5.9 | -46.85 |  |  |  | 24.62
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | [6 empty] | -30.2822 | 3.6876 | 0.75693
| 2 | [6 empty] | -27.4567 | 4.4245 | 0.16261
| 3 | [6 empty] | -33.8377 | 3.8943 | -1.4341
| 4 | [6 empty] | -37.567 | 3.6721 | -2.7015
| 5 | [6 empty] | -35.0231 | 3.6641 | -4.1002
| 6 | [6 empty] | -35.993 | 3.803 | -1.779
| 7 | [6 empty] | -38.7016 | 4.3213 | 0.21141
| 8 | [6 empty] | -35.4235 | 4.3945 | 1.1998
| 9 | [6 empty] | -36.8689 | 4.9064 | 2.2849
| 10 | [6 empty] | -36.1031 | 6.2008 | 5.0591
| 11 | [6 empty] | -34.5636 | 6.9765 | 5.4079
| 12 | [6 empty] | -33.6763 | 6.2647 | 5.1147
| 13 | [6 empty] | -31.6698 | 4.1911 | 5.5711
| 14 | [6 empty] | -33.2373 | 3.1788 | 4.9914
| 15 | [6 empty] | -33.224 | 1.9243 | 6.0132
| 16 | [6 empty] | -33.5 | 1.1489 | 5.4557
| 17 | [6 empty] | -34.0382 | 3.2979 | 6.5386
| 18 | [6 empty] | -36.3464 | 3.2977 | 5.6681
| 19 | [6 empty] | -36.4727 | 2.4978 | 5.1895
| 20 | [6 empty] | -36.913 | 1.9983 | 5.7177
| 21 | [6 empty] | -37.9742 | 2.0062 | 2.1391
| 22 | [6 empty] | -38.9062 | 1.8319 | 2.1388
| 23 | [6 empty] | -38.9555 | 0.95143 | 1.541
| 24 | [6 empty] | -38.5188 | 0.95172 | 0.44827
* Direct-Beam and Diffuse
| Month: Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [6 empty] | Conditioned Zone
| kWh: Zone Loads**; Day: Zone Loads** | [6 empty] | Temperatures
| kWh: Feb 1 (Clear/Cold); Hour: July 14 (Clear/Hot) | [6 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
-50
-49
-48
-47
-46
-45
-44
-43
-42
-41
-40
-39
-38
-37
-36
-35
-34
-33
-32
-31
-30
-29
-28
-27
-26
-25
-24
-23
-22
-21
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10
-9
-8
-7
-6
-5
-4
-3
-2
-1
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
| 97 |  |  | Sum (check)
| 98 |  |  | 0